01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4230.00 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4230.00 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.8. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.9. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.10. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.11. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.2. PAYNES 4 (602036) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRE-WILLMAR8 (619977) 69.0 kV to GRE-WILLMR2T (619979) 12.5 kV Three Winding #1 b.4. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. GRANITF9 (652297) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.7. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. HRDLKCOL9 (620114) 34.5 kV to G380 RUGBY W (620115) 0.6 kV Two Winding #1 b.3. HRDLKCOL9 (620114) 34.5 kV to RGBYCOL9 (620168) 34.5 kV Transmission Circuit #1 b.4. RGBYWND4 (620368) 230.0 kV to RGBYCOL9 (620168) 34.5 kV Two Winding #1 b.5. RGBYWND4 (620368) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. RUGBY T (620179) 13.8 kV to RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.2. WINGER 4 (657758) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 b.4. WALLE 4 (657761) 230.0 kV to WALLE 8 (657316) 69.0 kV to WALLE 9 (657782) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on J526 SUB 345.00 (621480) 345 kV Bus a. Apply Fault at the J526 SUB 345.00 (621480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. DEUEL CO 3 (620480) 345.0 kV to J526 SUB (621480) 345.0 kV Transmission Circuit #1 b.3. J526 COL (621010) 34.5 kV to J526 FDR1 (621011) 34.5 kV Transmission Circuit #1 b.4. J526 FDR1 (621011) 34.5 kV to J526 G (621012) 0.7 kV Two Winding #1 b.5. J526 COL2 (621013) 34.5 kV to J526 FDR2 (621014) 34.5 kV Transmission Circuit #1 b.6. J526 FDR2 (621014) 34.5 kV to J526 G2 (621015) 0.7 kV Two Winding #1 b.7. J526 SUB (621480) 345.0 kV to J526 COL (621010) 34.5 kV Two Winding #1 b.8. J526 SUB (621480) 345.0 kV to J526 COL2 (621013) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply Fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BIGSTN1G (620315) 24.0 kV Two Winding #1 b.2. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAHPETN4 (620329) 230.0 kV to WAHPETN7 (620229) 115.0 kV to WAHPETN9 (620129) 41.6 kV Three Winding #2 b.2. HANKSON4 (620327) 230.0 kV to WAHPETN4 (620329) 230.0 kV Transmission Circuit #1 b.3. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to ALICE 7 (620259) 115.0 kV Transmission Circuit #1 b.2. ALICE 7 (620259) 115.0 kV to ENDERLN7 (620260) 115.0 kV Transmission Circuit #1 b.3. ENDERLN7 (620260) 115.0 kV to LISBON 7 (620261) 115.0 kV Transmission Circuit #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 41.6 kV Transmission Circuit #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.6. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.7. NEW EFFNGTN4 (620328) 230.0 kV to NEW EFFNGTN9 (620128) 41.6 kV Two Winding #1 b.8. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.9. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.4. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on MAPLE R3 345.00 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 345.00 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.5. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.6. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.7. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.8. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.9. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.10. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.11. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.12. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.13. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.14. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.15. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.16. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.17. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.18. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.19. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.20. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.21. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 b.23. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.24. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.2. WINGER 4 (657758) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.4. WALLE 4 (657761) 230.0 kV to WALLE 8 (657316) 69.0 kV to WALLE 9 (657782) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.3. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.4. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on GLENBOR4 230.00 (667052) 230 kV Bus a. Apply Fault at the GLENBOR4 230.00 (667052) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 b.2. GLENBOR4 (667052) 230.0 kV to GLENBOR8 (668405) 65.1 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on J436 COL 34.500 (620096) 34.5 kV Bus a. Apply Fault at the J436 COL 34.500 (620096) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to DAKOTA RNG 3 (620418) 345.0 kV Transmission Circuit #1 b.3. J437 COL (620098) 34.5 kV to DAKOTA RNG 3 (620418) 345.0 kV Two Winding #1 b.4. J437 COL (620098) 34.5 kV to J437 FDR (620099) 34.5 kV Transmission Circuit #1 b.5. J437 COL (620098) 34.5 kV to J437 DVAR (620095) 0.5 kV Two Winding #1 b.6. J437 FDR (620099) 34.5 kV to J437 DK RNG2 (620995) 0.6 kV Two Winding #1 b.7. J436 COL (620096) 34.5 kV to DAKOTA RNG 3 (620418) 345.0 kV Two Winding #1 b.8. J436 COL (620096) 34.5 kV to J436 DVAR (620094) 0.5 kV Two Winding #1 b.9. J436 COL (620096) 34.5 kV to J436 FDR (620097) 34.5 kV Transmission Circuit #1 b.10. J436 COL (620096) 34.5 kV to J436 DK RNG1 (620102) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.3. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.4. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.5. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on ALXLNRCTRT 345.00 (658049) 345 kV Bus a. Apply Fault at the ALXLNRCTRT 345.00 (658049) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to ALXLNRCTRT (658049) 345.0 kV Transmission Circuit #1 b.3. ALEXMRES3 (658047) 345.0 kV to ALXLNRCTRT (658049) 345.0 kV Transmission Circuit #z1 b.4. ALXLNRCTRT (658049) 345.0 kV to ALXLNRCTR (658201) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRA TR7 9 (605746) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #7 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRA TR7 9 (605746) 13.8 kV Three Winding #7 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on ELN345SHNT 3345.00 (661950) 345 kV Bus a. Apply Fault at the ELN345SHNT 3345.00 (661950) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1989 POI (49894) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 b.2. J1990 SUB (49903) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 b.3. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.4. ELLENDL345 3 (661097) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on J488 COL2 34.500 (621002) 34.5 kV Bus a. Apply Fault at the J488 COL2 34.500 (621002) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to DAKOTA RNG (621000) 345.0 kV Transmission Circuit #1 b.3. DAKOTA RNG (621000) 345.0 kV to J488 COL1 (621001) 34.5 kV Two Winding #1 b.4. J488 COL1 (621001) 34.5 kV to J488 COL2 (621002) 34.5 kV Transmission Circuit #1 b.5. J488 COL2 (621002) 34.5 kV to J488 G (621003) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. DEUEL CO 3 (620480) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.3. DEUEL CO 3 (620480) 345.0 kV to J526 SUB (621480) 345.0 kV Transmission Circuit #1 b.4. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply Fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 b.3. PEACE GARD 9 (606093) 34.5 kV to PEACE GARD 5 (602057) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. DEUEL CO 3 (620480) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.3. DEUEL CO 3 (620480) 345.0 kV to J526 SUB (621480) 345.0 kV Transmission Circuit #1 b.4. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on LAKE PARK T4230.00 (620337) 230 kV Bus a. Apply Fault at the LAKE PARK T4230.00 (620337) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to LAKE PARK T4 (620337) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.3. AUDUBON4 (620336) 230.0 kV to LAKE PARK T4 (620337) 230.0 kV Transmission Circuit #1 b.4. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE6 9 (605730) 13.8 kV Three Winding #6 b.7. LAKE PARK T4 (620337) 230.0 kV to LAKEPK 8 (657275) 69.0 kV to LAKEPK 9 (657781) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-RAMSEY 4 (615335) 230.0 kV to GRE-RMSYCB14 (615907) 230.0 kV Transmission Circuit #z b.2. GRE-RMSYCB14 (615907) 230.0 kV to GRE-RMSYCB24 (615908) 230.0 kV Transmission Circuit #z b.3. GRE-RMSYCB24 (615908) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on GLENBOR4 230.00 (667052) 230 kV Bus a. Apply Fault at the GLENBOR4 230.00 (667052) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 b.2. GLENBOR4 (667052) 230.0 kV to GLENBOR8 (668405) 65.1 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply Fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARIETT7 (620213) 115.0 kV to BIGSTON7 (620214) 115.0 kV Transmission Circuit #1 b.2. BIGSTON7 (620214) 115.0 kV to HIWY12 7 (620215) 115.0 kV Transmission Circuit #1 b.3. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. BIGSTON7 (620214) 115.0 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #1 b.5. BIGSTON7 (620214) 115.0 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #2 b.6. BIGSTON9 (620316) 13.8 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV Three Winding #1 b.7. BIGSTON9 (620316) 13.8 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.5. TIOGA4 7 (661085) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.3. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on J2086 SUB 345.00 (50863) 345 kV Bus a. Apply Fault at the J2086 SUB 345.00 (50863) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J2086 SUB (50863) 345.0 kV to J2086 COL (50862) 34.5 kV to J2086 T (50865) 13.8 kV Three Winding #1 b.2. J2086 SUB (50863) 345.0 kV to J2086 COL (50862) 34.5 kV to J2086 T (50864) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to BRKNGCO3 (601031) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 4 (620363) 230.0 kV to OAKES 4 (620362) 230.0 kV Transmission Circuit #1 b.2. FORMAN 4 (620363) 230.0 kV to HANKSON4 (620327) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to WAYSIDE4 (640404) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV to MPC4300 POI (657110) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451-RAUN 3 (645551) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLT RK3 (601006) 345.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.2. SPLT RK7 (603016) 115.0 kV to SPLT RK3 (601006) 345.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to CSLTNET7 (620180) 115.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 b.2. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE7 (652412) 115.0 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 b.2. MI CTYE7 (652412) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 7 (652436) 115.0 kV to FARGO 8 (652203) 69.0 kV Two Winding #2 b.2. FARGO 7 (652436) 115.0 kV to FARGO 4 (652435) 230.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.2. NUNDRWD7 (652485) 115.0 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 7 (652538) 115.0 kV to WHITE 3 (652537) 345.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 b.2. WHITE 7 (652538) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 b.2. PRAIRIE4 (657755) 230.0 kV to GRNDFKS4 (652437) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_UMZ_FAULT_001 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_UMZ_FAULT_002 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_UMZ_FAULT_003 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 b.2. CCR.KV4A-BE9 (659319) 13.8 kV to remove bus # b.3. CCR.KV3A-BE9 (659318) 13.8 kV to remove bus # b.4. CHARL_CK-BE4 (659302) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Transfer | GROUP1_P4_UMZ_FAULT_004 | Single Phase Fault with Stuck Breaker on JDS 345 (659333) 345 kV Bus a. Apply Fault at the JDS 345 (659333) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to remove bus # b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_002 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_004 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_005 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_006 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_007 | 3 Phase fault on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_008 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Two Winding #1 b.5. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_009 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_010 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_011 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_012 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_013 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_014 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_015 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_016 | 3 Phase fault on FARMVL_T-MW7115.00 (655943) 115 kV Bus a. Apply fault at the FARMVL_T-MW7115.00 (655943) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.2. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.3. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.5. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.6. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.7. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_017 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 b.2. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 b.3. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_018 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_019 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_020 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_021 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_022 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_023 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_025 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_026 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_027 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_028 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_029 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_030 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_031 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_032 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_033 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_034 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_035 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_036 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_037 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_038 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_039 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_040 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_041 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_042 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_043 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_044 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_045 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_046 | 3 Phase fault on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VEEDER -MK7 (655849) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_047 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_050 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_051 | 3 Phase fault on DPLWC___-MK7115.00 (655875) 115 kV Bus a. Apply fault at the DPLWC___-MK7115.00 (655875) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWC___-MK7 (655875) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_052 | 3 Phase fault on DPLWCTAP-MK7115.00 (655876) 115 kV Bus a. Apply fault at the DPLWCTAP-MK7115.00 (655876) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWCTAP-MK7 (655876) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_053 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to COYOTCHR-MK7 (655897) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_054 | 3 Phase fault on DAP_____-MK7115.00 (655881) 115 kV Bus a. Apply fault at the DAP_____-MK7115.00 (655881) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAP_____-MK7 (655881) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_055 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_056 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_057 | 3 Phase fault on FNCYBTAP-MK7115.00 (655899) 115 kV Bus a. Apply fault at the FNCYBTAP-MK7115.00 (655899) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNCYBTAP-MK7 (655899) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_058 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_059 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_060 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_063 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_064 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_065 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_066 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_067 | 3 Phase fault on N.WILSTN-MW7115.00 (655936) 115 kV Bus a. Apply fault at the N.WILSTN-MW7115.00 (655936) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to SE.WLSTN-MW7 (655938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_069 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_070 | 3 Phase fault on SE.WLSTN-MW7115.00 (655938) 115 kV Bus a. Apply fault at the SE.WLSTN-MW7115.00 (655938) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_071 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_072 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_073 | 3 Phase fault on ELLISVIL-MW7115.00 (655954) 115 kV Bus a. Apply fault at the ELLISVIL-MW7115.00 (655954) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_074 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_075 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_076 | 3 Phase fault on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_077 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_078 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_079 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_080 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_081 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_082 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_083 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_084 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_085 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_086 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_087 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_088 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_089 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_090 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_091 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_092 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_093 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_094 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_095 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_096 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_097 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_098 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_099 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_101 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_102 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_103 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_104 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_105 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_106 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_107 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_108 | 3 Phase fault on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_109 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_110 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_111 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_112 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_113 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_114 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_115 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_116 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_117 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_118 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_119 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_120 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_121 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_122 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_123 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_124 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_125 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_126 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_127 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_001 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_002 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_004 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_005 | 3 Phase fault on BISON 3 345.00 (601067) 345 kV Bus a. Apply fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_007 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_009 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_010 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_016 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_017 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_020 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_021 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_022 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597) and G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_023 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_024 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_025 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_026 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_028 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_029 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_030 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_031 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_032 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_033 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_035 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_036 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_037 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_041 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_050 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_051 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_052 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_053 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_057 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_058 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_059 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_060 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_062 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_063 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.5. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 b.3. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 b.4. CCR.KV3A-BE9 (659318) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #1 b.5. CCR.KV4A-BE9 (659319) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.4. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.4. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.4. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on LTLMUDY7 115.00 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 115.00 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply Fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.9. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 b.10. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply Fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON -MW7 (655925) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #1 b.2. JUDSON -MW7 (655925) 115.0 kV to STATELIN-MW7 (655924) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply Fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.2. NE.WLSTN-MW7 (655937) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply Fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. PATENTGT-BE3 (659390) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 b.2. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EFORK_-BE334 (659600) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE4 (659334) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. JUDSON__-BE4 (659334) 230.0 kV to JUDSON__-BE3 (659333) 345.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on FOLVAG -MW7115.00 (655958) 115 kV Bus a. Apply Fault at the FOLVAG -MW7115.00 (655958) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLVAG -MW7 (655958) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.2. FOLVAG -MW7 (655958) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GEN-2022-009345.00 (767161) 345 kV Bus a. Apply Fault at the GEN-2022-009345.00 (767161) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-009 (767161) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-009 (767161) 345.0 kV to G22-009GEN1 (767162) 13.8 kV to G22-009GEN2 (767163) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GEN-2020-091345.00 (764225) 345 kV Bus a. Apply Fault at the GEN-2020-091345.00 (764225) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-091 (764225) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-091 (764225) 345.0 kV to G20-091-XFM1 (764228) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU17A-BE7 (659466) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. PG.KU17A-BE7 (659466) 115.0 kV to PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU19A-BE7 (659467) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. PG.KU19A-BE7 (659467) 115.0 kV to PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply Fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE4 (659337) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. TANDE___-BE4 (659337) 230.0 kV to TANDE___-BE3 (659336) 345.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 b.2. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EASTFORK-MW7 (655957) 115.0 kV to N.MISRDG-MW7 (655933) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7 (659391) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on EFORK_-BE334 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334 (659600) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on EASTFORK-MW7 (655957) 115 kV Bus a. Apply Fault at the EASTFORK-MW7 (655957) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WILLISTON27 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 (652391) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on JUDSON -MW7 (655925) 115 kV Bus a. Apply Fault at the JUDSON -MW7 (655925) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. JUDSON -MW7 (655925) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on WILISTN4 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 (652400) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J2250 SUB (52503) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.3. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.4. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.5. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.6. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.7. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.8. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.9. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.11. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.12. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.14. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.15. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.17. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.19. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.20. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.21. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.23. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.25. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.2. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4230.00 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4230.00 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.8. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.9. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.10. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.11. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.2. PAYNES 4 (602036) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRE-WILLMAR8 (619977) 69.0 kV to GRE-WILLMR2T (619979) 12.5 kV Three Winding #1 b.4. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. GRANITF9 (652297) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.7. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. HRDLKCOL9 (620114) 34.5 kV to G380 RUGBY W (620115) 0.6 kV Two Winding #1 b.3. HRDLKCOL9 (620114) 34.5 kV to RGBYCOL9 (620168) 34.5 kV Transmission Circuit #1 b.4. RGBYWND4 (620368) 230.0 kV to RGBYCOL9 (620168) 34.5 kV Two Winding #1 b.5. RGBYWND4 (620368) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. RUGBY T (620179) 13.8 kV to RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.2. WINGER 4 (657758) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 b.4. WALLE 4 (657761) 230.0 kV to WALLE 8 (657316) 69.0 kV to WALLE 9 (657782) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on J526 SUB 345.00 (621480) 345 kV Bus a. Apply Fault at the J526 SUB 345.00 (621480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. DEUEL CO 3 (620480) 345.0 kV to J526 SUB (621480) 345.0 kV Transmission Circuit #1 b.3. J526 COL (621010) 34.5 kV to J526 FDR1 (621011) 34.5 kV Transmission Circuit #1 b.4. J526 FDR1 (621011) 34.5 kV to J526 G (621012) 0.7 kV Two Winding #1 b.5. J526 COL2 (621013) 34.5 kV to J526 FDR2 (621014) 34.5 kV Transmission Circuit #1 b.6. J526 FDR2 (621014) 34.5 kV to J526 G2 (621015) 0.7 kV Two Winding #1 b.7. J526 SUB (621480) 345.0 kV to J526 COL (621010) 34.5 kV Two Winding #1 b.8. J526 SUB (621480) 345.0 kV to J526 COL2 (621013) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply Fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BIGSTN1G (620315) 24.0 kV Two Winding #1 b.2. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAHPETN4 (620329) 230.0 kV to WAHPETN7 (620229) 115.0 kV to WAHPETN9 (620129) 41.6 kV Three Winding #2 b.2. HANKSON4 (620327) 230.0 kV to WAHPETN4 (620329) 230.0 kV Transmission Circuit #1 b.3. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to ALICE 7 (620259) 115.0 kV Transmission Circuit #1 b.2. ALICE 7 (620259) 115.0 kV to ENDERLN7 (620260) 115.0 kV Transmission Circuit #1 b.3. ENDERLN7 (620260) 115.0 kV to LISBON 7 (620261) 115.0 kV Transmission Circuit #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 41.6 kV Transmission Circuit #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.6. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.7. NEW EFFNGTN4 (620328) 230.0 kV to NEW EFFNGTN9 (620128) 41.6 kV Two Winding #1 b.8. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.9. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.4. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on MAPLE R3 345.00 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 345.00 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.5. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.6. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.7. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.8. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.9. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.10. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.11. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.12. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.13. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.14. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.15. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.16. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.17. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.18. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.19. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.20. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.21. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 b.23. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.24. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.2. WINGER 4 (657758) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.4. WALLE 4 (657761) 230.0 kV to WALLE 8 (657316) 69.0 kV to WALLE 9 (657782) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.3. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.4. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on GLENBOR4 230.00 (667052) 230 kV Bus a. Apply Fault at the GLENBOR4 230.00 (667052) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 b.2. GLENBOR4 (667052) 230.0 kV to GLENBOR8 (668405) 65.1 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on J436 COL 34.500 (620096) 34.5 kV Bus a. Apply Fault at the J436 COL 34.500 (620096) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to DAKOTA RNG 3 (620418) 345.0 kV Transmission Circuit #1 b.3. J437 COL (620098) 34.5 kV to DAKOTA RNG 3 (620418) 345.0 kV Two Winding #1 b.4. J437 COL (620098) 34.5 kV to J437 FDR (620099) 34.5 kV Transmission Circuit #1 b.5. J437 COL (620098) 34.5 kV to J437 DVAR (620095) 0.5 kV Two Winding #1 b.6. J437 FDR (620099) 34.5 kV to J437 DK RNG2 (620995) 0.6 kV Two Winding #1 b.7. J436 COL (620096) 34.5 kV to DAKOTA RNG 3 (620418) 345.0 kV Two Winding #1 b.8. J436 COL (620096) 34.5 kV to J436 DVAR (620094) 0.5 kV Two Winding #1 b.9. J436 COL (620096) 34.5 kV to J436 FDR (620097) 34.5 kV Transmission Circuit #1 b.10. J436 COL (620096) 34.5 kV to J436 DK RNG1 (620102) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.3. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.4. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.5. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on ALXLNRCTRT 345.00 (658049) 345 kV Bus a. Apply Fault at the ALXLNRCTRT 345.00 (658049) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to ALXLNRCTRT (658049) 345.0 kV Transmission Circuit #1 b.3. ALEXMRES3 (658047) 345.0 kV to ALXLNRCTRT (658049) 345.0 kV Transmission Circuit #z1 b.4. ALXLNRCTRT (658049) 345.0 kV to ALXLNRCTR (658201) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRA TR7 9 (605746) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #7 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRA TR7 9 (605746) 13.8 kV Three Winding #7 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on ELN345SHNT 3345.00 (661950) 345 kV Bus a. Apply Fault at the ELN345SHNT 3345.00 (661950) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1989 POI (49894) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 b.2. J1990 SUB (49903) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 b.3. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.4. ELLENDL345 3 (661097) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on J488 COL2 34.500 (621002) 34.5 kV Bus a. Apply Fault at the J488 COL2 34.500 (621002) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to DAKOTA RNG (621000) 345.0 kV Transmission Circuit #1 b.3. DAKOTA RNG (621000) 345.0 kV to J488 COL1 (621001) 34.5 kV Two Winding #1 b.4. J488 COL1 (621001) 34.5 kV to J488 COL2 (621002) 34.5 kV Transmission Circuit #1 b.5. J488 COL2 (621002) 34.5 kV to J488 G (621003) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. DEUEL CO 3 (620480) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.3. DEUEL CO 3 (620480) 345.0 kV to J526 SUB (621480) 345.0 kV Transmission Circuit #1 b.4. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply Fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 b.3. PEACE GARD 9 (606093) 34.5 kV to PEACE GARD 5 (602057) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. DEUEL CO 3 (620480) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.3. DEUEL CO 3 (620480) 345.0 kV to J526 SUB (621480) 345.0 kV Transmission Circuit #1 b.4. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on LAKE PARK T4230.00 (620337) 230 kV Bus a. Apply Fault at the LAKE PARK T4230.00 (620337) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to LAKE PARK T4 (620337) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.3. AUDUBON4 (620336) 230.0 kV to LAKE PARK T4 (620337) 230.0 kV Transmission Circuit #1 b.4. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE6 9 (605730) 13.8 kV Three Winding #6 b.7. LAKE PARK T4 (620337) 230.0 kV to LAKEPK 8 (657275) 69.0 kV to LAKEPK 9 (657781) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-RAMSEY 4 (615335) 230.0 kV to GRE-RMSYCB14 (615907) 230.0 kV Transmission Circuit #z b.2. GRE-RMSYCB14 (615907) 230.0 kV to GRE-RMSYCB24 (615908) 230.0 kV Transmission Circuit #z b.3. GRE-RMSYCB24 (615908) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on GLENBOR4 230.00 (667052) 230 kV Bus a. Apply Fault at the GLENBOR4 230.00 (667052) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 b.2. GLENBOR4 (667052) 230.0 kV to GLENBOR8 (668405) 65.1 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply Fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARIETT7 (620213) 115.0 kV to BIGSTON7 (620214) 115.0 kV Transmission Circuit #1 b.2. BIGSTON7 (620214) 115.0 kV to HIWY12 7 (620215) 115.0 kV Transmission Circuit #1 b.3. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. BIGSTON7 (620214) 115.0 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #1 b.5. BIGSTON7 (620214) 115.0 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #2 b.6. BIGSTON9 (620316) 13.8 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV Three Winding #1 b.7. BIGSTON9 (620316) 13.8 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.5. TIOGA4 7 (661085) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.3. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on J2086 SUB 345.00 (50863) 345 kV Bus a. Apply Fault at the J2086 SUB 345.00 (50863) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J2086 SUB (50863) 345.0 kV to J2086 COL (50862) 34.5 kV to J2086 T (50865) 13.8 kV Three Winding #1 b.2. J2086 SUB (50863) 345.0 kV to J2086 COL (50862) 34.5 kV to J2086 T (50864) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to BRKNGCO3 (601031) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 4 (620363) 230.0 kV to OAKES 4 (620362) 230.0 kV Transmission Circuit #1 b.2. FORMAN 4 (620363) 230.0 kV to HANKSON4 (620327) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to WAYSIDE4 (640404) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV to MPC4300 POI (657110) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451-RAUN 3 (645551) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLT RK3 (601006) 345.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.2. SPLT RK7 (603016) 115.0 kV to SPLT RK3 (601006) 345.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to CSLTNET7 (620180) 115.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 b.2. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE7 (652412) 115.0 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 b.2. MI CTYE7 (652412) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 7 (652436) 115.0 kV to FARGO 8 (652203) 69.0 kV Two Winding #2 b.2. FARGO 7 (652436) 115.0 kV to FARGO 4 (652435) 230.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.2. NUNDRWD7 (652485) 115.0 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-014 (588593 and 588597). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 7 (652538) 115.0 kV to WHITE 3 (652537) 345.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 b.2. WHITE 7 (652538) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 b.2. PRAIRIE4 (657755) 230.0 kV to GRNDFKS4 (652437) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_UMZ_FAULT_001 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_UMZ_FAULT_002 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_UMZ_FAULT_003 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 b.2. CCR.KV4A-BE9 (659319) 13.8 kV to remove bus # b.3. CCR.KV3A-BE9 (659318) 13.8 kV to remove bus # b.4. CHARL_CK-BE4 (659302) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25W | Transfer | GROUP1_P4_UMZ_FAULT_004 | Single Phase Fault with Stuck Breaker on JDS 345 (659333) 345 kV Bus a. Apply Fault at the JDS 345 (659333) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to remove bus # b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_002 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_004 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_005 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_006 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_007 | 3 Phase fault on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_008 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Two Winding #1 b.5. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_009 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_010 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_011 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_012 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_013 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_014 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_015 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_016 | 3 Phase fault on FARMVL_T-MW7115.00 (655943) 115 kV Bus a. Apply fault at the FARMVL_T-MW7115.00 (655943) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.2. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.3. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.5. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.6. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.7. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_017 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 b.2. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 b.3. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_018 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_019 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_020 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_021 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_022 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_023 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_025 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_026 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_027 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_028 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_029 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_030 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_031 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_032 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_033 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_034 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_035 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_036 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_037 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_038 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_039 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_040 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_041 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_042 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_043 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_044 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_045 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_046 | 3 Phase fault on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VEEDER -MK7 (655849) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_047 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_050 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_051 | 3 Phase fault on DPLWC___-MK7115.00 (655875) 115 kV Bus a. Apply fault at the DPLWC___-MK7115.00 (655875) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWC___-MK7 (655875) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_052 | 3 Phase fault on DPLWCTAP-MK7115.00 (655876) 115 kV Bus a. Apply fault at the DPLWCTAP-MK7115.00 (655876) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWCTAP-MK7 (655876) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_053 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to COYOTCHR-MK7 (655897) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_054 | 3 Phase fault on DAP_____-MK7115.00 (655881) 115 kV Bus a. Apply fault at the DAP_____-MK7115.00 (655881) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAP_____-MK7 (655881) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_055 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_056 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_057 | 3 Phase fault on FNCYBTAP-MK7115.00 (655899) 115 kV Bus a. Apply fault at the FNCYBTAP-MK7115.00 (655899) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNCYBTAP-MK7 (655899) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_058 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_059 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_060 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | PS_RCP-BEG (659431 and 659432) losses synchronism following fault clearance. | Reduce clearing time to 4 cycles per Transmission Owner indicated clearing time.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_063 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_064 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_065 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_066 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_067 | 3 Phase fault on N.WILSTN-MW7115.00 (655936) 115 kV Bus a. Apply fault at the N.WILSTN-MW7115.00 (655936) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to SE.WLSTN-MW7 (655938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_069 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_070 | 3 Phase fault on SE.WLSTN-MW7115.00 (655938) 115 kV Bus a. Apply fault at the SE.WLSTN-MW7115.00 (655938) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_071 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_072 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_073 | 3 Phase fault on ELLISVIL-MW7115.00 (655954) 115 kV Bus a. Apply fault at the ELLISVIL-MW7115.00 (655954) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_074 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_075 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_076 | 3 Phase fault on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_077 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_078 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_079 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_080 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_081 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_082 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_083 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_084 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_085 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_086 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_087 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G17-048 (588873 and 588876). | 1. Operational measures (tap points/voltage setpoints/etc.) 2. Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_088 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_089 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_090 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_091 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_092 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | GEN-2022-009 (767162 and 767163) becomes unstable following fault clearance. | Reduce clearing time to 4 cycles per Transmission Owner indicated clearing time.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_093 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_094 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_095 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_096 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_097 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_098 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_099 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_101 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_102 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_103 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_104 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_105 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_106 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_107 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_108 | 3 Phase fault on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_109 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_110 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_111 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_112 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_113 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_114 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_115 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_116 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_117 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_118 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_119 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_120 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_121 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_122 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_123 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_124 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_125 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_126 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_127 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_001 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_002 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_004 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_005 | 3 Phase fault on BISON 3 345.00 (601067) 345 kV Bus a. Apply fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_007 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_009 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_010 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_016 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_017 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_020 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_021 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_022 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_023 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_024 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_025 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_026 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_028 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_029 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_030 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_031 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_032 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_033 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_035 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_036 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_037 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_041 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_050 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_051 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_052 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G17-048 (588873 and 588876). | 1. Operational measures (tap points/voltage setpoints/etc.) 2. Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_053 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_057 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_058 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_059 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_060 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_062 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_063 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.5. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 b.3. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 b.4. CCR.KV3A-BE9 (659318) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #1 b.5. CCR.KV4A-BE9 (659319) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.4. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.4. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.4. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on LTLMUDY7 115.00 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 115.00 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply Fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.9. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 b.10. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply Fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON -MW7 (655925) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #1 b.2. JUDSON -MW7 (655925) 115.0 kV to STATELIN-MW7 (655924) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply Fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.2. NE.WLSTN-MW7 (655937) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply Fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. PATENTGT-BE3 (659390) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 b.2. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EFORK_-BE334 (659600) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE4 (659334) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. JUDSON__-BE4 (659334) 230.0 kV to JUDSON__-BE3 (659333) 345.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on FOLVAG -MW7115.00 (655958) 115 kV Bus a. Apply Fault at the FOLVAG -MW7115.00 (655958) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLVAG -MW7 (655958) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.2. FOLVAG -MW7 (655958) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GEN-2022-009345.00 (767161) 345 kV Bus a. Apply Fault at the GEN-2022-009345.00 (767161) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-009 (767161) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-009 (767161) 345.0 kV to G22-009GEN1 (767162) 13.8 kV to G22-009GEN2 (767163) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GEN-2020-091345.00 (764225) 345 kV Bus a. Apply Fault at the GEN-2020-091345.00 (764225) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-091 (764225) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-091 (764225) 345.0 kV to G20-091-XFM1 (764228) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU17A-BE7 (659466) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. PG.KU17A-BE7 (659466) 115.0 kV to PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU19A-BE7 (659467) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. PG.KU19A-BE7 (659467) 115.0 kV to PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply Fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE4 (659337) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. TANDE___-BE4 (659337) 230.0 kV to TANDE___-BE3 (659336) 345.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 b.2. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EASTFORK-MW7 (655957) 115.0 kV to N.MISRDG-MW7 (655933) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7 (659391) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on EFORK_-BE334 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334 (659600) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on EASTFORK-MW7 (655957) 115 kV Bus a. Apply Fault at the EASTFORK-MW7 (655957) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WILLISTON27 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 (652391) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on JUDSON -MW7 (655925) 115 kV Bus a. Apply Fault at the JUDSON -MW7 (655925) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. JUDSON -MW7 (655925) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on WILISTN4 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 (652400) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J2250 SUB (52503) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.3. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.4. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.5. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.6. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.7. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.8. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.9. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.11. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.12. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.14. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.15. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.17. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.19. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.20. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.21. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.23. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.25. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.2. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4230.00 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4230.00 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.8. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.9. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.10. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.11. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.2. PAYNES 4 (602036) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRE-WILLMAR8 (619977) 69.0 kV to GRE-WILLMR2T (619979) 12.5 kV Three Winding #1 b.4. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. GRANITF9 (652297) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.7. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. HRDLKCOL9 (620114) 34.5 kV to G380 RUGBY W (620115) 0.6 kV Two Winding #1 b.3. HRDLKCOL9 (620114) 34.5 kV to RGBYCOL9 (620168) 34.5 kV Transmission Circuit #1 b.4. RGBYWND4 (620368) 230.0 kV to RGBYCOL9 (620168) 34.5 kV Two Winding #1 b.5. RGBYWND4 (620368) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. RUGBY T (620179) 13.8 kV to RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.2. WINGER 4 (657758) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 b.4. WALLE 4 (657761) 230.0 kV to WALLE 8 (657316) 69.0 kV to WALLE 9 (657782) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on J526 SUB 345.00 (621480) 345 kV Bus a. Apply Fault at the J526 SUB 345.00 (621480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. DEUEL CO 3 (620480) 345.0 kV to J526 SUB (621480) 345.0 kV Transmission Circuit #1 b.3. J526 COL (621010) 34.5 kV to J526 FDR1 (621011) 34.5 kV Transmission Circuit #1 b.4. J526 FDR1 (621011) 34.5 kV to J526 G (621012) 0.7 kV Two Winding #1 b.5. J526 COL2 (621013) 34.5 kV to J526 FDR2 (621014) 34.5 kV Transmission Circuit #1 b.6. J526 FDR2 (621014) 34.5 kV to J526 G2 (621015) 0.7 kV Two Winding #1 b.7. J526 SUB (621480) 345.0 kV to J526 COL (621010) 34.5 kV Two Winding #1 b.8. J526 SUB (621480) 345.0 kV to J526 COL2 (621013) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply Fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BIGSTN1G (620315) 24.0 kV Two Winding #1 b.2. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAHPETN4 (620329) 230.0 kV to WAHPETN7 (620229) 115.0 kV to WAHPETN9 (620129) 41.6 kV Three Winding #2 b.2. HANKSON4 (620327) 230.0 kV to WAHPETN4 (620329) 230.0 kV Transmission Circuit #1 b.3. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to ALICE 7 (620259) 115.0 kV Transmission Circuit #1 b.2. ALICE 7 (620259) 115.0 kV to ENDERLN7 (620260) 115.0 kV Transmission Circuit #1 b.3. ENDERLN7 (620260) 115.0 kV to LISBON 7 (620261) 115.0 kV Transmission Circuit #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 41.6 kV Transmission Circuit #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.6. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.7. NEW EFFNGTN4 (620328) 230.0 kV to NEW EFFNGTN9 (620128) 41.6 kV Two Winding #1 b.8. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.9. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.4. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on MAPLE R3 345.00 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 345.00 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.5. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.6. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.7. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.8. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.9. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.10. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.11. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.12. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.13. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.14. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.15. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.16. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.17. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.18. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.19. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.20. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.21. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 b.23. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.24. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.2. WINGER 4 (657758) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.4. WALLE 4 (657761) 230.0 kV to WALLE 8 (657316) 69.0 kV to WALLE 9 (657782) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.3. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.4. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on GLENBOR4 230.00 (667052) 230 kV Bus a. Apply Fault at the GLENBOR4 230.00 (667052) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 b.2. GLENBOR4 (667052) 230.0 kV to GLENBOR8 (668405) 65.1 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on J436 COL 34.500 (620096) 34.5 kV Bus a. Apply Fault at the J436 COL 34.500 (620096) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to DAKOTA RNG 3 (620418) 345.0 kV Transmission Circuit #1 b.3. J437 COL (620098) 34.5 kV to DAKOTA RNG 3 (620418) 345.0 kV Two Winding #1 b.4. J437 COL (620098) 34.5 kV to J437 FDR (620099) 34.5 kV Transmission Circuit #1 b.5. J437 COL (620098) 34.5 kV to J437 DVAR (620095) 0.5 kV Two Winding #1 b.6. J437 FDR (620099) 34.5 kV to J437 DK RNG2 (620995) 0.6 kV Two Winding #1 b.7. J436 COL (620096) 34.5 kV to DAKOTA RNG 3 (620418) 345.0 kV Two Winding #1 b.8. J436 COL (620096) 34.5 kV to J436 DVAR (620094) 0.5 kV Two Winding #1 b.9. J436 COL (620096) 34.5 kV to J436 FDR (620097) 34.5 kV Transmission Circuit #1 b.10. J436 COL (620096) 34.5 kV to J436 DK RNG1 (620102) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.3. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.4. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.5. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on ALXLNRCTRT 345.00 (658049) 345 kV Bus a. Apply Fault at the ALXLNRCTRT 345.00 (658049) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to ALXLNRCTRT (658049) 345.0 kV Transmission Circuit #1 b.3. ALEXMRES3 (658047) 345.0 kV to ALXLNRCTRT (658049) 345.0 kV Transmission Circuit #z1 b.4. ALXLNRCTRT (658049) 345.0 kV to ALXLNRCTR (658201) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRA TR7 9 (605746) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #7 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRA TR7 9 (605746) 13.8 kV Three Winding #7 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on ELN345SHNT 3345.00 (661950) 345 kV Bus a. Apply Fault at the ELN345SHNT 3345.00 (661950) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1989 POI (49894) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 b.2. J1990 SUB (49903) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 b.3. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.4. ELLENDL345 3 (661097) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on J488 COL2 34.500 (621002) 34.5 kV Bus a. Apply Fault at the J488 COL2 34.500 (621002) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to DAKOTA RNG (621000) 345.0 kV Transmission Circuit #1 b.3. DAKOTA RNG (621000) 345.0 kV to J488 COL1 (621001) 34.5 kV Two Winding #1 b.4. J488 COL1 (621001) 34.5 kV to J488 COL2 (621002) 34.5 kV Transmission Circuit #1 b.5. J488 COL2 (621002) 34.5 kV to J488 G (621003) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. DEUEL CO 3 (620480) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.3. DEUEL CO 3 (620480) 345.0 kV to J526 SUB (621480) 345.0 kV Transmission Circuit #1 b.4. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply Fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 b.3. PEACE GARD 9 (606093) 34.5 kV to PEACE GARD 5 (602057) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. DEUEL CO 3 (620480) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.3. DEUEL CO 3 (620480) 345.0 kV to J526 SUB (621480) 345.0 kV Transmission Circuit #1 b.4. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on LAKE PARK T4230.00 (620337) 230 kV Bus a. Apply Fault at the LAKE PARK T4230.00 (620337) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to LAKE PARK T4 (620337) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.3. AUDUBON4 (620336) 230.0 kV to LAKE PARK T4 (620337) 230.0 kV Transmission Circuit #1 b.4. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE6 9 (605730) 13.8 kV Three Winding #6 b.7. LAKE PARK T4 (620337) 230.0 kV to LAKEPK 8 (657275) 69.0 kV to LAKEPK 9 (657781) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-RAMSEY 4 (615335) 230.0 kV to GRE-RMSYCB14 (615907) 230.0 kV Transmission Circuit #z b.2. GRE-RMSYCB14 (615907) 230.0 kV to GRE-RMSYCB24 (615908) 230.0 kV Transmission Circuit #z b.3. GRE-RMSYCB24 (615908) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on GLENBOR4 230.00 (667052) 230 kV Bus a. Apply Fault at the GLENBOR4 230.00 (667052) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 b.2. GLENBOR4 (667052) 230.0 kV to GLENBOR8 (668405) 65.1 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply Fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARIETT7 (620213) 115.0 kV to BIGSTON7 (620214) 115.0 kV Transmission Circuit #1 b.2. BIGSTON7 (620214) 115.0 kV to HIWY12 7 (620215) 115.0 kV Transmission Circuit #1 b.3. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. BIGSTON7 (620214) 115.0 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #1 b.5. BIGSTON7 (620214) 115.0 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #2 b.6. BIGSTON9 (620316) 13.8 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV Three Winding #1 b.7. BIGSTON9 (620316) 13.8 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.5. TIOGA4 7 (661085) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.3. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on J2086 SUB 345.00 (50863) 345 kV Bus a. Apply Fault at the J2086 SUB 345.00 (50863) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J2086 SUB (50863) 345.0 kV to J2086 COL (50862) 34.5 kV to J2086 T (50865) 13.8 kV Three Winding #1 b.2. J2086 SUB (50863) 345.0 kV to J2086 COL (50862) 34.5 kV to J2086 T (50864) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to BRKNGCO3 (601031) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 4 (620363) 230.0 kV to OAKES 4 (620362) 230.0 kV Transmission Circuit #1 b.2. FORMAN 4 (620363) 230.0 kV to HANKSON4 (620327) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to WAYSIDE4 (640404) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV to MPC4300 POI (657110) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451-RAUN 3 (645551) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLT RK3 (601006) 345.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.2. SPLT RK7 (603016) 115.0 kV to SPLT RK3 (601006) 345.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to CSLTNET7 (620180) 115.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 b.2. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE7 (652412) 115.0 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 b.2. MI CTYE7 (652412) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 7 (652436) 115.0 kV to FARGO 8 (652203) 69.0 kV Two Winding #2 b.2. FARGO 7 (652436) 115.0 kV to FARGO 4 (652435) 230.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.2. NUNDRWD7 (652485) 115.0 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 7 (652538) 115.0 kV to WHITE 3 (652537) 345.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 b.2. WHITE 7 (652538) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 b.2. PRAIRIE4 (657755) 230.0 kV to GRNDFKS4 (652437) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_UMZ_FAULT_001 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_UMZ_FAULT_002 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_UMZ_FAULT_003 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 b.2. CCR.KV4A-BE9 (659319) 13.8 kV to remove bus # b.3. CCR.KV3A-BE9 (659318) 13.8 kV to remove bus # b.4. CHARL_CK-BE4 (659302) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25S | Transfer | GROUP1_P4_UMZ_FAULT_004 | Single Phase Fault with Stuck Breaker on JDS 345 (659333) 345 kV Bus a. Apply Fault at the JDS 345 (659333) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to remove bus # b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_002 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_004 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_005 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_006 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_007 | 3 Phase fault on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_008 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Two Winding #1 b.5. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_009 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_010 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_011 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_012 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_013 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_014 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_015 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_016 | 3 Phase fault on FARMVL_T-MW7115.00 (655943) 115 kV Bus a. Apply fault at the FARMVL_T-MW7115.00 (655943) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.2. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.3. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.5. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.6. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.7. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_017 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 b.2. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 b.3. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_018 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_019 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_020 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_021 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_022 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_023 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_025 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_026 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_027 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_028 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_029 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_030 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_031 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_032 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_033 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_034 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_035 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_036 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_037 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_038 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_039 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_040 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_041 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_042 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_043 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_044 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_045 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_046 | 3 Phase fault on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VEEDER -MK7 (655849) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_047 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_050 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_051 | 3 Phase fault on DPLWC___-MK7115.00 (655875) 115 kV Bus a. Apply fault at the DPLWC___-MK7115.00 (655875) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWC___-MK7 (655875) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_052 | 3 Phase fault on DPLWCTAP-MK7115.00 (655876) 115 kV Bus a. Apply fault at the DPLWCTAP-MK7115.00 (655876) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWCTAP-MK7 (655876) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_053 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to COYOTCHR-MK7 (655897) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_054 | 3 Phase fault on DAP_____-MK7115.00 (655881) 115 kV Bus a. Apply fault at the DAP_____-MK7115.00 (655881) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAP_____-MK7 (655881) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_055 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_056 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_057 | 3 Phase fault on FNCYBTAP-MK7115.00 (655899) 115 kV Bus a. Apply fault at the FNCYBTAP-MK7115.00 (655899) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNCYBTAP-MK7 (655899) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_058 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_059 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_060 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_063 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_064 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_065 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_066 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_067 | 3 Phase fault on N.WILSTN-MW7115.00 (655936) 115 kV Bus a. Apply fault at the N.WILSTN-MW7115.00 (655936) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to SE.WLSTN-MW7 (655938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_069 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_070 | 3 Phase fault on SE.WLSTN-MW7115.00 (655938) 115 kV Bus a. Apply fault at the SE.WLSTN-MW7115.00 (655938) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_071 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_072 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_073 | 3 Phase fault on ELLISVIL-MW7115.00 (655954) 115 kV Bus a. Apply fault at the ELLISVIL-MW7115.00 (655954) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_074 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_075 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_076 | 3 Phase fault on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_077 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_078 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_079 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_080 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_081 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_082 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_083 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_084 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_085 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_086 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_087 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G17-048 (588873 and 588876). | 1. Operational measures (tap points/voltage setpoints/etc.) 2. Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_088 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_089 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_090 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_091 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_092 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | GEN-2022-009 (767162 and 767163) becomes unstable following fault clearance. | Reduce clearing time to 4 cycles per Transmission Owner indicated clearing time.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_093 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_094 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_095 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_096 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_097 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_098 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_099 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_101 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_102 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_103 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_104 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_105 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_106 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_107 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_108 | 3 Phase fault on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_109 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_110 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_111 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_112 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_113 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_114 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_115 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_116 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_117 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_118 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_119 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_120 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_121 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_122 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_123 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_124 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_125 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_126 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_127 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_001 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_002 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_004 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_005 | 3 Phase fault on BISON 3 345.00 (601067) 345 kV Bus a. Apply fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_007 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_009 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_010 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_016 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_017 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_020 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_021 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_022 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_023 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_024 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_025 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_026 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_028 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_029 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_030 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_031 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_032 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_033 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_035 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_036 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_037 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_041 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_050 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_051 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_052 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | No | Yes | No | Voltage protection trips G17-048 (588873 and 588876). | 1. Operational measures (tap points/voltage setpoints/etc.) 2. Protection disabled with no impact to stability.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_053 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_057 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_058 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_059 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_060 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_062 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_063 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.5. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 b.3. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 b.4. CCR.KV3A-BE9 (659318) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #1 b.5. CCR.KV4A-BE9 (659319) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.4. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.4. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.4. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on LTLMUDY7 115.00 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 115.00 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply Fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.9. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 b.10. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply Fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON -MW7 (655925) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #1 b.2. JUDSON -MW7 (655925) 115.0 kV to STATELIN-MW7 (655924) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply Fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.2. NE.WLSTN-MW7 (655937) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply Fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply Fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. PATENTGT-BE3 (659390) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 b.2. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EFORK_-BE334 (659600) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE4 (659334) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. JUDSON__-BE4 (659334) 230.0 kV to JUDSON__-BE3 (659333) 345.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on FOLVAG -MW7115.00 (655958) 115 kV Bus a. Apply Fault at the FOLVAG -MW7115.00 (655958) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLVAG -MW7 (655958) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.2. FOLVAG -MW7 (655958) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GEN-2022-009345.00 (767161) 345 kV Bus a. Apply Fault at the GEN-2022-009345.00 (767161) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-009 (767161) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-009 (767161) 345.0 kV to G22-009GEN1 (767162) 13.8 kV to G22-009GEN2 (767163) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GEN-2020-091345.00 (764225) 345 kV Bus a. Apply Fault at the GEN-2020-091345.00 (764225) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-091 (764225) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-091 (764225) 345.0 kV to G20-091-XFM1 (764228) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU17A-BE7 (659466) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. PG.KU17A-BE7 (659466) 115.0 kV to PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PG.KU19A-BE7 (659467) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. PG.KU19A-BE7 (659467) 115.0 kV to PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply Fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE4 (659337) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. TANDE___-BE4 (659337) 230.0 kV to TANDE___-BE3 (659336) 345.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 b.2. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EASTFORK-MW7 (655957) 115.0 kV to N.MISRDG-MW7 (655933) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7 (659391) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on EFORK_-BE334 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334 (659600) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on EASTFORK-MW7 (655957) 115 kV Bus a. Apply Fault at the EASTFORK-MW7 (655957) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WILLISTON27 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 (652391) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on JUDSON -MW7 (655925) 115 kV Bus a. Apply Fault at the JUDSON -MW7 (655925) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. JUDSON -MW7 (655925) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on WILISTN4 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 (652400) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J2250 SUB (52503) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.3. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.4. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.5. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.6. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.7. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.8. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.9. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.11. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.12. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.14. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.15. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.17. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.19. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.20. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.21. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.23. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.25. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on EXIRA 5 161.00 (652603) 161 kV Bus a. Apply Fault at the EXIRA 5 161.00 (652603) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.3. EXIRA 5 (652603) 161.0 kV to EXIRA 1G (658000) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.2. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4230.00 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4230.00 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.8. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.9. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.10. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.11. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.2. PAYNES 4 (602036) 230.0 kV to GRE-WILLMAR4 (619975) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRE-WILLMAR8 (619977) 69.0 kV to GRE-WILLMR2T (619979) 12.5 kV Three Winding #1 b.4. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. GRANITF9 (652297) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.7. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. HRDLKCOL9 (620114) 34.5 kV to G380 RUGBY W (620115) 0.6 kV Two Winding #1 b.3. HRDLKCOL9 (620114) 34.5 kV to RGBYCOL9 (620168) 34.5 kV Transmission Circuit #1 b.4. RGBYWND4 (620368) 230.0 kV to RGBYCOL9 (620168) 34.5 kV Two Winding #1 b.5. RGBYWND4 (620368) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. RUGBY T (620179) 13.8 kV to RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.2. WINGER 4 (657758) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 b.4. WALLE 4 (657761) 230.0 kV to WALLE 8 (657316) 69.0 kV to WALLE 9 (657782) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on J526 SUB 345.00 (621480) 345 kV Bus a. Apply Fault at the J526 SUB 345.00 (621480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. DEUEL CO 3 (620480) 345.0 kV to J526 SUB (621480) 345.0 kV Transmission Circuit #1 b.3. J526 COL (621010) 34.5 kV to J526 FDR1 (621011) 34.5 kV Transmission Circuit #1 b.4. J526 FDR1 (621011) 34.5 kV to J526 G (621012) 0.7 kV Two Winding #1 b.5. J526 COL2 (621013) 34.5 kV to J526 FDR2 (621014) 34.5 kV Transmission Circuit #1 b.6. J526 FDR2 (621014) 34.5 kV to J526 G2 (621015) 0.7 kV Two Winding #1 b.7. J526 SUB (621480) 345.0 kV to J526 COL (621010) 34.5 kV Two Winding #1 b.8. J526 SUB (621480) 345.0 kV to J526 COL2 (621013) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply Fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BIGSTN1G (620315) 24.0 kV Two Winding #1 b.2. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAHPETN4 (620329) 230.0 kV to WAHPETN7 (620229) 115.0 kV to WAHPETN9 (620129) 41.6 kV Three Winding #2 b.2. HANKSON4 (620327) 230.0 kV to WAHPETN4 (620329) 230.0 kV Transmission Circuit #1 b.3. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to ALICE 7 (620259) 115.0 kV Transmission Circuit #1 b.2. ALICE 7 (620259) 115.0 kV to ENDERLN7 (620260) 115.0 kV Transmission Circuit #1 b.3. ENDERLN7 (620260) 115.0 kV to LISBON 7 (620261) 115.0 kV Transmission Circuit #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 41.6 kV Transmission Circuit #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.6. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.7. NEW EFFNGTN4 (620328) 230.0 kV to NEW EFFNGTN9 (620128) 41.6 kV Two Winding #1 b.8. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.9. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.4. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on MAPLE R3 345.00 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 345.00 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.5. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.6. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.7. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.8. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.9. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.10. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.11. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.12. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.13. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.14. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.15. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.16. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.17. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.18. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.19. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.20. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.21. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 b.23. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.24. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.2. WINGER 4 (657758) 230.0 kV to WALLE 4 (657761) 230.0 kV Transmission Circuit #1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.4. WALLE 4 (657761) 230.0 kV to WALLE 8 (657316) 69.0 kV to WALLE 9 (657782) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.3. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.4. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on GLENBOR4 230.00 (667052) 230 kV Bus a. Apply Fault at the GLENBOR4 230.00 (667052) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 b.2. GLENBOR4 (667052) 230.0 kV to GLENBOR8 (668405) 65.1 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on J436 COL 34.500 (620096) 34.5 kV Bus a. Apply Fault at the J436 COL 34.500 (620096) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to DAKOTA RNG 3 (620418) 345.0 kV Transmission Circuit #1 b.3. J437 COL (620098) 34.5 kV to DAKOTA RNG 3 (620418) 345.0 kV Two Winding #1 b.4. J437 COL (620098) 34.5 kV to J437 FDR (620099) 34.5 kV Transmission Circuit #1 b.5. J437 COL (620098) 34.5 kV to J437 DVAR (620095) 0.5 kV Two Winding #1 b.6. J437 FDR (620099) 34.5 kV to J437 DK RNG2 (620995) 0.6 kV Two Winding #1 b.7. J436 COL (620096) 34.5 kV to DAKOTA RNG 3 (620418) 345.0 kV Two Winding #1 b.8. J436 COL (620096) 34.5 kV to J436 DVAR (620094) 0.5 kV Two Winding #1 b.9. J436 COL (620096) 34.5 kV to J436 FDR (620097) 34.5 kV Transmission Circuit #1 b.10. J436 COL (620096) 34.5 kV to J436 DK RNG1 (620102) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.3. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.4. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.5. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on ALXLNRCTRT 345.00 (658049) 345 kV Bus a. Apply Fault at the ALXLNRCTRT 345.00 (658049) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to ALXLNRCTRT (658049) 345.0 kV Transmission Circuit #1 b.3. ALEXMRES3 (658047) 345.0 kV to ALXLNRCTRT (658049) 345.0 kV Transmission Circuit #z1 b.4. ALXLNRCTRT (658049) 345.0 kV to ALXLNRCTR (658201) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRA TR7 9 (605746) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #7 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRA TR7 9 (605746) 13.8 kV Three Winding #7 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on ELN345SHNT 3345.00 (661950) 345 kV Bus a. Apply Fault at the ELN345SHNT 3345.00 (661950) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1989 POI (49894) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 b.2. J1990 SUB (49903) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 b.3. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.4. ELLENDL345 3 (661097) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on J488 COL2 34.500 (621002) 34.5 kV Bus a. Apply Fault at the J488 COL2 34.500 (621002) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to DAKOTA RNG (621000) 345.0 kV Transmission Circuit #1 b.3. DAKOTA RNG (621000) 345.0 kV to J488 COL1 (621001) 34.5 kV Two Winding #1 b.4. J488 COL1 (621001) 34.5 kV to J488 COL2 (621002) 34.5 kV Transmission Circuit #1 b.5. J488 COL2 (621002) 34.5 kV to J488 G (621003) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. DEUEL CO 3 (620480) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.3. DEUEL CO 3 (620480) 345.0 kV to J526 SUB (621480) 345.0 kV Transmission Circuit #1 b.4. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply Fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 b.3. PEACE GARD 9 (606093) 34.5 kV to PEACE GARD 5 (602057) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. DEUEL CO 3 (620480) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.3. DEUEL CO 3 (620480) 345.0 kV to J526 SUB (621480) 345.0 kV Transmission Circuit #1 b.4. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on LAKE PARK T4230.00 (620337) 230 kV Bus a. Apply Fault at the LAKE PARK T4230.00 (620337) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to LAKE PARK T4 (620337) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.3. AUDUBON4 (620336) 230.0 kV to LAKE PARK T4 (620337) 230.0 kV Transmission Circuit #1 b.4. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE6 9 (605730) 13.8 kV Three Winding #6 b.7. LAKE PARK T4 (620337) 230.0 kV to LAKEPK 8 (657275) 69.0 kV to LAKEPK 9 (657781) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-RAMSEY 4 (615335) 230.0 kV to GRE-RMSYCB14 (615907) 230.0 kV Transmission Circuit #z b.2. GRE-RMSYCB14 (615907) 230.0 kV to GRE-RMSYCB24 (615908) 230.0 kV Transmission Circuit #z b.3. GRE-RMSYCB24 (615908) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on GLENBOR4 230.00 (667052) 230 kV Bus a. Apply Fault at the GLENBOR4 230.00 (667052) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 b.2. GLENBOR4 (667052) 230.0 kV to GLENBOR8 (668405) 65.1 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply Fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARIETT7 (620213) 115.0 kV to BIGSTON7 (620214) 115.0 kV Transmission Circuit #1 b.2. BIGSTON7 (620214) 115.0 kV to HIWY12 7 (620215) 115.0 kV Transmission Circuit #1 b.3. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. BIGSTON7 (620214) 115.0 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #1 b.5. BIGSTON7 (620214) 115.0 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON9 (620316) 13.8 kV Three Winding #2 b.6. BIGSTON9 (620316) 13.8 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV Three Winding #1 b.7. BIGSTON9 (620316) 13.8 kV to BIGSTON4 (620314) 230.0 kV to BIGSTON7 (620214) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.5. TIOGA4 7 (661085) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.3. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_128 | Single Phase Fault with Stuck Breaker on J2086 SUB 345.00 (50863) 345 kV Bus a. Apply Fault at the J2086 SUB 345.00 (50863) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J2086 SUB (50863) 345.0 kV to J2086 COL (50862) 34.5 kV to J2086 T (50865) 13.8 kV Three Winding #1 b.2. J2086 SUB (50863) 345.0 kV to J2086 COL (50862) 34.5 kV to J2086 T (50864) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_129 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_130 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_131 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to BRKNGCO3 (601031) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_132 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_133 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_134 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 4 (620363) 230.0 kV to OAKES 4 (620362) 230.0 kV Transmission Circuit #1 b.2. FORMAN 4 (620363) 230.0 kV to HANKSON4 (620327) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_135 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_136 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_137 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_138 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to WAYSIDE4 (640404) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_139 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_140 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (657946) 345.0 kV to MPC4300 POI (657110) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_141 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_142 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451-RAUN 3 (645551) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_143 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLT RK3 (601006) 345.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.2. SPLT RK7 (603016) 115.0 kV to SPLT RK3 (601006) 345.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_144 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to CSLTNET7 (620180) 115.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_145 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 b.2. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_146 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE7 (652412) 115.0 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 b.2. MI CTYE7 (652412) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_147 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 7 (652436) 115.0 kV to FARGO 8 (652203) 69.0 kV Two Winding #2 b.2. FARGO 7 (652436) 115.0 kV to FARGO 4 (652435) 230.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_148 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.2. NUNDRWD7 (652485) 115.0 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_149 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 7 (652538) 115.0 kV to WHITE 3 (652537) 345.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 b.2. WHITE 7 (652538) 115.0 kV to BROOKNG7 (652504) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_150 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 b.2. PRAIRIE4 (657755) 230.0 kV to GRNDFKS4 (652437) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_151 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_UMZ_FAULT_001 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_UMZ_FAULT_002 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_UMZ_FAULT_003 | Single Phase Fault with Stuck Breaker on CCR 345 (659183) 345 kV Bus a. Apply Fault at the CCR 345 (659183) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 b.2. CCR.KV4A-BE9 (659319) 13.8 kV to remove bus # b.3. CCR.KV3A-BE9 (659318) 13.8 kV to remove bus # b.4. CHARL_CK-BE4 (659302) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 CF | 25W | Transfer | GROUP1_P4_UMZ_FAULT_004 | Single Phase Fault with Stuck Breaker on JDS 345 (659333) 345 kV Bus a. Apply Fault at the JDS 345 (659333) 345 kV Bus b. Clear Fault after 10 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to remove bus # b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25S | Base | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 | 25W | Base | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25S | Base | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a non-convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2022-001 CF | 25W | Base | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | The controller model response of J416 (629922 and 629923), J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units cause non-convergence causing the simulation to crash. The disabling of those units allows the simulation to complete without any issues observed. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0001 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0002 | 3 Phase fault on 5ELDON 1 161.00 (344532) 161 kV Bus a. Apply fault at the 5ELDON 1 161.00 (344532) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.2. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.3. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.4. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0003 | 3 Phase fault on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOYMART 1 (344040) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.2. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0004 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0005 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0006 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0007 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0008 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0009 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BOONE (300061) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0010 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0011 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0012 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0013 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0014 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0015 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0016 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0017 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0018 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0019 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0020 | 3 Phase fault on OAKGRV 5 161.00 (541227) 161 kV Bus a. Apply fault at the OAKGRV 5 161.00 (541227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAINVL5 (541226) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 b.2. OAKGRV 5 (541227) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0021 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0022 | 3 Phase fault on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0023 | 3 Phase fault on STALEY 2 69.000 (541261) 69 kV Bus a. Apply fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0024 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0025 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0026 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0027 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0028 | 3 Phase fault on BRMALL 2 69.000 (541283) 69 kV Bus a. Apply fault at the BRMALL 2 69.000 (541283) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMALL 2 (541283) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0029 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0030 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0031 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0032 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0033 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0034 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0035 | 3 Phase fault on SUB E 69.000 (548804) 69 kV Bus a. Apply fault at the SUB E 69.000 (548804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0036 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0037 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0038 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0039 | 3 Phase fault on SUB B 69.000 (548810) 69 kV Bus a. Apply fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0040 | 3 Phase fault on SUB J 69.000 (548811) 69 kV Bus a. Apply fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0041 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0042 | 3 Phase fault on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0043 | 3 Phase fault on STRLNGRD 69.000 (548826) 69 kV Bus a. Apply fault at the STRLNGRD 69.000 (548826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.3. SUB C (548825) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0044 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0045 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0046 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0047 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0048 | 3 Phase fault on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0049 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0050 | 3 Phase fault on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0051 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0052 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0053 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 b.2. ST JOE_CAP5 (541147) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0054 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.3. RNRIDGE_CAP5 (541145) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0055 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0056 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0057 | 3 Phase fault on NAVY 5 161.00 (542989) 161 kV Bus a. Apply fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0058 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0059 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0060 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. BARRY_CAP 5 (542944) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0061 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0062 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0063 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0064 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0065 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0066 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0067 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0068 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0069 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0070 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0071 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0072 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0073 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0074 | 3 Phase fault on MILCKJT2 69.000 (543110) 69 kV Bus a. Apply fault at the MILCKJT2 69.000 (543110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.3. IND WTR2 (543086) 69.0 kV to CEMCITY2 (543090) 69.0 kV Transmission Circuit #1 b.4. IND WTR2 (543086) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.5. TMP LAF2 (543103) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.6. LAFJCT 2 (543104) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.7. MILCKJT2 (543110) 69.0 kV to LAFARGE2 (543111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0075 | 3 Phase fault on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 b.3. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0076 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0077 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0078 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0079 | 3 Phase fault on WPRTTS 2 69.000 (530596) 69 kV Bus a. Apply fault at the WPRTTS 2 69.000 (530596) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.2. GB STH 2 (530569) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.3. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.4. WPRTTS 2 (530596) 69.0 kV to WPRT2 2 (530597) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0080 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0081 | 3 Phase fault on COLLEG 2 69.000 (530574) 69 kV Bus a. Apply fault at the COLLEG 2 69.000 (530574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 b.2. COLLEG 2 (530574) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0082 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0083 | 3 Phase fault on NEKOMA 2 69.000 (530564) 69 kV Bus a. Apply fault at the NEKOMA 2 69.000 (530564) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0084 | 3 Phase fault on BKHLTAP2 69.000 (530589) 69 kV Bus a. Apply fault at the BKHLTAP2 69.000 (530589) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.2. SUSANK 2 (530571) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.3. BNK HL 2 (530572) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.4. HITHMN 2 (530573) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0085 | 3 Phase fault on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0086 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0087 | 3 Phase fault on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0088 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0089 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0090 | 3 Phase fault on SEGNTP 3 115.00 (530682) 115 kV Bus a. Apply fault at the SEGNTP 3 115.00 (530682) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEGNTP 3 (530682) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0091 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0092 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0093 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0094 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0095 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0096 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.2. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.3. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.6. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0097 | 3 Phase fault on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0098 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0099 | 3 Phase fault on HOXIE 3 115.00 (530556) 115 kV Bus a. Apply fault at the HOXIE 3 115.00 (530556) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0100 | 3 Phase fault on ANGELUS 115.00 (530717) 115 kV Bus a. Apply fault at the ANGELUS 115.00 (530717) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.2. SEGNTP 3 (530682) 115.0 kV to SEGUIN 3 (530683) 115.0 kV Transmission Circuit #1 b.3. SEGUIN 3 (530683) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0101 | 3 Phase fault on HUNTSVL3 115.00 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 115.00 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0102 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0103 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0104 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0105 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0106 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0107 | 3 Phase fault on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0108 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0109 | 3 Phase fault on GRHMSUB3 115.00 (531386) 115 kV Bus a. Apply fault at the GRHMSUB3 115.00 (531386) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0110 | 3 Phase fault on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0111 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0112 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0113 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0114 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0115 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0116 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0117 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0118 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0119 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0120 | 3 Phase fault on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0121 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0122 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0123 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0124 | 3 Phase fault on BEACH 3 115.00 (530557) 115 kV Bus a. Apply fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0125 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0126 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0127 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0128 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.2. STOCKVL7 (640365) 115.0 kV to STOCKVL8 (640366) 69.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 b.4. STOCKVLLET19 (643146) 13.8 kV to STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0129 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0130 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0131 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0132 | 3 Phase fault on ATHEY 7 115.00 (641244) 115 kV Bus a. Apply fault at the ATHEY 7 115.00 (641244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 b.2. ATHEY 7 (641244) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 b.3. LAMAR___-TS7 (659804) 115.0 kV to CRETE___-TS7 (659813) 115.0 kV Transmission Circuit #1 b.4. CRETE___-TS7 (659813) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0133 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0134 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0135 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0136 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0137 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0138 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0139 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0140 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0141 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0142 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0143 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0144 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0145 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0146 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0147 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0148 | 3 Phase fault on BEVERLY8 69.000 (640083) 69 kV Bus a. Apply fault at the BEVERLY8 69.000 (640083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0149 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0150 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0151 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0152 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0153 | 3 Phase fault on MCCOOK 8 69.000 (640270) 69 kV Bus a. Apply fault at the MCCOOK 8 69.000 (640270) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0154 | 3 Phase fault on STOCKVL8 69.000 (640366) 69 kV Bus a. Apply fault at the STOCKVL8 69.000 (640366) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKVL8 (640366) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0155 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0156 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0157 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0158 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0159 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0160 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0161 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0162 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0163 | 3 Phase fault on ANTHONY4 138.00 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 138.00 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0164 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0165 | 3 Phase fault on GRINNEL3 115.00 (531412) 115 kV Bus a. Apply fault at the GRINNEL3 115.00 (531412) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 b.2. ARNOLD3 (531409) 115.0 kV to GOVE 3 (531411) 115.0 kV Transmission Circuit #1 b.3. ARNOLD3 (531409) 115.0 kV to RANSOM 3 (531414) 115.0 kV Transmission Circuit #1 b.4. GOVE 3 (531411) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0166 | 3 Phase fault on SETAB 3 115.00 (531464) 115 kV Bus a. Apply fault at the SETAB 3 115.00 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0167 | 3 Phase fault on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0168 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0169 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0170 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0171 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0172 | 3 Phase fault on WILLIAM3 115.00 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 115.00 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0173 | 3 Phase fault on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEOTI 3 (531428) 115.0 kV to SELKIRK3 (531434) 115.0 kV Transmission Circuit #1 b.2. LEOTI 3 (531428) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 b.3. SELKIRK3 (531434) 115.0 kV to TRIB SW3 (531438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0174 | 3 Phase fault on ATWODSW3 115.00 (531364) 115 kV Bus a. Apply fault at the ATWODSW3 115.00 (531364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.2. LUDELLT3 (531220) 115.0 kV to LUDELL 3 (531221) 115.0 kV Transmission Circuit #1 b.3. LUDELLT3 (531220) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.4. LUDELLT3 (531220) 115.0 kV to HERNDON3 (531367) 115.0 kV Transmission Circuit #1 b.5. ATWODSW3 (531364) 115.0 kV to NATWOOD3 (531369) 115.0 kV Transmission Circuit #1 b.6. HERNDON3 (531367) 115.0 kV to JOHNSON3 (531371) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0175 | 3 Phase fault on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.3. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0176 | 3 Phase fault on GANO 3 115.00 (531493) 115 kV Bus a. Apply fault at the GANO 3 115.00 (531493) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.3. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0177 | 3 Phase fault on KSAVWTP3 115.00 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 115.00 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0178 | 3 Phase fault on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0179 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0180 | 3 Phase fault on SUNCITY3 115.00 (539697) 115 kV Bus a. Apply fault at the SUNCITY3 115.00 (539697) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.3. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.4. GRNBURG3 (539664) 115.0 kV to GRNBURG1 (539710) 34.5 kV to GRNBUG-T (539910) 13.8 kV Three Winding #1 b.5. SUNCITY3 (539697) 115.0 kV to SUNCITY1 (539733) 34.5 kV to SUNCT-T (539937) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0181 | 3 Phase fault on FORD 3 115.00 (539758) 115 kV Bus a. Apply fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.3. FORD 3 (539758) 115.0 kV to FORD 1 (539765) 34.5 kV to FORD T (539968) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0182 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0183 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0184 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0185 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0186 | 3 Phase fault on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0187 | 3 Phase fault on DCBEEF3 115.00 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 115.00 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0188 | 3 Phase fault on SPEARVL3 115.00 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 115.00 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0189 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0190 | 3 Phase fault on N-DODGE3 115.00 (539680) 115 kV Bus a. Apply fault at the N-DODGE3 115.00 (539680) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DODG3 (539641) 115.0 kV to N-DODGE3 (539680) 115.0 kV Transmission Circuit #1 b.2. N-DODGE3 (539680) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. N-DODGE3 (539680) 115.0 kV to N-DODGE1 (539720) 34.5 kV to N-DODG-T (539922) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0191 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0192 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0193 | 3 Phase fault on WALDO 3 115.00 (539698) 115 kV Bus a. Apply fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0194 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0195 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0196 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0197 | 3 Phase fault on HARPER 4 138.00 (539668) 138 kV Bus a. Apply fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0198 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0199 | 3 Phase fault on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL3 (539701) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0200 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0201 | 3 Phase fault on BYRONTP4 138.00 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 138.00 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.2. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0202 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0203 | 3 Phase fault on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0204 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0205 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0206 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0207 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0208 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0209 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0210 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0211 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0212 | 3 Phase fault on CARB-KW 3 115.00 (533195) 115 kV Bus a. Apply fault at the CARB-KW 3 115.00 (533195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 b.2. CARB-KW 3 (533195) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0213 | 3 Phase fault on OSAGE J3 115.00 (533171) 115 kV Bus a. Apply fault at the OSAGE J3 115.00 (533171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.2. OSAGE 3 (533170) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 b.3. OSAGE J3 (533171) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.4. OSAGE J3 (533171) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.5. READING3 (533306) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0214 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGCRK3 (533380) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.2. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.4. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0215 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0216 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0217 | 3 Phase fault on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0218 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0219 | 3 Phase fault on MORRIS 3 115.00 (533305) 115 kV Bus a. Apply fault at the MORRIS 3 115.00 (533305) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0220 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0221 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0222 | 3 Phase fault on NW LEAV3 115.00 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 115.00 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0223 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.2. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0224 | 3 Phase fault on STRANGR3 115.00 (533268) 115 kV Bus a. Apply fault at the STRANGR3 115.00 (533268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0225 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0226 | 3 Phase fault on FOWLER 4 138.00 (533043) 138 kV Bus a. Apply fault at the FOWLER 4 138.00 (533043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0227 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0228 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0229 | 3 Phase fault on 47TH ST4 138.00 (533058) 138 kV Bus a. Apply fault at the 47TH ST4 138.00 (533058) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0230 | 3 Phase fault on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0231 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0232 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0233 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0234 | 3 Phase fault on BELAIRE4 138.00 (532988) 138 kV Bus a. Apply fault at the BELAIRE4 138.00 (532988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0235 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0236 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0237 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0238 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0239 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0240 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0241 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0242 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0243 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0244 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0245 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0246 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0247 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0248 | 3 Phase fault on BU11PON4 138.00 (533032) 138 kV Bus a. Apply fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0249 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0250 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0251 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0252 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0253 | 3 Phase fault on BEECHTP4 138.00 (533028) 138 kV Bus a. Apply fault at the BEECHTP4 138.00 (533028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.2. BEECH 4 (533027) 138.0 kV to BEECHTP4 (533028) 138.0 kV Transmission Circuit #1 b.3. BEECHTP4 (533028) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 b.4. BEECHTP4 (533028) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0254 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0255 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0256 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0257 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0258 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0259 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0260 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0261 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0262 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0263 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0264 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0265 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0266 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0267 | 3 Phase fault on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0268 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0269 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0270 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0271 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0272 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0273 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0274 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0275 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0276 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0277 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0278 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0279 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0280 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0281 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0282 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0283 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0284 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0285 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0286 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0287 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0288 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0289 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0290 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0291 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0292 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0293 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0294 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0295 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0296 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0297 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0298 | 3 Phase fault on MEAD N 2 69.000 (533818) 69 kV Bus a. Apply fault at the MEAD N 2 69.000 (533818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD N 2 (533818) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0299 | 3 Phase fault on 17TH TP2 69.000 (533835) 69 kV Bus a. Apply fault at the 17TH TP2 69.000 (533835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.2. RIVERSD2 (533834) 69.0 kV to 17TH TP2 (533835) 69.0 kV Transmission Circuit #1 b.3. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.4. 17TH TP2 (533835) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.5. 17TH TP2 (533835) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0300 | 3 Phase fault on MOSSMAN2 69.000 (533820) 69 kV Bus a. Apply fault at the MOSSMAN2 69.000 (533820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSSMAN2 (533820) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0301 | 3 Phase fault on MASCOT 2 69.000 (533814) 69 kV Bus a. Apply fault at the MASCOT 2 69.000 (533814) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASCOT 2 (533814) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.2. MASCOT 2 (533814) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0302 | 3 Phase fault on EASTBOR2 69.000 (533792) 69 kV Bus a. Apply fault at the EASTBOR2 69.000 (533792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTBOR2 (533792) 69.0 kV to MINNEHA2 (533817) 69.0 kV Transmission Circuit #1 b.2. EASTBOR2 (533792) 69.0 kV to 64TH 2 (533842) 69.0 kV Transmission Circuit #1 b.3. MINNEHA2 (533817) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0303 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0304 | 3 Phase fault on ARCOTAP2 69.000 (533620) 69 kV Bus a. Apply fault at the ARCOTAP2 69.000 (533620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO 2 (533619) 69.0 kV to ARCOTAP2 (533620) 69.0 kV Transmission Circuit #1 b.2. ARCOTAP2 (533620) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.3. ARCOTAP2 (533620) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.4. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.5. COALCRK2 (533633) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.6. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0305 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0306 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to RA5HIPR2 (533706) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0307 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0308 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0309 | 3 Phase fault on ORCHARD2 69.000 (533643) 69 kV Bus a. Apply fault at the ORCHARD2 69.000 (533643) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.2. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.3. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0310 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0311 | 3 Phase fault on BELL 2 69.000 (533783) 69 kV Bus a. Apply fault at the BELL 2 69.000 (533783) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV to SC9ANSN2 (533866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0312 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 b.2. SC3MILL2 (533552) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 b.3. SC3MILL2 (533552) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 b.4. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0313 | 3 Phase fault on PECK 2 69.000 (533830) 69 kV Bus a. Apply fault at the PECK 2 69.000 (533830) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 b.2. GILL W 2 (533796) 69.0 kV to HAYSVJS2 (533802) 69.0 kV Transmission Circuit #1 b.3. HAYSVJS2 (533802) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0314 | 3 Phase fault on HYDRJS2 69.000 (533810) 69 kV Bus a. Apply fault at the HYDRJS2 69.000 (533810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALN 2 (533790) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 b.2. HYDRA N2 (533807) 69.0 kV to HYDRJS2 (533810) 69.0 kV Transmission Circuit #1 b.3. HYDRJS2 (533810) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 b.4. HYDRJS2 (533810) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0315 | 3 Phase fault on SHERIDN2 69.000 (533841) 69 kV Bus a. Apply fault at the SHERIDN2 69.000 (533841) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0316 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV to RIPLEYE2 (533859) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0317 | 3 Phase fault on BU5FURL2 69.000 (533861) 69 kV Bus a. Apply fault at the BU5FURL2 69.000 (533861) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THUNBRD2 (533603) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 b.2. CHISHLM2 (533786) 69.0 kV to GRANT 2 (533799) 69.0 kV Transmission Circuit #1 b.3. GRANT 2 (533799) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0318 | 3 Phase fault on WESTLNK2 69.000 (533854) 69 kV Bus a. Apply fault at the WESTLNK2 69.000 (533854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.3. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0319 | 3 Phase fault on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0320 | 3 Phase fault on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.2. SUNSET-2 (533844) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0321 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC7CRES2 (533555) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0322 | 3 Phase fault on WILLJCT2 69.000 (533713) 69 kV Bus a. Apply fault at the WILLJCT2 69.000 (533713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 b.2. WILLJCT2 (533713) 69.0 kV to ELKJSS 2 (533718) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0323 | 3 Phase fault on ELPASO 2 69.000 (533793) 69 kV Bus a. Apply fault at the ELPASO 2 69.000 (533793) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 2 (533793) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 b.2. ELPASO 2 (533793) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0324 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0325 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0326 | 3 Phase fault on WATER1 2 69.000 (533855) 69 kV Bus a. Apply fault at the WATER1 2 69.000 (533855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0327 | 3 Phase fault on WATER2 2 69.000 (533856) 69 kV Bus a. Apply fault at the WATER2 2 69.000 (533856) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.2. PLAZA E2 (533829) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0328 | 3 Phase fault on RIPLEYW2 69.000 (533832) 69 kV Bus a. Apply fault at the RIPLEYW2 69.000 (533832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.2. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.3. 21ST 2 (533846) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0329 | 3 Phase fault on INDEPEN2 69.000 (533694) 69 kV Bus a. Apply fault at the INDEPEN2 69.000 (533694) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDEPEN2 (533694) 69.0 kV to MONTGOM2 (533698) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0330 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0331 | 3 Phase fault on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0332 | 3 Phase fault on HYDRJN2 69.000 (533808) 69 kV Bus a. Apply fault at the HYDRJN2 69.000 (533808) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HYDRJN2 (533808) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.2. HYDRJN2 (533808) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0333 | 3 Phase fault on SENECA 2 69.000 (533839) 69 kV Bus a. Apply fault at the SENECA 2 69.000 (533839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.2. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.3. OSAGE 2 (533827) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0334 | 3 Phase fault on MEAD S 2 69.000 (533815) 69 kV Bus a. Apply fault at the MEAD S 2 69.000 (533815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0335 | 3 Phase fault on HAYSVJN2 69.000 (533804) 69 kV Bus a. Apply fault at the HAYSVJN2 69.000 (533804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 b.2. HAYSVJN2 (533804) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0336 | 3 Phase fault on LIN 2 69.000 (533812) 69 kV Bus a. Apply fault at the LIN 2 69.000 (533812) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.2. LIN 2 (533812) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 b.3. SUNSET-2 (533844) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 b.4. SG1CHEN2 (533871) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0337 | 3 Phase fault on MAHANNA2 69.000 (533738) 69 kV Bus a. Apply fault at the MAHANNA2 69.000 (533738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAHANNA2 (533738) 69.0 kV to ADAMS 2 (533746) 69.0 kV Transmission Circuit #1 b.2. MAHANNA2 (533738) 69.0 kV to GRANT J2 (533800) 69.0 kV Transmission Circuit #1 b.3. NEWTON 2 (533745) 69.0 kV to ADAMS 2 (533746) 69.0 kV Transmission Circuit #1 b.4. GRANT J2 (533800) 69.0 kV to RIPLEYW2 (533832) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0338 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0339 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0340 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0341 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0342 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0343 | 3 Phase fault on ASHGRJ22 69.000 (533660) 69 kV Bus a. Apply fault at the ASHGRJ22 69.000 (533660) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.2. ASHGRV22 (533658) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.3. ASHGRJ12 (533659) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #z1 b.4. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0344 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 b.3. EMANHAT6 (532861) 230.0 kV to EMANHAT3 (533326) 115.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0345 | 3 Phase fault on 64TH 4 138.00 (533066) 138 kV Bus a. Apply fault at the 64TH 4 138.00 (533066) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRY 4 (533048) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 b.3. 64TH 4 (533066) 138.0 kV to 64TH 2 (533842) 69.0 kV to 64TH 1 (533113) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0346 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0347 | 3 Phase fault on CANAL 4 138.00 (533033) 138 kV Bus a. Apply fault at the CANAL 4 138.00 (533033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. CANAL 4 (533033) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #1 b.3. CANAL 4 (533033) 138.0 kV to CANALS 2 (533784) 69.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0348 | 3 Phase fault on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0349 | 3 Phase fault on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.3. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.4. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0350 | 3 Phase fault on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0351 | 3 Phase fault on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0352 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.4. MONTGOM1 (533091) 13.2 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0353 | 3 Phase fault on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0354 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0355 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0356 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAUGHN 3 (533308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0357 | 3 Phase fault on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0358 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0359 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0360 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0361 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0362 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0363 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0364 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0365 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0366 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0367 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0368 | 3 Phase fault on BELL 2 69.000 (533783) 69 kV Bus a. Apply fault at the BELL 2 69.000 (533783) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0369 | 3 Phase fault on CANALN 2 69.000 (533790) 69 kV Bus a. Apply fault at the CANALN 2 69.000 (533790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALN 2 (533790) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0370 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0371 | 3 Phase fault on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0372 | 3 Phase fault on MACARTH2 69.000 (533813) 69 kV Bus a. Apply fault at the MACARTH2 69.000 (533813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACARTH2 (533813) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0373 | 3 Phase fault on MONTGOM2 69.000 (533698) 69 kV Bus a. Apply fault at the MONTGOM2 69.000 (533698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0374 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0375 | 3 Phase fault on PARSONS2 69.000 (533704) 69 kV Bus a. Apply fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0376 | 3 Phase fault on TIOGA 2 69.000 (533646) 69 kV Bus a. Apply fault at the TIOGA 2 69.000 (533646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0377 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0378 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0379 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0380 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0381 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0382 | 3 Phase fault on CHELSA4 138.00 (510410) 138 kV Bus a. Apply fault at the CHELSA4 138.00 (510410) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHELSA4 (510410) 138.0 kV to G22-234-TAP (771660) 138.0 kV Transmission Circuit #1 b.2. ALWUETP4 (510429) 138.0 kV to G22-234-TAP (771660) 138.0 kV Transmission Circuit #1 b.3. N.E.S.-4 (510396) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.4. CHELSA4 (510410) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.5. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0383 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0384 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 (510418) 69.0 kV to VINTAJC4 (510417) 138.0 kV to VINJT1-1 (510367) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0385 | 3 Phase fault on TERRACE5 161.00 (542991) 161 kV Bus a. Apply fault at the TERRACE5 161.00 (542991) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0386 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0387 | 3 Phase fault on BARBER 5 161.00 (546651) 161 kV Bus a. Apply fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0388 | 3 Phase fault on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0389 | 3 Phase fault on GIBBS 5 161.00 (546658) 161 kV Bus a. Apply fault at the GIBBS 5 161.00 (546658) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0390 | 3 Phase fault on PIPER 5 161.00 (546668) 161 kV Bus a. Apply fault at the PIPER 5 161.00 (546668) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0391 | 3 Phase fault on KAW 2 69.000 (546678) 69 kV Bus a. Apply fault at the KAW 2 69.000 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to BARBER 2 (546691) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0392 | 3 Phase fault on BARBER 5 161.00 (546651) 161 kV Bus a. Apply fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0393 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0394 | 3 Phase fault on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0395 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0396 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0397 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0398 | 3 Phase fault on 5ELMCRK 161.00 (300993) 161 kV Bus a. Apply fault at the 5ELMCRK 161.00 (300993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit #1 b.2. 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0399 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0400 | 3 Phase fault on NWMAID5 161.00 (512757) 161 kV Bus a. Apply fault at the NWMAID5 161.00 (512757) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0401 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0402 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0403 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0404 | 3 Phase fault on KANSATP5 161.00 (512714) 161 kV Bus a. Apply fault at the KANSATP5 161.00 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 412SUB 5 (512637) 161.0 kV to KANSATP5 (512714) 161.0 kV Transmission Circuit #1 b.2. KANSATP5 (512714) 161.0 kV to KANSAS 5 (512716) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0405 | 3 Phase fault on PENSA 5 161.00 (512654) 161 kV Bus a. Apply fault at the PENSA 5 161.00 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0406 | 3 Phase fault on LOCSTGVKM 5 161.00 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 161.00 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0407 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0408 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0409 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0410 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0411 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0412 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0413 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0414 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0415 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0416 | 3 Phase fault on 2NEWPORT 69.000 (301467) 69 kV Bus a. Apply fault at the 2NEWPORT 69.000 (301467) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MONKEY (301465) 69.0 kV to 2NEWPORT (301467) 69.0 kV Transmission Circuit #1 b.2. 2NEWPORT (301467) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0417 | 3 Phase fault on SAILBOA2 69.000 (510409) 69 kV Bus a. Apply fault at the SAILBOA2 69.000 (510409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAILBOA2 (510409) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0418 | 3 Phase fault on AMERCAST S2 69.000 (512681) 69 kV Bus a. Apply fault at the AMERCAST S2 69.000 (512681) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to AMERCAST S2 (512681) 69.0 kV Transmission Circuit #1 b.2. CPPTAP 2 (512661) 69.0 kV to AMERCAST S2 (512681) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0419 | 3 Phase fault on REDDEN 2 69.000 (512698) 69 kV Bus a. Apply fault at the REDDEN 2 69.000 (512698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to REDDEN 2 (512698) 69.0 kV Transmission Circuit #1 b.2. AMERCAST N2 (512683) 69.0 kV to CASTING TAP2 (512685) 69.0 kV Transmission Circuit #1 b.3. CASTING TAP2 (512685) 69.0 kV to REDDEN 2 (512698) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0420 | 3 Phase fault on CLEORTP2 69.000 (512692) 69 kV Bus a. Apply fault at the CLEORTP2 69.000 (512692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEORA (301460) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 b.2. PENSA 2 (512628) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 b.3. AFTON 2 (512633) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0421 | 3 Phase fault on ESH TP 2 69.000 (512680) 69 kV Bus a. Apply fault at the ESH TP 2 69.000 (512680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2J6 (300829) 69.0 kV to AFTP TP2 (512620) 69.0 kV Transmission Circuit #1 b.2. 2J6 (300829) 69.0 kV to VINEOTP2 (512673) 69.0 kV Transmission Circuit #1 b.3. 2VINITAHQ (300983) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.4. 2ESHOSP (301468) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.5. 2VIN NEO (301478) 69.0 kV to VINEOTP2 (512673) 69.0 kV Transmission Circuit #1 b.6. VINITA-2 (510404) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.7. AFTONTP2 (510415) 69.0 kV to A-CONT 2 (510427) 69.0 kV Transmission Circuit #1 b.8. AFTONTP2 (510415) 69.0 kV to AFTN-EX2 (510428) 69.0 kV Transmission Circuit #1 b.9. AFTONTP2 (510415) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.10. AFTP TP2 (512620) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.11. AFTON 2 (512633) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.12. VINEOTP2 (512673) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0422 | 3 Phase fault on FAIRTAP2 69.000 (512708) 69 kV Bus a. Apply fault at the FAIRTAP2 69.000 (512708) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to FAIRNEO2 (512691) 69.0 kV Transmission Circuit #1 b.2. AFTON 2 (512633) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 b.3. FAIRNEO2 (512691) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 b.4. FAIRTAP2 (512708) 69.0 kV to FRL363 2 (547583) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0423 | 3 Phase fault on MIAMI 2 69.000 (512630) 69 kV Bus a. Apply fault at the MIAMI 2 69.000 (512630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI1 2 (513020) 69.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI3 2 (513024) 69.0 kV Transmission Circuit #1 b.3. MIAMI1 2 (513020) 69.0 kV to MIAMI4 2 (513022) 69.0 kV Transmission Circuit #1 b.4. MIAMI4 2 (513022) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 b.5. MIAMI3 2 (513024) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0424 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0425 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0426 | 3 Phase fault on 2WLKRTP 69.000 (300760) 69 kV Bus a. Apply fault at the 2WLKRTP 69.000 (300760) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSHO (300750) 69.0 kV to 2WLKRTP (300760) 69.0 kV Transmission Circuit #1 b.2. 2WLKRTP (300760) 69.0 kV to 2WLKRVL (300761) 69.0 kV Transmission Circuit #1 b.3. 2WLKRTP (300760) 69.0 kV to 2SENECA (300830) 69.0 kV Transmission Circuit #1 b.4. 2SENECA (300830) 69.0 kV to 2MIAETP (300852) 69.0 kV Transmission Circuit #1 b.5. 2MIAETP (300852) 69.0 kV to MIAMI 2 (512630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0427 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0428 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0429 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0430 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0431 | 3 Phase fault on TONECE7 345.00 (512750) 345 kV Bus a. Apply fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0432 | 3 Phase fault on KERR BRK1 5 161.00 (512770) 161 kV Bus a. Apply fault at the KERR BRK1 5 161.00 (512770) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK1 5 (512770) 161.0 kV to KERR GR3 (512634) 115.0 kV to KERR1 1 (512846) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0433 | 3 Phase fault on KERR BRK4 5 161.00 (512771) 161 kV Bus a. Apply fault at the KERR BRK4 5 161.00 (512771) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK4 5 (512771) 161.0 kV to KERR GR3 (512634) 115.0 kV to KERR2 1 (512847) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0434 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0435 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0436 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0437 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0438 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0439 | 3 Phase fault on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0440 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0441 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0442 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0443 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0444 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. HOC404A1 (547715) 12.5 kV to HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0445 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0446 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0447 | 3 Phase fault on 5MCBAIN T 161.00 (345071) 161 kV Bus a. Apply fault at the 5MCBAIN T 161.00 (345071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0448 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0449 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0450 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0451 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0452 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0453 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0454 | 3 Phase fault on 5APCH TP 161.00 (344026) 161 kV Bus a. Apply fault at the 5APCH TP 161.00 (344026) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0455 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MPLTAP (300036) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 b.3. 5MPLTAP (300036) 161.0 kV to 5LATHROP (344923) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0456 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0457 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0458 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0459 | 3 Phase fault on 5LOYMART 1 161.00 (344040) 161 kV Bus a. Apply fault at the 5LOYMART 1 161.00 (344040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOYMART 1 (344040) 161.0 kV to 5LOYMART 2 (344041) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0460 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0461 | 3 Phase fault on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GUTHRIE 1 (344677) 161.0 kV to 5GUTHRIE 2 (344678) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0462 | 3 Phase fault on 5JC ZION 161.00 (344814) 161 kV Bus a. Apply fault at the 5JC ZION 161.00 (344814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JC ZION (344814) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #z b.2. 2JC ZION (346089) 69.0 kV to 5JC ZION (344814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0463 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0464 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0465 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0466 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0467 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to VSC2_3 (992003) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0468 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0469 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0470 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BOONE (300061) 161.0 kV to 5MCBAINB1 (300501) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0471 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BOONE (300061) 161.0 kV to 5MLRSBGB1 (300519) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0472 | 3 Phase fault on 5CALIF 161.00 (300063) 161 kV Bus a. Apply fault at the 5CALIF 161.00 (300063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF (300063) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0473 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0474 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0475 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0476 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0477 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0478 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0479 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0480 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0481 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0482 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0483 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0484 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0485 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0486 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0487 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0488 | 3 Phase fault on 5OSBORN 161.00 (300107) 161 kV Bus a. Apply fault at the 5OSBORN 161.00 (300107) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSBORN (300107) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0489 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0490 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0491 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0492 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0493 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2MOCITY (300304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0494 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0495 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0496 | 3 Phase fault on 2ASHLND 69.000 (300492) 69 kV Bus a. Apply fault at the 2ASHLND 69.000 (300492) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHLND (300492) 69.0 kV to 2BOONE (300493) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0497 | 3 Phase fault on 2BOONE 69.000 (300493) 69 kV Bus a. Apply fault at the 2BOONE 69.000 (300493) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOONE (300493) 69.0 kV to 2DEERPK (300497) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0498 | 3 Phase fault on 2BOONE 69.000 (300493) 69 kV Bus a. Apply fault at the 2BOONE 69.000 (300493) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOONE (300493) 69.0 kV to 2GRINDSTN (343006) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0499 | 3 Phase fault on 5MCBAINB1 161.00 (300501) 161 kV Bus a. Apply fault at the 5MCBAINB1 161.00 (300501) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB1 (300501) 161.0 kV to 5MCBAINB2 (301489) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0500 | 3 Phase fault on 5MLRSBGB1 161.00 (300519) 161 kV Bus a. Apply fault at the 5MLRSBGB1 161.00 (300519) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MLRSBGB1 (300519) 161.0 kV to 5MLRSBGB2 (301498) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0501 | 3 Phase fault on 2DRESDN 69.000 (300528) 69 kV Bus a. Apply fault at the 2DRESDN 69.000 (300528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DRESDN (300528) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0502 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0503 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0504 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0505 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0506 | 3 Phase fault on 2HUGHSV 69.000 (300533) 69 kV Bus a. Apply fault at the 2HUGHSV 69.000 (300533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HUGHSV (300533) 69.0 kV to 2SWSPJC (300543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0507 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0508 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0509 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0510 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GI91 (99915). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0511 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0512 | 3 Phase fault on 2CALIF 69.000 (300550) 69 kV Bus a. Apply fault at the 2CALIF 69.000 (300550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 2FORTNA (300554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0513 | 3 Phase fault on 2CALIF 69.000 (300550) 69 kV Bus a. Apply fault at the 2CALIF 69.000 (300550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 2PRARIE (300561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0514 | 3 Phase fault on 2CALIF 69.000 (300550) 69 kV Bus a. Apply fault at the 2CALIF 69.000 (300550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 2ST_MARTINS (301442) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0515 | 3 Phase fault on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FORTNA (300554) 69.0 kV to 2NEEDY (300559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0516 | 3 Phase fault on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FORTNA (300554) 69.0 kV to 2SYRACS (300564) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0517 | 3 Phase fault on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FORTNA (300554) 69.0 kV to 2VERSAL (300565) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0518 | 3 Phase fault on 5GRAVOIB1 161.00 (300555) 161 kV Bus a. Apply fault at the 5GRAVOIB1 161.00 (300555) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRAVOIB1 (300555) 161.0 kV to 5GRAVOIB2 (300574) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0519 | 3 Phase fault on 2HIGHPT 69.000 (300556) 69 kV Bus a. Apply fault at the 2HIGHPT 69.000 (300556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HIGHPT (300556) 69.0 kV to 2BARNET (300618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0520 | 3 Phase fault on 2PILOTG 69.000 (300560) 69 kV Bus a. Apply fault at the 2PILOTG 69.000 (300560) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PILOTG (300560) 69.0 kV to 2PRARIE (300561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0521 | 3 Phase fault on 2VERSAL 69.000 (300565) 69 kV Bus a. Apply fault at the 2VERSAL 69.000 (300565) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERSAL (300565) 69.0 kV to 2BARNET (300618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0522 | 3 Phase fault on 2BARNET 69.000 (300618) 69 kV Bus a. Apply fault at the 2BARNET 69.000 (300618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BARNET (300618) 69.0 kV to 2MTPLSTC (300633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0523 | 3 Phase fault on 2SCRUGG 69.000 (300637) 69 kV Bus a. Apply fault at the 2SCRUGG 69.000 (300637) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SCRUGG (300637) 69.0 kV to 2ST_MARTINS (301442) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0524 | 3 Phase fault on 2BLLMYTP 69.000 (300647) 69 kV Bus a. Apply fault at the 2BLLMYTP 69.000 (300647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLLMYTP (300647) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0525 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0526 | 3 Phase fault on 2LAMR 69.000 (300651) 69 kV Bus a. Apply fault at the 2LAMR 69.000 (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0527 | 3 Phase fault on 2LAMR 69.000 (300651) 69 kV Bus a. Apply fault at the 2LAMR 69.000 (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2LAMARPT (300685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0528 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0529 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0530 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0531 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0532 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0533 | 3 Phase fault on 2MIAETP 69.000 (300852) 69 kV Bus a. Apply fault at the 2MIAETP 69.000 (300852) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MIAETP (300852) 69.0 kV to 2MIAENEO (301461) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0534 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0535 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0536 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0537 | 3 Phase fault on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PLATCTY (301552) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0538 | 3 Phase fault on 5REBEL 161.00 (343007) 161 kV Bus a. Apply fault at the 5REBEL 161.00 (343007) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REBEL (343007) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0539 | 3 Phase fault on 2APCH FLT 69.000 (344027) 69 kV Bus a. Apply fault at the 2APCH FLT 69.000 (344027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2APCH FLT (344027) 69.0 kV to 2JC RAINB (346082) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0540 | 3 Phase fault on 2APCH FLT 69.000 (344027) 69 kV Bus a. Apply fault at the 2APCH FLT 69.000 (344027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2APCH FLT (344027) 69.0 kV to 2JC SCRGG (346084) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0541 | 3 Phase fault on 5APCH FLT 161.00 (344028) 161 kV Bus a. Apply fault at the 5APCH FLT 161.00 (344028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0542 | 3 Phase fault on 5JC ZION TP 161.00 (344815) 161 kV Bus a. Apply fault at the 5JC ZION TP 161.00 (344815) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JC ZION TP (344815) 161.0 kV to 5MARIOSA (345027) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0543 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0544 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0545 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2MACON_AM (346096) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0546 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2DUPONT (346169) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0547 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2ROTH TAP (346170) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0548 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2SPRK TAP (346171) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0549 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0550 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0551 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to KERR BRK1 5 (512770) 161.0 kV Transmission Circuit #z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0552 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to KERR BRK4 5 (512771) 161.0 kV Transmission Circuit #z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0553 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0554 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to G21-047-TAP (765721) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0555 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0556 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0557 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0558 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0559 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0560 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0561 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0562 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0563 | 3 Phase fault on N HAYS3 115.00 (530581) 115 kV Bus a. Apply fault at the N HAYS3 115.00 (530581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0564 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0565 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0566 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0567 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0568 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0569 | 3 Phase fault on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0570 | 3 Phase fault on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0571 | 3 Phase fault on VINETAP3 115.00 (530693) 115 kV Bus a. Apply fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0572 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0573 | 3 Phase fault on GEM_SW 3 115.00 (530713) 115 kV Bus a. Apply fault at the GEM_SW 3 115.00 (530713) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEM_SW 3 (530713) 115.0 kV to COLBY_PUMP3 (530716) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0574 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0575 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0576 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284) and G22-075 (768484). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0577 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0578 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0579 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0580 | 3 Phase fault on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0581 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0582 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0583 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0584 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0585 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0586 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0587 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0588 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0589 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0590 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0591 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0592 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0593 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0594 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0595 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0596 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0597 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to TCBURNS4 (532994) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0598 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0599 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0600 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0601 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0602 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0603 | 3 Phase fault on CENTENN4 138.00 (533034) 138 kV Bus a. Apply fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0604 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0605 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0606 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0607 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0608 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0609 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0610 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0611 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0612 | 3 Phase fault on WACO S 4 138.00 (533071) 138 kV Bus a. Apply fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0613 | 3 Phase fault on WACO 4 138.00 (533072) 138 kV Bus a. Apply fault at the WACO 4 138.00 (533072) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0614 | 3 Phase fault on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0615 | 3 Phase fault on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0616 | 3 Phase fault on LANG 3 115.00 (533304) 115 kV Bus a. Apply fault at the LANG 3 115.00 (533304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0617 | 3 Phase fault on READING3 115.00 (533306) 115 kV Bus a. Apply fault at the READING3 115.00 (533306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. READING3 (533306) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0618 | 3 Phase fault on FLORENC3 115.00 (533366) 115 kV Bus a. Apply fault at the FLORENC3 115.00 (533366) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0619 | 3 Phase fault on SPRGCRK3 115.00 (533380) 115 kV Bus a. Apply fault at the SPRGCRK3 115.00 (533380) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0620 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0621 | 3 Phase fault on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0622 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0623 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0624 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0625 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to BURLIND2 (533625) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0626 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to CC1BURL2 (533628) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0627 | 3 Phase fault on ALTAMNT2 69.000 (533671) 69 kV Bus a. Apply fault at the ALTAMNT2 69.000 (533671) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0628 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODESH2 (533699) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0629 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0630 | 3 Phase fault on YELLOWJ2 69.000 (533692) 69 kV Bus a. Apply fault at the YELLOWJ2 69.000 (533692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YELLOWJ2 (533692) 69.0 kV to NEW ALB2 (533701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0631 | 3 Phase fault on LABETTE2 69.000 (533695) 69 kV Bus a. Apply fault at the LABETTE2 69.000 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0632 | 3 Phase fault on NEODJCT2 69.000 (533700) 69 kV Bus a. Apply fault at the NEODJCT2 69.000 (533700) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEODJCT2 (533700) 69.0 kV to RA6BROO2 (533707) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0633 | 3 Phase fault on NEW ALB2 69.000 (533701) 69 kV Bus a. Apply fault at the NEW ALB2 69.000 (533701) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEW ALB2 (533701) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0634 | 3 Phase fault on ORDNCE 2 69.000 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 69.000 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0635 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0636 | 3 Phase fault on CANALS 2 69.000 (533784) 69 kV Bus a. Apply fault at the CANALS 2 69.000 (533784) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0637 | 3 Phase fault on CANALS 2 69.000 (533784) 69 kV Bus a. Apply fault at the CANALS 2 69.000 (533784) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0638 | 3 Phase fault on CHENEY 2 69.000 (533785) 69 kV Bus a. Apply fault at the CHENEY 2 69.000 (533785) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHENEY 2 (533785) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0639 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0640 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCAN 2 (533850) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0641 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0642 | 3 Phase fault on GLENDAL2 69.000 (533797) 69 kV Bus a. Apply fault at the GLENDAL2 69.000 (533797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL2 (533797) 69.0 kV to OLIVER 2 (533826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0643 | 3 Phase fault on GLENDAL2 69.000 (533797) 69 kV Bus a. Apply fault at the GLENDAL2 69.000 (533797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL2 (533797) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0644 | 3 Phase fault on HAYSV 2 69.000 (533803) 69 kV Bus a. Apply fault at the HAYSV 2 69.000 (533803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYSV 2 (533803) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0645 | 3 Phase fault on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0646 | 3 Phase fault on HOOVERS2 69.000 (533806) 69 kV Bus a. Apply fault at the HOOVERS2 69.000 (533806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0647 | 3 Phase fault on LIN 2 69.000 (533812) 69 kV Bus a. Apply fault at the LIN 2 69.000 (533812) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0648 | 3 Phase fault on OAKLAWN2 69.000 (533824) 69 kV Bus a. Apply fault at the OAKLAWN2 69.000 (533824) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAWN2 (533824) 69.0 kV to OLIVER 2 (533826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0649 | 3 Phase fault on PLAZA E2 69.000 (533829) 69 kV Bus a. Apply fault at the PLAZA E2 69.000 (533829) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0650 | 3 Phase fault on RIPLEYW2 69.000 (533832) 69 kV Bus a. Apply fault at the RIPLEYW2 69.000 (533832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIPLEYW2 (533832) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0651 | 3 Phase fault on GALE TP2 69.000 (533845) 69 kV Bus a. Apply fault at the GALE TP2 69.000 (533845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALE TP2 (533845) 69.0 kV to SG4ANDL2 (533872) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0652 | 3 Phase fault on GALE TP2 69.000 (533845) 69 kV Bus a. Apply fault at the GALE TP2 69.000 (533845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALE TP2 (533845) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0653 | 3 Phase fault on PLAZA M2 69.000 (533857) 69 kV Bus a. Apply fault at the PLAZA M2 69.000 (533857) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0654 | 3 Phase fault on GODDTAP2 69.000 (533879) 69 kV Bus a. Apply fault at the GODDTAP2 69.000 (533879) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GODDTAP2 (533879) 69.0 kV to GODDARD2 (533880) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0655 | 3 Phase fault on RAGO 4 138.00 (539000) 138 kV Bus a. Apply fault at the RAGO 4 138.00 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0656 | 3 Phase fault on NW-DGTP3 115.00 (539628) 115 kV Bus a. Apply fault at the NW-DGTP3 115.00 (539628) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DGTP3 (539628) 115.0 kV to W-DODGE3 (539699) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0657 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0658 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0659 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0660 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0661 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0662 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0663 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0664 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0665 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0666 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0667 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0668 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0669 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0670 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0671 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0672 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0673 | 3 Phase fault on WBURGE_CAP5 161.00 (541148) 161 kV Bus a. Apply fault at the WBURGE_CAP5 161.00 (541148) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE_CAP5 (541148) 161.0 kV to WBURGE 5 (541228) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0674 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0675 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0676 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0677 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0678 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0679 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD unit (541171) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0680 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD unit (541171) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0681 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD unit (541171) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0682 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0683 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0684 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0685 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0686 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0687 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0688 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0689 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0690 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to POPE (541349) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0691 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0692 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0693 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0694 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0695 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0696 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0697 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0698 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0699 | 3 Phase fault on KCI 5 161.00 (541212) 161 kV Bus a. Apply fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCI 5 (541212) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0700 | 3 Phase fault on KCI 5 161.00 (541212) 161 kV Bus a. Apply fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCI 5 (541212) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0701 | 3 Phase fault on FRLVW 5 161.00 (541213) 161 kV Bus a. Apply fault at the FRLVW 5 161.00 (541213) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRLVW 5 (541213) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0702 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0703 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0704 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0705 | 3 Phase fault on RAYTOWN5 161.00 (541219) 161 kV Bus a. Apply fault at the RAYTOWN5 161.00 (541219) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0706 | 3 Phase fault on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0707 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0708 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0709 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0710 | 3 Phase fault on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 5 (541229) 161.0 kV to LEX161 5 (541232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0711 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0712 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0713 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0714 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0715 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0716 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0717 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0718 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0719 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0720 | 3 Phase fault on EAST 5 161.00 (541254) 161 kV Bus a. Apply fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0721 | 3 Phase fault on IND PRK5 161.00 (541256) 161 kV Bus a. Apply fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0722 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0723 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0724 | 3 Phase fault on KNOSTER2 69.000 (541270) 69 kV Bus a. Apply fault at the KNOSTER2 69.000 (541270) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOSTER2 (541270) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0725 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to KELHYS 2 (541273) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0726 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0727 | 3 Phase fault on SEDS 2 69.000 (541272) 69 kV Bus a. Apply fault at the SEDS 2 69.000 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0728 | 3 Phase fault on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0729 | 3 Phase fault on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0730 | 3 Phase fault on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0731 | 3 Phase fault on COLECMP2 69.000 (541276) 69 kV Bus a. Apply fault at the COLECMP2 69.000 (541276) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLECMP2 (541276) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0732 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0733 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0734 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0735 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBW5 (541336) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0736 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0737 | 3 Phase fault on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161.0 kV to WAFBE5 (541338) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0738 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0739 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0740 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0741 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0742 | 3 Phase fault on IATAN5 161.00 (541350) 161 kV Bus a. Apply fault at the IATAN5 161.00 (541350) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0743 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0744 | 3 Phase fault on MONSERTP 69.000 (541524) 69 kV Bus a. Apply fault at the MONSERTP 69.000 (541524) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONSERTP (541524) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0745 | 3 Phase fault on KNOSTERTP 69.000 (541534) 69 kV Bus a. Apply fault at the KNOSTERTP 69.000 (541534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOSTERTP (541534) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0746 | 3 Phase fault on LAMONTETP 69.000 (541535) 69 kV Bus a. Apply fault at the LAMONTETP 69.000 (541535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMONTETP (541535) 69.0 kV to LAMONTE (541536) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0747 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0748 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0749 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0750 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY_CAP 5 (542944) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0751 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0752 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0753 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0754 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0755 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0756 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0757 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0758 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0759 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0760 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0761 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0762 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0763 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0764 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0765 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0766 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0767 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0768 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0769 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0770 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0771 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0772 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0773 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0774 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0775 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0776 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0777 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0778 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0779 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 4.75 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 4.75 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Unstable oscillatory active power response and damping issue was observed at WCGS U1 (532751) unit. The following CQ units were found to contribute to the issue: GEN-2022-004: PTDF = 0.07262 GEN-2022-054: PTDF = 0.17717 GEN-2022-214: PTDF = 0.0669 | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0780 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0781 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0782 | 3 Phase fault on TROOST 5 161.00 (542986) 161 kV Bus a. Apply fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0783 | 3 Phase fault on TROOST 5 161.00 (542986) 161 kV Bus a. Apply fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0784 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0785 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0786 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0787 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0788 | 3 Phase fault on CROSTWN5 161.00 (542990) 161 kV Bus a. Apply fault at the CROSTWN5 161.00 (542990) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSTWN5 (542990) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0789 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0790 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0791 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0792 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0793 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to ROEPARK5 (543040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0794 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0795 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0796 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0797 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0798 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0799 | 3 Phase fault on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0800 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0801 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0802 | 3 Phase fault on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0803 | 3 Phase fault on CLAYCM15 161.00 (543022) 161 kV Bus a. Apply fault at the CLAYCM15 161.00 (543022) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLAYCM15 (543022) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0804 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0805 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0806 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0807 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0808 | 3 Phase fault on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to ROEPARK5 (543040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0809 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0810 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0811 | 3 Phase fault on OXFORD 5 161.00 (543046) 161 kV Bus a. Apply fault at the OXFORD 5 161.00 (543046) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 5 (543046) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0812 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0813 | 3 Phase fault on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0814 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0815 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0816 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0817 | 3 Phase fault on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSTVAL5 (543077) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0818 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0819 | 3 Phase fault on SUGRCRK_N2 69.000 (543089) 69 kV Bus a. Apply fault at the SUGRCRK_N2 69.000 (543089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_N2 (543089) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0820 | 3 Phase fault on DUNCNRD2 69.000 (543091) 69 kV Bus a. Apply fault at the DUNCNRD2 69.000 (543091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0821 | 3 Phase fault on LIBRTYS2 69.000 (543095) 69 kV Bus a. Apply fault at the LIBRTYS2 69.000 (543095) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0822 | 3 Phase fault on SUGRCK_TP_W269.000 (543164) 69 kV Bus a. Apply fault at the SUGRCK_TP_W269.000 (543164) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0823 | 3 Phase fault on KAW 5 161.00 (546214) 161 kV Bus a. Apply fault at the KAW 5 161.00 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0824 | 3 Phase fault on KAW 5 161.00 (546214) 161 kV Bus a. Apply fault at the KAW 5 161.00 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0825 | 3 Phase fault on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to MILLST 5 (546224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0826 | 3 Phase fault on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0827 | 3 Phase fault on SCAM66 2 69.000 (547409) 69 kV Bus a. Apply fault at the SCAM66 2 69.000 (547409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCAM66 2 (547409) 69.0 kV to SCM66T 2 (547455) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0828 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0829 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to SEK225 2 (547413) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0830 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to SMN425 2 (547414) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0831 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to SHR444 2 (547415) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0832 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0833 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to CHE299 2 (547417) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0834 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to CHE300 2 (547418) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0835 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0836 | 3 Phase fault on CHE300 2 69.000 (547418) 69 kV Bus a. Apply fault at the CHE300 2 69.000 (547418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE300 2 (547418) 69.0 kV to TWN388 2 (547419) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0837 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0838 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0839 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0840 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0841 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0842 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0843 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0844 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0845 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0846 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0847 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0848 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0849 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0850 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0851 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0852 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0853 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0854 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0855 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0856 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0857 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0858 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0859 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0860 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0861 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0862 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0863 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0864 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0865 | 3 Phase fault on GAT258 2 69.000 (547551) 69 kV Bus a. Apply fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0866 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0867 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0868 | 3 Phase fault on GAL278 2 69.000 (547555) 69 kV Bus a. Apply fault at the GAL278 2 69.000 (547555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAL278 2 (547555) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0869 | 3 Phase fault on COM381T2 69.000 (547579) 69 kV Bus a. Apply fault at the COM381T2 69.000 (547579) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COM381T2 (547579) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0870 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0871 | 3 Phase fault on JOP389 2 69.000 (547592) 69 kV Bus a. Apply fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0872 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0873 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0874 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0875 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0876 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0877 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0878 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0879 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0880 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0881 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0882 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0883 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0884 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0885 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0886 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0887 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0888 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0889 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0890 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0891 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0892 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0893 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0894 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0895 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0896 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0897 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0898 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0899 | 3 Phase fault on MALONEY7 115.00 (640265) 115 kV Bus a. Apply fault at the MALONEY7 115.00 (640265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0900 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0901 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0902 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0903 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0904 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0905 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0906 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0907 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0908 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0909 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0910 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0911 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | The Grand Prairie Wind Units (645065, 645066, 645067 and 645068) become unstable following the fault clearance and protection trips the units. Reducing the critical clearing time to 2.7 cycles mitigates the issue. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0912 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0913 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0914 | 3 Phase fault on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284) and frequency protection trips G19-053 (763849) and G19-055 (763872). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0915 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT11_2 (543663) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0916 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT12_2 (543664) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0917 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5KINGDMB1 (300090) 161.0 kV to 7KINGDM (300043) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0918 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0919 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF3 (301506) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0920 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0921 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BARNET (300618) 69.0 kV to 5BARNET (300057) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0922 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOONE (300493) 69.0 kV to 5BOONE (300061) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0923 | 3 Phase fault on 5CALIF 161.00 (300063) 161 kV Bus a. Apply fault at the 5CALIF 161.00 (300063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 5CALIF (300063) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0924 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLARK (300802) 69.0 kV to 5CLARK (300070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0925 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0926 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0927 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0928 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHRP (300302) 69.0 kV to 5LATHRP (300091) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0929 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0930 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0931 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0932 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0933 | 3 Phase fault on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PLATCTY (300307) 69.0 kV to 5PLATCTY (301552) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0934 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0935 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0936 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0937 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0938 | 3 Phase fault on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PERCHE (343004) 161.0 kV to 2PERCHE (343005) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0939 | 3 Phase fault on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PERCHE (343004) 161.0 kV to 2PERCHE2 (343052) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0940 | 3 Phase fault on 5GRINDSTN 161.00 (343014) 161 kV Bus a. Apply fault at the 5GRINDSTN 161.00 (343014) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GRINDSTN (343006) 69.0 kV to 5GRINDSTN (343014) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0941 | 3 Phase fault on 5APCH FLT 161.00 (344028) 161 kV Bus a. Apply fault at the 5APCH FLT 161.00 (344028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0942 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0943 | 3 Phase fault on 5LATHROP 161.00 (344923) 161 kV Bus a. Apply fault at the 5LATHROP 161.00 (344923) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHROP (346093) 69.0 kV to 5LATHROP (344923) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0944 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0945 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0946 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0947 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0948 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0949 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0950 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0951 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to CATOOSA4 (509790) 138.0 kV to CATTER1 1 (512833) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0952 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to CATOOSA4 (509790) 138.0 kV to CATTER2 1 (512834) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0953 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0954 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0955 | 3 Phase fault on PENSA 5 161.00 (512654) 161 kV Bus a. Apply fault at the PENSA 5 161.00 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to PENSA 2 (512628) 69.0 kV to PENSA 1 (512841) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0956 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0957 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0958 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0959 | 3 Phase fault on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138.0 kV to WAKITA 2 (521085) 69.0 kV to WAKITA_13.8 (520435) 13.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0960 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0961 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0962 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0963 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0964 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0965 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0966 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0967 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0968 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0969 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0970 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0971 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0972 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0973 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0974 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0975 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0976 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0977 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 2X1 (532840) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0978 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0979 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0980 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0981 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0982 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0983 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0984 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0985 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0986 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0987 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0988 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0989 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0990 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0991 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0992 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0993 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MCDOWEL3 (533335) 115.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0994 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0995 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0996 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0997 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0998 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0999 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1000 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1001 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1002 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1003 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1004 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1005 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1006 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1007 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1008 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1009 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1010 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1011 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1012 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1013 | 3 Phase fault on 17TH 4 138.00 (533064) 138 kV Bus a. Apply fault at the 17TH 4 138.00 (533064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1014 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1015 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1016 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1017 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1018 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1019 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1020 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1021 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1022 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1023 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1024 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1025 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN2 (533876) 69.0 kV to FRANKLIN5 (532938) 161.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1026 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1027 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1028 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1029 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1030 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD unit (541171) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1031 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD unit (541171) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1032 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK unit (641514) and OUTLAW unit (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1033 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1034 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1035 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1036 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1037 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 2 (541269) 69.0 kV to WBURGE 5 (541228) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1038 | 3 Phase fault on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 2 (541267) 69.0 kV to ODESSA 5 (541229) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1039 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1040 | 3 Phase fault on LEX161 5 161.00 (541232) 161 kV Bus a. Apply fault at the LEX161 5 161.00 (541232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX69 2 (541264) 69.0 kV to LEX161 5 (541232) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1041 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1042 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1043 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1044 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to LBRTYST5 (541248) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1045 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1046 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1047 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1048 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1049 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to ATLNTIC3 (533279) 115.0 kV to ATLNT2X1 (533916) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1050 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to ATLNTIC3 (533279) 115.0 kV to ATLNT1X1 (533915) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1051 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1052 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1053 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1054 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1055 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1056 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1057 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1058 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1059 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1060 | 3 Phase fault on IATAN 7 345.00 (542982) 345 kV Bus a. Apply fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD1_1 (541171). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1061 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1062 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips ROCKCK unit (641514) and OUTLAW unit (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1063 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage protection trips ROCKCK unit (641514) and OUTLAW unit (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1064 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1065 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1066 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1067 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1068 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1069 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1070 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1071 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1072 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1073 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1074 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1075 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG8 (640101) 69.0 kV to CAMBRIG7 (640100) 115.0 kV to CAMBRIDGET19 (643028) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1076 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 8 (640168) 69.0 kV to ENDERS 7 (640167) 115.0 kV to ENDERS T1 9 (643055) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1077 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1078 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1079 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT8 (640288) 69.0 kV to N.PLATT7 (640287) 115.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1080 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1081 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1082 | 3 Phase fault on VSC2_3 345.00 (992003) 345 kV Bus a. Apply fault at the VSC2_3 345.00 (992003) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VSC2_3 (992003) 345.0 kV to VSC2_2 (992002) 276.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1083 | 3 Phase fault on VSC2_3 345.00 (992003) 345 kV Bus a. Apply fault at the VSC2_3 345.00 (992003) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VSC2_3 (992003) 345.0 kV to VSC2_6 (992006) 276.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1084 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GI91 (99915). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1085 | 3 Phase fault on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1086 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1087 | 3 Phase fault on JOP430 2 69.000 (547608) 69 kV Bus a. Apply fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP430 2 (547608) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1088 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1089 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1090 | 3 Phase fault on SUB M 69.000 (548815) 69 kV Bus a. Apply fault at the SUB M 69.000 (548815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1091 | 3 Phase fault on SUB N 69.000 (548821) 69 kV Bus a. Apply fault at the SUB N 69.000 (548821) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1092 | 3 Phase fault on SUB C 69.000 (548825) 69 kV Bus a. Apply fault at the SUB C 69.000 (548825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB C (548825) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1093 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0001 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0002 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0003 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0004 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0005 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0006 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0007 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0008 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0009 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0010 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0011 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0013 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0014 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0015 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0016 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0017 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0018 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0019 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0020 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0021 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0022 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0023 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0024 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0025 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0026 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0027 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0028 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0029 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0030 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0031 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0032 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD unit (541171) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0033 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD unit (541171) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD unit (541171) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0035 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0036 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0037 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0038 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0039 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0040 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0041 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0042 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0043 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0044 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0045 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0046 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0048 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0049 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD unit (541171) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips LAKERD unit (541171) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0051 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0001 | Single Phase Fault with Stuck Breaker on 5GRINDSTN 161.00 (343014) 161 kV Bus a. Apply Fault at the 5GRINDSTN 161.00 (343014) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BOONE (300061) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 b.2. 2GRINDSTN (343006) 69.0 kV to 5GRINDSTN (343014) 161.0 kV Two Winding #1 b.3. 5REBEL (343007) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0002 | Single Phase Fault with Stuck Breaker on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply Fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 b.2. 5PERCHE (343004) 161.0 kV to 2PERCHE (343005) 69.0 kV Two Winding #1 b.3. 5PERCHE (343004) 161.0 kV to 2PERCHE2 (343052) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0003 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0007 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0008 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0010 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 b.3. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0011 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0012 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0013 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0014 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0015 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0016 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-100-TAP (768980) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0017 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0018 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0019 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0020 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0021 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0022 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0023 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0024 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0025 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0026 | Single Phase Fault with Stuck Breaker on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply Fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 b.3. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 b.4. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 b.5. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0027 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-100-TAP (768980) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0028 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0029 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 b.4. SALSBRY5 (543062) 161.0 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0030 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0031 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0032 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0033 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0034 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0035 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NEAST_DG1 (543160) 4.2 kV to NE CT11 (542958) 13.8 kV Two Winding #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 b.6. NEASTN5 (543666) 161.0 kV to Load #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0036 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEAST_DG1 (543160) 4.2 kV to NE CT11 (542958) 13.8 kV Two Winding #1 b.3. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0037 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # b.6. NEASTN5 (543666) 161.0 kV to Load #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0038 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NE CT17 (542983) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT18 (542984) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0039 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NE CT17 (542983) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT18 (542984) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0040 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0041 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0042 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0043 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 b.2. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0044 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0045 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0046 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0047 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0048 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0049 | Single Phase Fault with Stuck Breaker on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply Fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT7 1 (542963) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.2. HAWCT8 1 (542964) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.3. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0050 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to Load #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0051 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NRTHST_B90_1 (543082) 13.8 kV to Load #90 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0052 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NRTHST_B34_1 (543081) 13.8 kV to Load #34 b.3. NEASTN5 (543666) 161.0 kV to Load #78 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0053 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NRTHST_B34_1 (543081) 13.8 kV to Load #34 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0054 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # b.2. NEASTN5 (543666) 161.0 kV to Load #78 b.3. NRTHST_B90_1 (543082) 13.8 kV to Load #90 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0055 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0056 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0057 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0058 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0059 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.4. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0060 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0061 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0062 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0063 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0064 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0065 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0066 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0067 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Unstable oscillatory active power response and damping issue was observed at WCGS U1 (532751) unit. The following CQ units were found to contribute to the issue: GEN-2022-006: PTDF = 0.0820 GEN-2022-013: PTDF = 0.0998 GEN-2022-024: PTDF = 0.0998 GEN-2022-054: PTDF = 0.0988 | Reroute the existing LaCygne – Neosho 345kV line to tap the exiting GEN-2020-007 tap switching station
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0068 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 b.2. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0069 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0070 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0071 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0072 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0073 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0074 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0075 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0076 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0077 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0078 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0079 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0080 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0081 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0082 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0083 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0084 | Single Phase Fault with Stuck Breaker on COLBY 3 115.00 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0085 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.3. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0086 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 b.2. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 b.4. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0087 | Single Phase Fault with Stuck Breaker on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply Fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 b.2. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 b.3. ENDERS 7 (640167) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #1 b.4. ENDERS 7 (640167) 115.0 kV to ENDERS 8 (640168) 69.0 kV to ENDERS T1 9 (643055) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0088 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to MCCOOK G (640017) 13.8 kV Two Winding #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.4. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.5. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 b.6. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0089 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.4. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.5. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0090 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.3. N.PLATTG (640018) 13.8 kV to N.PLATT9 (640289) 34.5 kV to N.PLATT7 (640287) 115.0 kV Three Winding #1 b.4. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 b.6. N.PLATT7 (640287) 115.0 kV to N.PLATT8 (640288) 69.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 b.7. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to N.PLATTG (640018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0091 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.3. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.4. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.5. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 b.6. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 b.7. N.PLATT7 (640287) 115.0 kV to N.PLATT8 (640288) 69.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 b.8. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to N.PLATTG (640018) 13.8 kV Three Winding #1 b.9. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to NORTHPLT T79 (643107) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0092 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 b.3. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0093 | Single Phase Fault with Stuck Breaker on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply Fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.6. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.7. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.8. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.9. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 b.10. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.11. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.12. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.13. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.14. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0094 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.4. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.7. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.8. HARPER 4 (539668) 138.0 kV to HARPER 1 (539713) 34.5 kV to HARPER-T (539913) 8.7 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0095 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0096 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0097 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0098 | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply Fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.3. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.4. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.8. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0099 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0100 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.2. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.3. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.4. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.6. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.9. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0101 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.2. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.3. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0102 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 b.4. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0103 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0104 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0105 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0106 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0107 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0108 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0109 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0110 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0111 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0112 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0113 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-065-TAP (768280) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0114 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0115 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0116 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0117 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 b.5. HOLCOMB3 (531448) 115.0 kV to Load #S1 b.6. HOLCOMB3 (531448) 115.0 kV to Load #S2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0118 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0119 | Single Phase Fault with Stuck Breaker on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply Fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. FTDODGP1 (539670) 15.0 kV to FTDODGE3 (539671) 115.0 kV Two Winding #1 b.4. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.5. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 b.6. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. FTDODGE3 (539671) 115.0 kV to FTDDGDV1 (539715) 34.5 kV to FTDODG-T (539915) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0120 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0121 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0122 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0123 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0124 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0125 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0126 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0127 | Single Phase Fault with Stuck Breaker on SPRINGH3 115.00 (533267) 115 kV Bus a. Apply Fault at the SPRINGH3 115.00 (533267) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.4. SPRINGH3 (533267) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0128 | Single Phase Fault with Stuck Breaker on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply Fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.4. SPRINGH3 (533267) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0129 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 b.4. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 2X1 (532840) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0130 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0131 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0132 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0133 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0134 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0135 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC6 1 (532743) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0136 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0137 | Single Phase Fault with Stuck Breaker on GEARY 7 345.00 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.3. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0138 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.3. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0139 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0140 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0141 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0142 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0143 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0144 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0145 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0146 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0147 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0148 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0149 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0150 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0151 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0152 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0153 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0154 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0155 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0156 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0157 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to GEN-2016-174 (588250) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0158 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0159 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0160 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0161 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0162 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0163 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0164 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0165 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0166 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0167 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0168 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0169 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. BLUMILS5 (543004) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0170 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0171 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0172 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY (548806) 69.0 kV to Load #T2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0173 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0174 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0175 | Single Phase Fault with Stuck Breaker on BLUVLY 69.000 (548806) 69 kV Bus a. Apply Fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.3. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.4. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.5. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 b.6. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 b.7. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 b.8. BLUVLY (548806) 69.0 kV to Load #T1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0176 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.3. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0177 | Single Phase Fault with Stuck Breaker on SUB N-161 161.00 (548820) 161 kV Bus a. Apply Fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0178 | Single Phase Fault with Stuck Breaker on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply Fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 b.2. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0179 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0181 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0182 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0183 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0184 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0185 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0186 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0187 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0188 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0189 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0190 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0191 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0192 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0193 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0194 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0195 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0196 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP5 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0197 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0198 | Single Phase Fault with Stuck Breaker on AFTON 5 161.00 (512632) 161 kV Bus a. Apply Fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.4. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0199 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.2. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.3. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0200 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.2. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.3. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.6. 1CHOTCT2 (300033) 16.0 kV to Load #P2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0201 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.2. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.3. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0202 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.5. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.6. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.7. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.8. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.9. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0203 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0204 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.6. 1CHOTCT4 (300020) 16.0 kV to Load #P1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0205 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.6. 1CHOTCT5 (300021) 16.0 kV to Load #P2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0206 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0207 | Single Phase Fault with Stuck Breaker on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply Fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.5. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0208 | Single Phase Fault with Stuck Breaker on 5APCH FLT 161.00 (344028) 161 kV Bus a. Apply Fault at the 5APCH FLT 161.00 (344028) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.2. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.4. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.5. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0209 | Single Phase Fault with Stuck Breaker on 5BARNET 161.00 (300057) 161 kV Bus a. Apply Fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.3. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.4. 2BARNET (300618) 69.0 kV to 5BARNET (300057) 161.0 kV Two Winding #1 b.5. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.6. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0210 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 161.00 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 161.00 (344234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5CALIF (300063) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.4. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.5. 1CALIF (346027) 34.5 kV to 5CALIF UE 2 (344234) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0211 | Single Phase Fault with Stuck Breaker on 5JC ZION 161.00 (344814) 161 kV Bus a. Apply Fault at the 5JC ZION 161.00 (344814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.2. 5MARIOSA (345027) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.3. 5JC ZION (344814) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #z b.4. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.5. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.6. 2JC ZION (346089) 69.0 kV to 5JC ZION (344814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0212 | Single Phase Fault with Stuck Breaker on 5ELDON 2 161.00 (344533) 161 kV Bus a. Apply Fault at the 5ELDON 2 161.00 (344533) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.3. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.4. 2BARNET (300618) 69.0 kV to 5BARNET (300057) 161.0 kV Two Winding #1 b.5. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.6. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.7. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.8. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 b.9. 1ELDON 2 (346045) 34.5 kV to 5ELDON 2 (344533) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0213 | Single Phase Fault with Stuck Breaker on 5ELDON 2 161.00 (344533) 161 kV Bus a. Apply Fault at the 5ELDON 2 161.00 (344533) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.2. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.3. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.4. 4OSAGE (345400) 138.0 kV to 4OSG_1&2TAP (345401) 138.0 kV Transmission Circuit #z b.5. 4OSAGE (345400) 138.0 kV to 4OSG_5&6TAP (345406) 138.0 kV Transmission Circuit #1 b.6. 4OSAGE (345400) 138.0 kV to 4OSG_7&8TAP (345407) 138.0 kV Transmission Circuit #1 b.7. 4OSAGE (345400) 138.0 kV to 1OSAGE (346116) 34.5 kV Two Winding #1 b.8. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.9. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 b.10. 1ELDON 2 (346045) 34.5 kV to 5ELDON 2 (344533) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0214 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 161.00 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 161.00 (344234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CALIF (300063) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.2. 2CALIF (300550) 69.0 kV to 5CALIF (300063) 161.0 kV Two Winding #2 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.4. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z b.5. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.6. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 b.7. 1CALIF (346027) 34.5 kV to 5CALIF UE 2 (344234) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0215 | Single Phase Fault with Stuck Breaker on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply Fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0216 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.4. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.5. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0217 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0218 | Single Phase Fault with Stuck Breaker on RIV167 5 161.00 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0219 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0220 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.4. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0221 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0222 | Single Phase Fault with Stuck Breaker on FIR417 5 161.00 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 161.00 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0223 | Single Phase Fault with Stuck Breaker on OAK432 5 161.00 (547494) 161 kV Bus a. Apply Fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0224 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. OAK432 5 (547494) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0225 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0226 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0227 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0228 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0229 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0230 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0231 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0232 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0233 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0234 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0235 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0236 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0237 | Single Phase Fault with Stuck Breaker on 5APCH TP 161.00 (344026) 161 kV Bus a. Apply Fault at the 5APCH TP 161.00 (344026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.4. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.5. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0238 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0239 | Single Phase Fault with Stuck Breaker on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply Fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5LOYMART 1 (344040) 161.0 kV to 5LOYMART 2 (344041) 161.0 kV Transmission Circuit #z b.3. 5LOYMART 1 (344040) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.4. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.5. 5J994 SUB (344656) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.6. 5GUTHRIE 1 (344677) 161.0 kV to 5GUTHRIE 2 (344678) 161.0 kV Transmission Circuit #z b.7. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.8. 1LOYMART 1 (346010) 12.5 kV to 5LOYMART 1 (344040) 161.0 kV Two Winding #1 b.9. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0240 | Single Phase Fault with Stuck Breaker on 5ELDON 2 161.00 (344533) 161 kV Bus a. Apply Fault at the 5ELDON 2 161.00 (344533) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.2. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.3. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.4. 4OSAGE (345400) 138.0 kV to 4OSG_1&2TAP (345401) 138.0 kV Transmission Circuit #z b.5. 4OSAGE (345400) 138.0 kV to 4OSG_3&4TAP (345404) 138.0 kV Transmission Circuit #z b.6. 4OSAGE (345400) 138.0 kV to 4OSG_5&6TAP (345406) 138.0 kV Transmission Circuit #1 b.7. 4OSAGE (345400) 138.0 kV to 4OSG_7&8TAP (345407) 138.0 kV Transmission Circuit #1 b.8. 4OSAGE (345400) 138.0 kV to 1OSAGE (346116) 34.5 kV Two Winding #1 b.9. 4OSAGE (345400) 138.0 kV to 1OSAGE (346116) 34.5 kV Two Winding #2 b.10. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.11. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 b.12. 1ELDON 2 (346045) 34.5 kV to 5ELDON 2 (344533) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0241 | Single Phase Fault with Stuck Breaker on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply Fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LOYMART 1 (344040) 161.0 kV to 5LOYMART 2 (344041) 161.0 kV Transmission Circuit #z b.2. 5LOYMART 1 (344040) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.3. 5J994 SUB (344656) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.4. 5GUTHRIE 1 (344677) 161.0 kV to 5GUTHRIE 2 (344678) 161.0 kV Transmission Circuit #z b.5. 5GUTHRIE 2 (344678) 161.0 kV to 5MONTGMRY 1 (345231) 161.0 kV Transmission Circuit #1 b.6. 5GUTHRIE 2 (344678) 161.0 kV to 5MOREAU 1 (345239) 161.0 kV Transmission Circuit #1 b.7. 1LOYMART 1 (346010) 12.5 kV to 5LOYMART 1 (344040) 161.0 kV Two Winding #1 b.8. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0242 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.6. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.7. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0243 | Single Phase Fault with Stuck Breaker on 5JC ZION 161.00 (344814) 161 kV Bus a. Apply Fault at the 5JC ZION 161.00 (344814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.2. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.3. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.4. 5JC ZION (344814) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #z b.5. 2JC ZION (346089) 69.0 kV to 5JC ZION (344814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0244 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0245 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.4. NE CT17 (542983) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT18 (542984) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0246 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0247 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0248 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0249 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0250 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0251 | Single Phase Fault with Stuck Breaker on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply Fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.6. NKMA2 1 (530630) 12.5 kV to NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0252 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0253 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.4. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.5. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0254 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0255 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.4. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.5. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0256 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0257 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0258 | Single Phase Fault with Stuck Breaker on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply Fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0259 | Single Phase Fault with Stuck Breaker on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. RULETON3 (531357) 115.0 kV to LAWNRID3 (531368) 115.0 kV Transmission Circuit #1 b.5. BIRDCTY3 (531365) 115.0 kV to STFRAN 3 (531370) 115.0 kV Transmission Circuit #1 b.6. BIRDCTY3 (531365) 115.0 kV to MCDONLD3 (531487) 115.0 kV Transmission Circuit #1 b.7. LAWNRID3 (531368) 115.0 kV to STFRANT3 (531471) 115.0 kV Transmission Circuit #1 b.8. STFRAN 3 (531370) 115.0 kV to STFRANT3 (531471) 115.0 kV Transmission Circuit #1 b.9. CSTFRAN3 (531441) 115.0 kV to STFRANT3 (531471) 115.0 kV Transmission Circuit #1 b.10. MCDONLD3 (531487) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.11. BVERVLLY (531488) 115.0 kV to ONEOK 3 (531489) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0260 | Single Phase Fault with Stuck Breaker on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. LUDELLT3 (531220) 115.0 kV to LUDELL 3 (531221) 115.0 kV Transmission Circuit #1 b.5. LUDELLT3 (531220) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.6. LUDELLT3 (531220) 115.0 kV to HERNDON3 (531367) 115.0 kV Transmission Circuit #1 b.7. ATWODSW3 (531364) 115.0 kV to NATWOOD3 (531369) 115.0 kV Transmission Circuit #1 b.8. HERNDON3 (531367) 115.0 kV to JOHNSON3 (531371) 115.0 kV Transmission Circuit #1 b.9. JOHNSON3 (531371) 115.0 kV to OBER T 3 (531457) 115.0 kV Transmission Circuit #1 b.10. NORCATR3 (531372) 115.0 kV to RHOADES3 (531373) 115.0 kV Transmission Circuit #1 b.11. NORCATR3 (531372) 115.0 kV to OBER T 3 (531457) 115.0 kV Transmission Circuit #1 b.12. OBER T 3 (531457) 115.0 kV to OBERLIN3 (531458) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0261 | Single Phase Fault with Stuck Breaker on GEM_SW 3 115.00 (530713) 115 kV Bus a. Apply Fault at the GEM_SW 3 115.00 (530713) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. SEGNTP 3 (530682) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.3. GEM_SW 3 (530713) 115.0 kV to COLBY_PUMP3 (530716) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0262 | Single Phase Fault with Stuck Breaker on SEGNTP 3 115.00 (530682) 115 kV Bus a. Apply Fault at the SEGNTP 3 115.00 (530682) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.3. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.4. SEGNTP 3 (530682) 115.0 kV to SEGUIN 3 (530683) 115.0 kV Transmission Circuit #1 b.5. SEGNTP 3 (530682) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.6. SEGUIN 3 (530683) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0263 | Single Phase Fault with Stuck Breaker on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply Fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.2. PH RUN 3 (530559) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 b.3. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. SEGNTP 3 (530682) 115.0 kV to SEGUIN 3 (530683) 115.0 kV Transmission Circuit #1 b.5. SEGUIN 3 (530683) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0264 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.5. BEACH 3 (530557) 115.0 kV to HILLCTY3 (531387) 34.5 kV Two Winding #1 b.6. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.7. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0265 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0266 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0267 | Single Phase Fault with Stuck Breaker on GMEC 3 115.00 (530676) 115 kV Bus a. Apply Fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0268 | Single Phase Fault with Stuck Breaker on SALINE 3 115.00 (530551) 115 kV Bus a. Apply Fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0269 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.5. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.6. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.7. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0270 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0271 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0272 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0273 | Single Phase Fault with Stuck Breaker on NESCTY 3 115.00 (530607) 115 kV Bus a. Apply Fault at the NESCTY 3 115.00 (530607) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NESCTY 3 (530607) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NESCTY 3 (530607) 115.0 kV to NESS-CT1 (539722) 34.5 kV to NES-CT-T (539924) 13.8 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0274 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.9. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0275 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.10. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0276 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0277 | Single Phase Fault with Stuck Breaker on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply Fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.2. PH RUN 3 (530559) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 b.3. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. ARNOLD3 (531409) 115.0 kV to GOVE 3 (531411) 115.0 kV Transmission Circuit #1 b.5. ARNOLD3 (531409) 115.0 kV to RANSOM 3 (531414) 115.0 kV Transmission Circuit #1 b.6. GOVE 3 (531411) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0278 | Single Phase Fault with Stuck Breaker on GODLNDT3 115.00 (531443) 115 kV Bus a. Apply Fault at the GODLNDT3 115.00 (531443) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. BREWSTR3 (531351) 115.0 kV to GOODLND3 (531353) 115.0 kV Transmission Circuit #1 b.3. BREWSTR3 (531351) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. GOODLND3 (531353) 115.0 kV to GODLNDT3 (531443) 115.0 kV Transmission Circuit #1 b.5. RULETON3 (531357) 115.0 kV to GODLNDT3 (531443) 115.0 kV Transmission Circuit #1 b.6. GODLNDT3 (531443) 115.0 kV to GOODCTY3 (531444) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0279 | Single Phase Fault with Stuck Breaker on MINGO 3 115.00 (531429) 115 kV Bus a. Apply Fault at the MINGO 3 115.00 (531429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0280 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.5. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0281 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.5. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.7. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0282 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0283 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0284 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0285 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0286 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0287 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0288 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0289 | Single Phase Fault with Stuck Breaker on SHAYS_230 230.00 (530610) 230 kV Bus a. Apply Fault at the SHAYS_230 230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0290 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 b.8. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0291 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-065-TAP (768280) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0292 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0293 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0294 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0295 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0296 | Single Phase Fault with Stuck Breaker on BUFLOCRK6 230.00 (530688) 230 kV Bus a. Apply Fault at the BUFLOCRK6 230.00 (530688) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.3. BUFLOCRK1 (530689) 34.5 kV to PRWNDCL1 (530701) 34.5 kV Transmission Circuit #1 b.4. PRWINDG1 (530690) 0.7 kV to PRWNDCL1 (530701) 34.5 kV Two Winding #1 b.5. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.8. BUFLOCRK6 (530688) 230.0 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0297 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0298 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0299 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0300 | Single Phase Fault with Stuck Breaker on COLBY 3 115.00 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to Load #1 b.2. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0301 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0302 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0303 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0304 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0305 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0306 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLM1G (640010) 23.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0307 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0308 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.3. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0309 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0310 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0311 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0312 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0313 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0314 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.3. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0315 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0316 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0317 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0318 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0319 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0320 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0321 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0322 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0323 | Single Phase Fault with Stuck Breaker on BARBER 5 161.00 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.3. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.4. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.5. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.6. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0324 | Single Phase Fault with Stuck Breaker on WOLCOTT5 161.00 (546669) 161 kV Bus a. Apply Fault at the WOLCOTT5 161.00 (546669) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.2. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.3. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0325 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0326 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.4. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 b.7. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0327 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0328 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0329 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0330 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0331 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0332 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0333 | Single Phase Fault with Stuck Breaker on J1490_POI 345.00 (44888) 345 kV Bus a. Apply Fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1490_POI (44888) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 b.2. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0334 | Single Phase Fault with Stuck Breaker on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply Fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 b.2. 7KINGDM (300043) 345.0 kV to 5KINGDMB1 (300090) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0335 | Single Phase Fault with Stuck Breaker on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply Fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to VSC2_3 (992003) 345.0 kV Transmission Circuit #1 b.2. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0336 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to 5MORGANXF2 (301622) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0337 | Single Phase Fault with Stuck Breaker on 5BOONE 161.00 (300061) 161 kV Bus a. Apply Fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BOONE (300061) 161.0 kV to 5MLRSBGB1 (300519) 161.0 kV Transmission Circuit #1 b.2. 5BOONE (300061) 161.0 kV to 2BOONE (300493) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0338 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 b.2. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0339 | Single Phase Fault with Stuck Breaker on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply Fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LATHRP (300091) 161.0 kV to 5MPLTAP (300036) 161.0 kV Transmission Circuit #1 b.2. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0340 | Single Phase Fault with Stuck Breaker on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply Fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 b.2. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0341 | Single Phase Fault with Stuck Breaker on 5NORTON 161.00 (300105) 161 kV Bus a. Apply Fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 b.2. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0342 | Single Phase Fault with Stuck Breaker on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply Fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 b.2. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0343 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to 2SEDALI (300541) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0344 | Single Phase Fault with Stuck Breaker on 5MCBAINB1 161.00 (300501) 161 kV Bus a. Apply Fault at the 5MCBAINB1 161.00 (300501) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB1 (300501) 161.0 kV to 5MCBAINB2 (301489) 161.0 kV Transmission Circuit #z1 b.2. 5MCBAINB1 (300501) 161.0 kV to 5BOONE (300061) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0345 | Single Phase Fault with Stuck Breaker on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply Fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0346 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0347 | Single Phase Fault with Stuck Breaker on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply Fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0348 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 b.2. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0349 | Single Phase Fault with Stuck Breaker on 5CALIF 161.00 (300063) 161 kV Bus a. Apply Fault at the 5CALIF 161.00 (300063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CALIF (300550) 69.0 kV to 5CALIF (300063) 161.0 kV Two Winding #2 b.2. 2CALIF (300550) 69.0 kV to 2FORTNA (300554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0350 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0351 | Single Phase Fault with Stuck Breaker on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply Fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 b.2. 5LAMAR (300794) 161.0 kV to 2LAMR (300651) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0352 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to 5JASPER (300950) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0353 | Single Phase Fault with Stuck Breaker on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply Fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PLATCTY (301552) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #z1 b.2. 5PLATCTY (301552) 161.0 kV to 2PLATCTY (300307) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0354 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0355 | Single Phase Fault with Stuck Breaker on MIDLTNT4 138.00 (514804) 138 kV Bus a. Apply Fault at the MIDLTNT4 138.00 (514804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.2. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0356 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0357 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0358 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0359 | Single Phase Fault with Stuck Breaker on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0360 | Single Phase Fault with Stuck Breaker on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply Fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to JAGGER 3 (531360) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0361 | Single Phase Fault with Stuck Breaker on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply Fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEOTI 3 (531428) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 b.2. LEOTI 3 (531428) 115.0 kV to SELKIRK3 (531434) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0362 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 b.2. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0363 | Single Phase Fault with Stuck Breaker on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply Fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 b.2. SCOTCTY3 (531433) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0364 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0365 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 b.2. SETAB 3 (531464) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0366 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #2 b.2. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0367 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0368 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0369 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0370 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0371 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0372 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0373 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0374 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0375 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0376 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0377 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0378 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0379 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0380 | Single Phase Fault with Stuck Breaker on BURNS 7 345.00 (532803) 345 kV Bus a. Apply Fault at the BURNS 7 345.00 (532803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURNS 7 (532803) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. BURNS 7 (532803) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0381 | Single Phase Fault with Stuck Breaker on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0382 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 7 (532770) 345.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 b.2. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0383 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 b.2. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0384 | Single Phase Fault with Stuck Breaker on BAKER 2 69.000 (532926) 69 kV Bus a. Apply Fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0385 | Single Phase Fault with Stuck Breaker on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 b.2. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0386 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. MARMTNW5 (532935) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0387 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.2. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0388 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to LITCH 5 (532932) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0389 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to MIDLTNT4 (514804) 138.0 kV Transmission Circuit #1 b.2. CRESWLN4 (532981) 138.0 kV to CRESWLS2 (533573) 69.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0390 | Single Phase Fault with Stuck Breaker on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply Fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 4 (532982) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0391 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0392 | Single Phase Fault with Stuck Breaker on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply Fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.2. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0393 | Single Phase Fault with Stuck Breaker on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0394 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 4 (532996) 138.0 kV to TIOGA 2 (533646) 69.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0395 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK4 (532997) 138.0 kV to BUTLER 4 (532987) 138.0 kV Transmission Circuit #1 b.2. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0396 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. ALTOONA4 (533001) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0397 | Single Phase Fault with Stuck Breaker on DEARING4 138.00 (533002) 138 kV Bus a. Apply Fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0398 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0399 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONTGOM4 (533004) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0400 | Single Phase Fault with Stuck Breaker on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply Fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0401 | Single Phase Fault with Stuck Breaker on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply Fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0402 | Single Phase Fault with Stuck Breaker on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply Fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to HALSTD 4 (533011) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0403 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.2. NEOSHOS4 (533020) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0404 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.2. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0405 | Single Phase Fault with Stuck Breaker on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply Fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0406 | Single Phase Fault with Stuck Breaker on BU11PON4 138.00 (533032) 138 kV Bus a. Apply Fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BU11PON4 (533032) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0407 | Single Phase Fault with Stuck Breaker on CENTENN4 138.00 (533034) 138 kV Bus a. Apply Fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0408 | Single Phase Fault with Stuck Breaker on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0409 | Single Phase Fault with Stuck Breaker on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply Fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0410 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0411 | Single Phase Fault with Stuck Breaker on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply Fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0412 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0413 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to EVANS N4 (533040) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0414 | Single Phase Fault with Stuck Breaker on FARBER 4 138.00 (533042) 138 kV Bus a. Apply Fault at the FARBER 4 138.00 (533042) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0415 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0416 | Single Phase Fault with Stuck Breaker on GILL W 4 138.00 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.2. GILL W 4 (533045) 138.0 kV to GILL E 4 (533044) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0417 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.2. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0418 | Single Phase Fault with Stuck Breaker on GILL 4 138.00 (533047) 138 kV Bus a. Apply Fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL 4 (533047) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0419 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0420 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERS4 (533050) 138.0 kV to HOOVERN4 (533049) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0421 | Single Phase Fault with Stuck Breaker on 47TH ST4 138.00 (533058) 138 kV Bus a. Apply Fault at the 47TH ST4 138.00 (533058) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0422 | Single Phase Fault with Stuck Breaker on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. ROSEHIL4 (533062) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0423 | Single Phase Fault with Stuck Breaker on WACO S 4 138.00 (533071) 138 kV Bus a. Apply Fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WACO S 4 (533071) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #1 b.2. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0424 | Single Phase Fault with Stuck Breaker on WACO 4 138.00 (533072) 138 kV Bus a. Apply Fault at the WACO 4 138.00 (533072) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 b.2. WACO 4 (533072) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0425 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0426 | Single Phase Fault with Stuck Breaker on 4CORNER3 115.00 (533158) 115 kV Bus a. Apply Fault at the 4CORNER3 115.00 (533158) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CORNER3 (533158) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.2. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0427 | Single Phase Fault with Stuck Breaker on OSAGE J3 115.00 (533171) 115 kV Bus a. Apply Fault at the OSAGE J3 115.00 (533171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE J3 (533171) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.2. OSAGE J3 (533171) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0428 | Single Phase Fault with Stuck Breaker on EAST ST3 115.00 (533301) 115 kV Bus a. Apply Fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.2. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0429 | Single Phase Fault with Stuck Breaker on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply Fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0430 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LANG 3 (533304) 115.0 kV to LANG 7 (532769) 345.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 b.2. LANG 3 (533304) 115.0 kV to EAST ST3 (533301) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0431 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 3 (533305) 115.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 b.2. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0432 | Single Phase Fault with Stuck Breaker on READING3 115.00 (533306) 115 kV Bus a. Apply Fault at the READING3 115.00 (533306) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. READING3 (533306) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 b.2. READING3 (533306) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0433 | Single Phase Fault with Stuck Breaker on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply Fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (533307) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0434 | Single Phase Fault with Stuck Breaker on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply Fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0435 | Single Phase Fault with Stuck Breaker on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.2. WEMPORI3 (533309) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0436 | Single Phase Fault with Stuck Breaker on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply Fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WMBROSJ3 (533311) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0437 | Single Phase Fault with Stuck Breaker on BURLJCT2 69.000 (533626) 69 kV Bus a. Apply Fault at the BURLJCT2 69.000 (533626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0438 | Single Phase Fault with Stuck Breaker on CC2SHAR2 69.000 (533629) 69 kV Bus a. Apply Fault at the CC2SHAR2 69.000 (533629) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC2SHAR2 (533629) 69.0 kV to CC5SHAR1 (533888) 12.5 kV Two Winding #1 b.2. CC2SHAR2 (533629) 69.0 kV to CC6SHAR1 (533889) 12.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0439 | Single Phase Fault with Stuck Breaker on CC3WEST2 69.000 (533630) 69 kV Bus a. Apply Fault at the CC3WEST2 69.000 (533630) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC3WEST2 (533630) 69.0 kV to BURLJCT2 (533626) 69.0 kV Transmission Circuit #1 b.2. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0440 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0441 | Single Phase Fault with Stuck Breaker on UN1ELSM2 69.000 (533647) 69 kV Bus a. Apply Fault at the UN1ELSM2 69.000 (533647) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UN1ELSM2 (533647) 69.0 kV to MARMATN2 (533639) 69.0 kV Transmission Circuit #1 b.2. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0442 | Single Phase Fault with Stuck Breaker on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply Fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0443 | Single Phase Fault with Stuck Breaker on LABETTS2 69.000 (533696) 69 kV Bus a. Apply Fault at the LABETTS2 69.000 (533696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0444 | Single Phase Fault with Stuck Breaker on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply Fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0445 | Single Phase Fault with Stuck Breaker on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply Fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0446 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 b.2. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0447 | Single Phase Fault with Stuck Breaker on BELL 2 69.000 (533783) 69 kV Bus a. Apply Fault at the BELL 2 69.000 (533783) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELL 2 (533783) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 b.2. BELL 2 (533783) 69.0 kV to SC3MILL2 (533552) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0448 | Single Phase Fault with Stuck Breaker on CANAL 4 138.00 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 138.00 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALS 2 (533784) 69.0 kV to CANAL 4 (533033) 138.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 b.2. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0449 | Single Phase Fault with Stuck Breaker on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply Fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0450 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.2. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0451 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL W 2 (533796) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 b.2. GILL W 2 (533796) 69.0 kV to GILL E 4 (533044) 138.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0452 | Single Phase Fault with Stuck Breaker on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply Fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILLJCT2 (533798) 69.0 kV to GILL E 2 (533795) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0453 | Single Phase Fault with Stuck Breaker on HAYSVJS2 69.000 (533802) 69 kV Bus a. Apply Fault at the HAYSVJS2 69.000 (533802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYSVJS2 (533802) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #1 b.2. HAYSVJS2 (533802) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0454 | Single Phase Fault with Stuck Breaker on HAYSVJN2 69.000 (533804) 69 kV Bus a. Apply Fault at the HAYSVJN2 69.000 (533804) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYSVJN2 (533804) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #1 b.2. HAYSVJN2 (533804) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0455 | Single Phase Fault with Stuck Breaker on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply Fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0456 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERS2 (533806) 69.0 kV to HOOVERS4 (533050) 138.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 b.2. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0457 | Single Phase Fault with Stuck Breaker on HYDRJN2 69.000 (533808) 69 kV Bus a. Apply Fault at the HYDRJN2 69.000 (533808) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDRJN2 (533808) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 b.2. HYDRJN2 (533808) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0458 | Single Phase Fault with Stuck Breaker on HYDRJS2 69.000 (533810) 69 kV Bus a. Apply Fault at the HYDRJS2 69.000 (533810) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDRJS2 (533810) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 b.2. HYDRJS2 (533810) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0459 | Single Phase Fault with Stuck Breaker on LIN 2 69.000 (533812) 69 kV Bus a. Apply Fault at the LIN 2 69.000 (533812) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.2. LIN 2 (533812) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0460 | Single Phase Fault with Stuck Breaker on MACARTH2 69.000 (533813) 69 kV Bus a. Apply Fault at the MACARTH2 69.000 (533813) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MACARTH2 (533813) 69.0 kV to GILL E 2 (533795) 69.0 kV Transmission Circuit #1 b.2. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0461 | Single Phase Fault with Stuck Breaker on BLF-CRK4 138.00 (539002) 138 kV Bus a. Apply Fault at the BLF-CRK4 138.00 (539002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLF-CRK4 (539002) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0462 | Single Phase Fault with Stuck Breaker on CLDWELL4 138.00 (539003) 138 kV Bus a. Apply Fault at the CLDWELL4 138.00 (539003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLDWELL4 (539003) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0463 | Single Phase Fault with Stuck Breaker on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. MILAN_GOAB (539008) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0464 | Single Phase Fault with Stuck Breaker on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply Fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0465 | Single Phase Fault with Stuck Breaker on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply Fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0466 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to GRTBEND3 (539678) 115.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0467 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.2. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0468 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0469 | Single Phase Fault with Stuck Breaker on FORD 3 115.00 (539758) 115 kV Bus a. Apply Fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0470 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.2. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0471 | Single Phase Fault with Stuck Breaker on NFTDODG3 115.00 (539771) 115 kV Bus a. Apply Fault at the NFTDODG3 115.00 (539771) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NFTDODG3 (539771) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #2 b.2. NFTDODG3 (539771) 115.0 kV to SPRVL 3 (539759) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0472 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0473 | Single Phase Fault with Stuck Breaker on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply Fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345.0 kV to GEN-2008-124 (579480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0474 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0475 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0476 | Single Phase Fault with Stuck Breaker on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 b.2. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0477 | Single Phase Fault with Stuck Breaker on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. SMTHVL 5 (541204) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0478 | Single Phase Fault with Stuck Breaker on KCI 5 161.00 (541212) 161 kV Bus a. Apply Fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KCI 5 (541212) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. KCI 5 (541212) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0479 | Single Phase Fault with Stuck Breaker on FRLVW 5 161.00 (541213) 161 kV Bus a. Apply Fault at the FRLVW 5 161.00 (541213) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRLVW 5 (541213) 161.0 kV to KCI 5 (541212) 161.0 kV Transmission Circuit #1 b.2. FRLVW 5 (541213) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0480 | Single Phase Fault with Stuck Breaker on TWA 5 161.00 (541214) 161 kV Bus a. Apply Fault at the TWA 5 161.00 (541214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 b.2. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0481 | Single Phase Fault with Stuck Breaker on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply Fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 b.2. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0482 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0483 | Single Phase Fault with Stuck Breaker on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply Fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. PLTCTY 5 (541221) 161.0 kV to KCI 5 (541212) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0484 | Single Phase Fault with Stuck Breaker on GRAINVL5 161.00 (541226) 161 kV Bus a. Apply Fault at the GRAINVL5 161.00 (541226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAINVL5 (541226) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 b.2. GRAINVL5 (541226) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0485 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRIDGE5 (541230) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0486 | Single Phase Fault with Stuck Breaker on LEX161 5 161.00 (541232) 161 kV Bus a. Apply Fault at the LEX161 5 161.00 (541232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. LEX161 5 (541232) 161.0 kV to LEX69 2 (541264) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0487 | Single Phase Fault with Stuck Breaker on RICHMND5 161.00 (541236) 161 kV Bus a. Apply Fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to LEX161 5 (541232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0488 | Single Phase Fault with Stuck Breaker on BLSPW 5 161.00 (541237) 161 kV Bus a. Apply Fault at the BLSPW 5 161.00 (541237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPW 5 (541237) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0489 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDEAST5 (541241) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 b.2. SEDEAST5 (541241) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0490 | Single Phase Fault with Stuck Breaker on LBRTYWT5 161.00 (541247) 161 kV Bus a. Apply Fault at the LBRTYWT5 161.00 (541247) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYWT5 (541247) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 b.2. LBRTYWT5 (541247) 161.0 kV to HLLMRK 5 (541215) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0491 | Single Phase Fault with Stuck Breaker on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply Fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. LBRTYST5 (541248) 161.0 kV to LIBRTYS2 (543095) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0492 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 b.2. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0493 | Single Phase Fault with Stuck Breaker on STALEY 2 69.000 (541261) 69 kV Bus a. Apply Fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STALEY 2 (541261) 69.0 kV to RNRDGE 2 (541260) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0494 | Single Phase Fault with Stuck Breaker on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply Fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY2 (541262) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 b.2. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0495 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 b.2. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0496 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0497 | Single Phase Fault with Stuck Breaker on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply Fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDN 2 (541271) 69.0 kV Transmission Circuit #1 b.2. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0498 | Single Phase Fault with Stuck Breaker on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply Fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDS 2 (541272) 69.0 kV Transmission Circuit #1 b.2. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0499 | Single Phase Fault with Stuck Breaker on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply Fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDPLT 2 (541275) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 b.2. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0500 | Single Phase Fault with Stuck Breaker on COLECMP2 69.000 (541276) 69 kV Bus a. Apply Fault at the COLECMP2 69.000 (541276) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLECMP2 (541276) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 b.2. COLECMP2 (541276) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0501 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAFBE_SW5 (541337) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. WAFBE_SW5 (541337) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0502 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 b.2. S.HARP 5 (541341) 161.0 kV to ARCHIE 5 (541207) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0503 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0504 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0505 | Single Phase Fault with Stuck Breaker on KNOSTERTP 69.000 (541534) 69 kV Bus a. Apply Fault at the KNOSTERTP 69.000 (541534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOSTERTP (541534) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 b.2. KNOSTERTP (541534) 69.0 kV to MONSERTP (541524) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0506 | Single Phase Fault with Stuck Breaker on LAMONTETP 69.000 (541535) 69 kV Bus a. Apply Fault at the LAMONTETP 69.000 (541535) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMONTETP (541535) 69.0 kV to SEDN 2 (541271) 69.0 kV Transmission Circuit #1 b.2. LAMONTETP (541535) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0507 | Single Phase Fault with Stuck Breaker on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply Fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0508 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to ATLNTIC7 (542940) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0509 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0510 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 b.2. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0511 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0512 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0513 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LAC G1 1 (542955) 22.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0514 | Single Phase Fault with Stuck Breaker on TROOST 5 161.00 (542986) 161 kV Bus a. Apply Fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 b.2. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0515 | Single Phase Fault with Stuck Breaker on GRAND 5 161.00 (542987) 161 kV Bus a. Apply Fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0516 | Single Phase Fault with Stuck Breaker on GRAND W5 161.00 (542988) 161 kV Bus a. Apply Fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0517 | Single Phase Fault with Stuck Breaker on NAVY 5 161.00 (542989) 161 kV Bus a. Apply Fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NAVY 5 (542989) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0518 | Single Phase Fault with Stuck Breaker on CROSTWN5 161.00 (542990) 161 kV Bus a. Apply Fault at the CROSTWN5 161.00 (542990) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSTWN5 (542990) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. CROSTWN5 (542990) 161.0 kV to TROOST 5 (542986) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0519 | Single Phase Fault with Stuck Breaker on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply Fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDTOWN5 (542996) 161.0 kV to TROOST 5 (542986) 161.0 kV Transmission Circuit #1 b.2. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0520 | Single Phase Fault with Stuck Breaker on LEEDS 5 161.00 (542997) 161 kV Bus a. Apply Fault at the LEEDS 5 161.00 (542997) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEEDS 5 (542997) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0521 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0522 | Single Phase Fault with Stuck Breaker on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0523 | Single Phase Fault with Stuck Breaker on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to AVONDAL5 (543015) 161.0 kV Transmission Circuit #1 b.2. GLADSTN5 (543016) 161.0 kV to GLADSTN_CAP5 (542946) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0524 | Single Phase Fault with Stuck Breaker on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply Fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 b.2. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0525 | Single Phase Fault with Stuck Breaker on BARRY 5 161.00 (543019) 161 kV Bus a. Apply Fault at the BARRY 5 161.00 (543019) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRY 5 (543019) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. BARRY 5 (543019) 161.0 kV to BARRY_CAP 5 (542944) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0526 | Single Phase Fault with Stuck Breaker on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply Fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMGHAM5 (543020) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.2. BRMGHAM5 (543020) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0527 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV to NASHUA 7 (542980) 345.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 b.2. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0528 | Single Phase Fault with Stuck Breaker on SHOLCRK5 161.00 (543029) 161 kV Bus a. Apply Fault at the SHOLCRK5 161.00 (543029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHOLCRK5 (543029) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. SHOLCRK5 (543029) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0529 | Single Phase Fault with Stuck Breaker on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply Fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 b.2. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0530 | Single Phase Fault with Stuck Breaker on COURTNY2 69.000 (543085) 69 kV Bus a. Apply Fault at the COURTNY2 69.000 (543085) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0531 | Single Phase Fault with Stuck Breaker on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply Fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0532 | Single Phase Fault with Stuck Breaker on BLUSPRG2 69.000 (543088) 69 kV Bus a. Apply Fault at the BLUSPRG2 69.000 (543088) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0533 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 b.2. DUNCNRD2 (543091) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0534 | Single Phase Fault with Stuck Breaker on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply Fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUGRCK_TP_E2 (543165) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 b.2. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0535 | Single Phase Fault with Stuck Breaker on DAKOTA_5 161.00 (543650) 161 kV Bus a. Apply Fault at the DAKOTA_5 161.00 (543650) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAKOTA_5 (543650) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #1 b.2. DAKOTA_5 (543650) 161.0 kV to CNTRVIL5 (543065) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0536 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0537 | Single Phase Fault with Stuck Breaker on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply Fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0538 | Single Phase Fault with Stuck Breaker on COL 94 2 69.000 (547530) 69 kV Bus a. Apply Fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0539 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 2 (547539) 69.0 kV to JOP145 5 (547470) 161.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 b.2. JOP145 2 (547539) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0540 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to RIV4525 (547469) 161.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 b.2. RIV167 2 (547541) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0541 | Single Phase Fault with Stuck Breaker on BAX271 2 69.000 (547554) 69 kV Bus a. Apply Fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.2. BAX271 2 (547554) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0542 | Single Phase Fault with Stuck Breaker on GLF339 2 69.000 (547690) 69 kV Bus a. Apply Fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLF339 2 (547690) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0543 | Single Phase Fault with Stuck Breaker on SUB I 69.000 (548800) 69 kV Bus a. Apply Fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 b.2. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0544 | Single Phase Fault with Stuck Breaker on SUB K 69.000 (548801) 69 kV Bus a. Apply Fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0545 | Single Phase Fault with Stuck Breaker on SUB H 69.000 (548802) 69 kV Bus a. Apply Fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB H (548802) 69.0 kV to COURTNY2 (543085) 69.0 kV Transmission Circuit #1 b.2. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0546 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0547 | Single Phase Fault with Stuck Breaker on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply Fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0548 | Single Phase Fault with Stuck Breaker on SUB B 69.000 (548810) 69 kV Bus a. Apply Fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 b.2. SUB B (548810) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0549 | Single Phase Fault with Stuck Breaker on SUB J 69.000 (548811) 69 kV Bus a. Apply Fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB J (548811) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0550 | Single Phase Fault with Stuck Breaker on G15052_T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15052_T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15052_T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15052_T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0551 | Single Phase Fault with Stuck Breaker on G16-046-TAP 345.00 (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP 345.00 (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0552 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0553 | Single Phase Fault with Stuck Breaker on GEN-2022-161345.00 (562477) 345 kV Bus a. Apply Fault at the GEN-2022-161345.00 (562477) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-161 (562477) 345.0 kV to GEN-2014-001 (583850) 345.0 kV Transmission Circuit #z1 b.2. GEN-2022-161 (562477) 345.0 kV to G22-161XFMR2 (770205) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0554 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583850) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583850) 345.0 kV to GEN-2014-001 (583859) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583850) 345.0 kV to GEN-2022-161 (562477) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0555 | Single Phase Fault with Stuck Breaker on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply Fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-074 (587680) 345.0 kV to G16-074XFMR1 (587681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0556 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR1 (588361) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0557 | Single Phase Fault with Stuck Breaker on G16-153-TAP 345.00 (588364) 345 kV Bus a. Apply Fault at the G16-153-TAP 345.00 (588364) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-153-TAP (588364) 345.0 kV to GEN-2016-153 (588360) 345.0 kV Transmission Circuit #1 b.2. G16-153-TAP (588364) 345.0 kV to GEN-2017-086 (589240) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0558 | Single Phase Fault with Stuck Breaker on GEN-2017-005161.00 (588500) 161 kV Bus a. Apply Fault at the GEN-2017-005161.00 (588500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-005 (588500) 161.0 kV to G17-005XFMR1 (588501) 34.5 kV Two Winding #1 b.2. GEN-2017-005 (588500) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0559 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0560 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0561 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0562 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0563 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0564 | Single Phase Fault with Stuck Breaker on GI-95_POI 345.00 (709500) 345 kV Bus a. Apply Fault at the GI-95_POI 345.00 (709500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI-95_POI (709500) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. GI-95_POI (709500) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0565 | Single Phase Fault with Stuck Breaker on GEN-2017-183345.00 (761376) 345 kV Bus a. Apply Fault at the GEN-2017-183345.00 (761376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-183 (761376) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-183 (761376) 345.0 kV to G17-184XFMR2 (761401) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0566 | Single Phase Fault with Stuck Breaker on GEN-2018-125345.00 (763406) 345 kV Bus a. Apply Fault at the GEN-2018-125345.00 (763406) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-125 (763406) 345.0 kV to G18-125-XFM1 (763407) 34.5 kV Two Winding #1 b.2. GEN-2018-125 (763406) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0567 | Single Phase Fault with Stuck Breaker on GEN-2018-128345.00 (763417) 345 kV Bus a. Apply Fault at the GEN-2018-128345.00 (763417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-128 (763417) 345.0 kV to G18-128-XFM1 (763418) 34.5 kV Two Winding #1 b.2. GEN-2018-128 (763417) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0568 | Single Phase Fault with Stuck Breaker on GEN-2019-030345.00 (763670) 345 kV Bus a. Apply Fault at the GEN-2019-030345.00 (763670) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-030 (763670) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 b.2. GEN-2019-030 (763670) 345.0 kV to G19-030-XFM1 (763671) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0569 | Single Phase Fault with Stuck Breaker on G19-053/055 230.00 (763846) 230 kV Bus a. Apply Fault at the G19-053/055 230.00 (763846) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-053/055 (763846) 230.0 kV to G19-055-XFM1 (763869) 34.5 kV Two Winding #1 b.2. G19-053/055 (763846) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0570 | Single Phase Fault with Stuck Breaker on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply Fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0571 | Single Phase Fault with Stuck Breaker on G19-054/068 230.00 (763857) 230 kV Bus a. Apply Fault at the G19-054/068 230.00 (763857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054/068 (763857) 230.0 kV to G19-054-XFM1 (763858) 34.5 kV Two Winding #1 b.2. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0572 | Single Phase Fault with Stuck Breaker on GEN-2020-072161.00 (764345) 161 kV Bus a. Apply Fault at the GEN-2020-072161.00 (764345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-072 (764345) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-072 (764345) 161.0 kV to G20-072-XFM1 (764348) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0573 | Single Phase Fault with Stuck Breaker on GEN-2020-090345.00 (765190) 345 kV Bus a. Apply Fault at the GEN-2020-090345.00 (765190) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-090 (765190) 345.0 kV to G20-090-XFM1 (765193) 34.5 kV Two Winding #1 b.2. GEN-2020-090 (765190) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0574 | Single Phase Fault with Stuck Breaker on G20-090-TAP 345.00 (765200) 345 kV Bus a. Apply Fault at the G20-090-TAP 345.00 (765200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-090-TAP (765200) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. G20-090-TAP (765200) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0575 | Single Phase Fault with Stuck Breaker on GEN-2021-029345.00 (765570) 345 kV Bus a. Apply Fault at the GEN-2021-029345.00 (765570) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-029 (765570) 345.0 kV to G21-029-XFM1 (765574) 34.5 kV Two Winding #1 b.2. GEN-2021-029 (765570) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0576 | Single Phase Fault with Stuck Breaker on G21-029-TAP 345.00 (765571) 345 kV Bus a. Apply Fault at the G21-029-TAP 345.00 (765571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. G21-029-TAP (765571) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0577 | Single Phase Fault with Stuck Breaker on GEN-2021-068345.00 (765910) 345 kV Bus a. Apply Fault at the GEN-2021-068345.00 (765910) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-068 (765910) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-068 (765910) 345.0 kV to G21-068-XFM1 (765914) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0578 | Single Phase Fault with Stuck Breaker on G21-068-TAP 345.00 (765911) 345 kV Bus a. Apply Fault at the G21-068-TAP 345.00 (765911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-068-TAP (765911) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. G21-068-TAP (765911) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0579 | Single Phase Fault with Stuck Breaker on GEN-2020-007345.00 (766260) 345 kV Bus a. Apply Fault at the GEN-2020-007345.00 (766260) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-007 (766260) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-007 (766260) 345.0 kV to G20-007-XFM1 (766264) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0580 | Single Phase Fault with Stuck Breaker on G22-007-TAP 115.00 (767120) 115 kV Bus a. Apply Fault at the G22-007-TAP 115.00 (767120) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-007-TAP (767120) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.2. G22-007-TAP (767120) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0581 | Single Phase Fault with Stuck Breaker on G22-013-TAP 345.00 (767240) 345 kV Bus a. Apply Fault at the G22-013-TAP 345.00 (767240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-013-TAP (767240) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G22-013-TAP (767240) 345.0 kV to GEN-2022-013 (767241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0582 | Single Phase Fault with Stuck Breaker on G22-015-TAP 345.00 (767280) 345 kV Bus a. Apply Fault at the G22-015-TAP 345.00 (767280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. G22-015-TAP (767280) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0583 | Single Phase Fault with Stuck Breaker on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply Fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-065-TAP (768280) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. G22-065-TAP (768280) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0584 | Single Phase Fault with Stuck Breaker on G22-075-TAP 345.00 (768480) 345 kV Bus a. Apply Fault at the G22-075-TAP 345.00 (768480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-075-TAP (768480) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G22-075-TAP (768480) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0585 | Single Phase Fault with Stuck Breaker on G22-100-TAP 161.00 (768980) 161 kV Bus a. Apply Fault at the G22-100-TAP 161.00 (768980) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-100-TAP (768980) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. G22-100-TAP (768980) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0586 | Single Phase Fault with Stuck Breaker on G22-214-TAP 138.00 (771260) 138 kV Bus a. Apply Fault at the G22-214-TAP 138.00 (771260) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-214-TAP (771260) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 b.2. G22-214-TAP (771260) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0587 | Single Phase Fault with Stuck Breaker on 5BOONE 161.00 (300061) 161 kV Bus a. Apply Fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BOONE (300493) 69.0 kV to 5BOONE (300061) 161.0 kV Two Winding #1 b.2. 2BOONE (300493) 69.0 kV to 2DEERPK (300497) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0588 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEORGE (300531) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 b.2. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0589 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 b.2. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0590 | Single Phase Fault with Stuck Breaker on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply Fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PLATCTY (300307) 69.0 kV to 5PLATCTY (301552) 161.0 kV Two Winding #1 b.2. 2PLATCTY (300307) 69.0 kV to 2HOOVER (300298) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0591 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.2. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0592 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 b.2. 5JASPER (300950) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0593 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0594 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0595 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0596 | Single Phase Fault with Stuck Breaker on COLBY 3 115.00 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0597 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0598 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0599 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0600 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0601 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LANG 7 (532769) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0602 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 7 (532770) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0603 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0604 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.2. NEOSHON4 (533022) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0605 | Single Phase Fault with Stuck Breaker on CANAL 4 138.00 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 138.00 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANAL 4 (533033) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #1 b.2. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0606 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASOE4 (533059) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #z1 b.2. ELPASOE4 (533059) 138.0 kV to 47TH ST4 (533058) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0607 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 b.2. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0608 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 b.2. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0609 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 b.2. CRESWLS2 (533573) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0610 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 2 (533646) 69.0 kV to COALCRK2 (533633) 69.0 kV Transmission Circuit #1 b.2. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0611 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.2. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0612 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0613 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0614 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0615 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0616 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0617 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0618 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0619 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0620 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0621 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0622 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0623 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 b.2. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0624 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0625 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0626 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 b.2. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0627 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO7 (640326) 115.0 kV to BEVERLY7 (640082) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0628 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD7 (640381) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0629 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0630 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT4 (532992) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0631 | Single Phase Fault with Stuck Breaker on SHERIDN2 69.000 (533841) 69 kV Bus a. Apply Fault at the SHERIDN2 69.000 (533841) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHERIDN2 (533841) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0632 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0633 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 b.2. SUB M (548815) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0634 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOK 7 (640269) 115.0 kV to CAMBRIG7 (640100) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0635 | Single Phase Fault with Stuck Breaker on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply Fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7THOMHL (300049) 345.0 kV to 5THOMHLXF4 (301510) 161.0 kV Two Winding #4 b.2. 7THOMHL (300049) 345.0 kV to 5THOMHLXF3 (301506) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0636 | Single Phase Fault with Stuck Breaker on VSC2_3 345.00 (992003) 345 kV Bus a. Apply Fault at the VSC2_3 345.00 (992003) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VSC2_3 (992003) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 b.2. VSC2_3 (992003) 345.0 kV to VSC2_6 (992006) 276.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0637 | Single Phase Fault with Stuck Breaker on 5MLRSBGB1 161.00 (300519) 161 kV Bus a. Apply Fault at the 5MLRSBGB1 161.00 (300519) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MLRSBGB1 (300519) 161.0 kV to 5MLRSBGB2 (301498) 161.0 kV Transmission Circuit #z1 b.2. 5MLRSBGB1 (300519) 161.0 kV to 5BOONE (300061) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0638 | Single Phase Fault with Stuck Breaker on 5NORTONTP 161.00 (301567) 161 kV Bus a. Apply Fault at the 5NORTONTP 161.00 (301567) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTONTP (301567) 161.0 kV to 5GEORGE (300082) 161.0 kV Transmission Circuit #1 b.2. 5NORTONTP (301567) 161.0 kV to 5NORTON (300105) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0639 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0640 | Single Phase Fault with Stuck Breaker on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply Fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to 5PITTSV (300110) 161.0 kV Transmission Circuit #1 b.2. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0641 | Single Phase Fault with Stuck Breaker on G20-072-TAP 161.00 (764355) 161 kV Bus a. Apply Fault at the G20-072-TAP 161.00 (764355) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-072-TAP (764355) 161.0 kV to 5SEDALA (300117) 161.0 kV Transmission Circuit #1 b.2. G20-072-TAP (764355) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0642 | Single Phase Fault with Stuck Breaker on 5MCBAINB2 161.00 (301489) 161 kV Bus a. Apply Fault at the 5MCBAINB2 161.00 (301489) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5MCBAINB2 (301489) 161.0 kV to 5MCBAINB1 (300501) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0643 | Single Phase Fault with Stuck Breaker on 2SYLVAN 69.000 (300545) 69 kV Bus a. Apply Fault at the 2SYLVAN 69.000 (300545) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SYLVAN (300545) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2SYLVAN (300545) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0644 | Single Phase Fault with Stuck Breaker on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply Fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2FORTNA (300554) 69.0 kV to 2CALIF (300550) 69.0 kV Transmission Circuit #1 b.2. 2FORTNA (300554) 69.0 kV to 2SYRACS (300564) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0645 | Single Phase Fault with Stuck Breaker on 2PRARIE 69.000 (300561) 69 kV Bus a. Apply Fault at the 2PRARIE 69.000 (300561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PRARIE (300561) 69.0 kV to 2CALIF (300550) 69.0 kV Transmission Circuit #1 b.2. 2PRARIE (300561) 69.0 kV to 2PILOTG (300560) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0646 | Single Phase Fault with Stuck Breaker on 2ST_MARTINS 69.000 (301442) 69 kV Bus a. Apply Fault at the 2ST_MARTINS 69.000 (301442) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ST_MARTINS (301442) 69.0 kV to 2CALIF (300550) 69.0 kV Transmission Circuit #1 b.2. 2ST_MARTINS (301442) 69.0 kV to 2SCRUGG (300637) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0647 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0648 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0649 | Single Phase Fault with Stuck Breaker on G18-128-TAP 345.00 (763421) 345 kV Bus a. Apply Fault at the G18-128-TAP 345.00 (763421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-128-TAP (763421) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. G18-128-TAP (763421) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0650 | Single Phase Fault with Stuck Breaker on GEN-2021-076345.00 (765990) 345 kV Bus a. Apply Fault at the GEN-2021-076345.00 (765990) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-076 (765990) 345.0 kV to G21-076-XFM1 (765994) 34.5 kV Two Winding #1 b.2. GEN-2021-076 (765990) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0651 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 7 (532773) 345.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0652 | Single Phase Fault with Stuck Breaker on CNTRLPL3 115.00 (531485) 115 kV Bus a. Apply Fault at the CNTRLPL3 115.00 (531485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRLPL3 (531485) 115.0 kV to LEOTI 3 (531428) 115.0 kV Transmission Circuit #1 b.2. CNTRLPL3 (531485) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0653 | Single Phase Fault with Stuck Breaker on G19-030-TAP 345.00 (763677) 345 kV Bus a. Apply Fault at the G19-030-TAP 345.00 (763677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-030-TAP (763677) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G19-030-TAP (763677) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0654 | Single Phase Fault with Stuck Breaker on GEN-2021-107345.00 (766240) 345 kV Bus a. Apply Fault at the GEN-2021-107345.00 (766240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-107 (766240) 345.0 kV to G21-107-XFM1 (766244) 34.5 kV Two Winding #1 b.2. GEN-2021-107 (766240) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0655 | Single Phase Fault with Stuck Breaker on G16-111-TAP 345.00 (587884) 345 kV Bus a. Apply Fault at the G16-111-TAP 345.00 (587884) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-111-TAP (587884) 345.0 kV to RENO 7 (532771) 345.0 kV Transmission Circuit #1 b.2. G16-111-TAP (587884) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0656 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0657 | Single Phase Fault with Stuck Breaker on GEN-2017-220345.00 (760284) 345 kV Bus a. Apply Fault at the GEN-2017-220345.00 (760284) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-220 (760284) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-220 (760284) 345.0 kV to G17-220-XFM1 (760285) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0658 | Single Phase Fault with Stuck Breaker on G21-096-TAP 345.00 (766141) 345 kV Bus a. Apply Fault at the G21-096-TAP 345.00 (766141) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-096-TAP (766141) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. G21-096-TAP (766141) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0659 | Single Phase Fault with Stuck Breaker on GEN-2018-032345.00 (762680) 345 kV Bus a. Apply Fault at the GEN-2018-032345.00 (762680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-032 (762680) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-032 (762680) 345.0 kV to G18-032XFM1 (762681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0660 | Single Phase Fault with Stuck Breaker on GEN-2021-006345.00 (765350) 345 kV Bus a. Apply Fault at the GEN-2021-006345.00 (765350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-006 (765350) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-006 (765350) 345.0 kV to G21-006-XFM2 (765357) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0661 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583859) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583859) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583859) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583859) 345.0 kV to GEN-2014-001 (583850) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0662 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. UNIONRG6 (532874) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0663 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0664 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. G19-054-TAP (763862) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0665 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 b.2. NEOSHOS2 (533778) 69.0 kV to BAKER 2 (532926) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0666 | Single Phase Fault with Stuck Breaker on G17-005-TAP 161.00 (588504) 161 kV Bus a. Apply Fault at the G17-005-TAP 161.00 (588504) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-005-TAP (588504) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. G17-005-TAP (588504) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0667 | Single Phase Fault with Stuck Breaker on G20-079-TAP 161.00 (764310) 161 kV Bus a. Apply Fault at the G20-079-TAP 161.00 (764310) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-079-TAP (764310) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. G20-079-TAP (764310) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0668 | Single Phase Fault with Stuck Breaker on GEN-2022-006161.00 (767101) 161 kV Bus a. Apply Fault at the GEN-2022-006161.00 (767101) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-006 (767101) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. GEN-2022-006 (767101) 161.0 kV to G22-006XFMR1 (767102) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0669 | Single Phase Fault with Stuck Breaker on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply Fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SC10BEL4 (533063) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. SC10BEL4 (533063) 138.0 kV to FARBER 4 (533042) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0670 | Single Phase Fault with Stuck Breaker on GEN-2017-121138.00 (761838) 138 kV Bus a. Apply Fault at the GEN-2017-121138.00 (761838) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-121 (761838) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. GEN-2017-121 (761838) 138.0 kV to G17-121XFM2 (761842) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0671 | Single Phase Fault with Stuck Breaker on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply Fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TAYLOR 4 (533006) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. TAYLOR 4 (533006) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0672 | Single Phase Fault with Stuck Breaker on SG12COL4 138.00 (533065) 138 kV Bus a. Apply Fault at the SG12COL4 138.00 (533065) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SG12COL4 (533065) 138.0 kV to EVANS N4 (533040) 138.0 kV Transmission Circuit #1 b.2. SG12COL4 (533065) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0673 | Single Phase Fault with Stuck Breaker on WACO N 4 138.00 (533073) 138 kV Bus a. Apply Fault at the WACO N 4 138.00 (533073) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WACO N 4 (533073) 138.0 kV to CENTENN4 (533034) 138.0 kV Transmission Circuit #1 b.2. WACO N 4 (533073) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0674 | Single Phase Fault with Stuck Breaker on MAIZE 4 138.00 (533054) 138 kV Bus a. Apply Fault at the MAIZE 4 138.00 (533054) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAIZE 4 (533054) 138.0 kV to EVANS N4 (533040) 138.0 kV Transmission Circuit #1 b.2. MAIZE 4 (533054) 138.0 kV to CHISHLM4 (533035) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0675 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 45TH ST4 (533074) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #1 b.2. 45TH ST4 (533074) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0676 | Single Phase Fault with Stuck Breaker on STEARMN4 138.00 (533068) 138 kV Bus a. Apply Fault at the STEARMN4 138.00 (533068) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEARMN4 (533068) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. STEARMN4 (533068) 138.0 kV to BOEINGE4 (533030) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0677 | Single Phase Fault with Stuck Breaker on GEN-2017-226138.00 (760641) 138 kV Bus a. Apply Fault at the GEN-2017-226138.00 (760641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-226 (760641) 138.0 kV to G17-226XFMR1 (760642) 34.5 kV Two Winding #1 b.2. GEN-2017-226 (760641) 138.0 kV to G17-227XFMR1 (760662) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0678 | Single Phase Fault with Stuck Breaker on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply Fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKERDG4 (533053) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #1 b.2. LAKERDG4 (533053) 138.0 kV to HOOVERN4 (533049) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0679 | Single Phase Fault with Stuck Breaker on INTERST4 138.00 (533051) 138 kV Bus a. Apply Fault at the INTERST4 138.00 (533051) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTERST4 (533051) 138.0 kV to GILL E 4 (533044) 138.0 kV Transmission Circuit #1 b.2. INTERST4 (533051) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0680 | Single Phase Fault with Stuck Breaker on GEN-2022-004138.00 (767061) 138 kV Bus a. Apply Fault at the GEN-2022-004138.00 (767061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-004 (767061) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #1 b.2. GEN-2022-004 (767061) 138.0 kV to G22-004XFMR1 (767062) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0681 | Single Phase Fault with Stuck Breaker on 64TH 4 138.00 (533066) 138 kV Bus a. Apply Fault at the 64TH 4 138.00 (533066) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 64TH 4 (533066) 138.0 kV to 47TH ST4 (533058) 138.0 kV Transmission Circuit #1 b.2. 64TH 4 (533066) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0682 | Single Phase Fault with Stuck Breaker on SCRANTN3 115.00 (533173) 115 kV Bus a. Apply Fault at the SCRANTN3 115.00 (533173) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCRANTN3 (533173) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 b.2. SCRANTN3 (533173) 115.0 kV to 4CORNER3 (533158) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0683 | Single Phase Fault with Stuck Breaker on FLORENC3 115.00 (533366) 115 kV Bus a. Apply Fault at the FLORENC3 115.00 (533366) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLORENC3 (533366) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0684 | Single Phase Fault with Stuck Breaker on GREEN 2 69.000 (533636) 69 kV Bus a. Apply Fault at the GREEN 2 69.000 (533636) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREEN 2 (533636) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.2. GREEN 2 (533636) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0685 | Single Phase Fault with Stuck Breaker on MCKEE 2 69.000 (533640) 69 kV Bus a. Apply Fault at the MCKEE 2 69.000 (533640) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCKEE 2 (533640) 69.0 kV to MARMATN2 (533639) 69.0 kV Transmission Circuit #1 b.2. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0686 | Single Phase Fault with Stuck Breaker on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply Fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ZILAJCT2 (533654) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.2. ZILAJCT2 (533654) 69.0 kV to ALLEN 2 (533621) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0687 | Single Phase Fault with Stuck Breaker on PARSONS2 69.000 (533704) 69 kV Bus a. Apply Fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARSONS2 (533704) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 b.2. PARSONS2 (533704) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0688 | Single Phase Fault with Stuck Breaker on PECK 2 69.000 (533830) 69 kV Bus a. Apply Fault at the PECK 2 69.000 (533830) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECK 2 (533830) 69.0 kV to HAYSVJS2 (533802) 69.0 kV Transmission Circuit #1 b.2. PECK 2 (533830) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0689 | Single Phase Fault with Stuck Breaker on CANALN 2 69.000 (533790) 69 kV Bus a. Apply Fault at the CANALN 2 69.000 (533790) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALN 2 (533790) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #z1 b.2. CANALN 2 (533790) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0690 | Single Phase Fault with Stuck Breaker on RUTAN 2 69.000 (533838) 69 kV Bus a. Apply Fault at the RUTAN 2 69.000 (533838) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUTAN 2 (533838) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #1 b.2. RUTAN 2 (533838) 69.0 kV to GLENDAL2 (533797) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0691 | Single Phase Fault with Stuck Breaker on WESTLNK2 69.000 (533854) 69 kV Bus a. Apply Fault at the WESTLNK2 69.000 (533854) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTLNK2 (533854) 69.0 kV to COWSKIN2 (533788) 69.0 kV Transmission Circuit #1 b.2. WESTLNK2 (533854) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0692 | Single Phase Fault with Stuck Breaker on GODDTAP2 69.000 (533879) 69 kV Bus a. Apply Fault at the GODDTAP2 69.000 (533879) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GODDTAP2 (533879) 69.0 kV to COWSKIN2 (533788) 69.0 kV Transmission Circuit #1 b.2. GODDTAP2 (533879) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0693 | Single Phase Fault with Stuck Breaker on VULCTP 2 69.000 (533851) 69 kV Bus a. Apply Fault at the VULCTP 2 69.000 (533851) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VULCTP 2 (533851) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #1 b.2. VULCTP 2 (533851) 69.0 kV to LIN 2 (533812) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0694 | Single Phase Fault with Stuck Breaker on OATVILL2 69.000 (533825) 69 kV Bus a. Apply Fault at the OATVILL2 69.000 (533825) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OATVILL2 (533825) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. OATVILL2 (533825) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0695 | Single Phase Fault with Stuck Breaker on MIDLAND2 69.000 (533816) 69 kV Bus a. Apply Fault at the MIDLAND2 69.000 (533816) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDLAND2 (533816) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 b.2. MIDLAND2 (533816) 69.0 kV to HYDRJS2 (533810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0696 | Single Phase Fault with Stuck Breaker on VISTAPK2 69.000 (533849) 69 kV Bus a. Apply Fault at the VISTAPK2 69.000 (533849) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VISTAPK2 (533849) 69.0 kV to HOOVERN2 (533805) 69.0 kV Transmission Circuit #1 b.2. VISTAPK2 (533849) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0697 | Single Phase Fault with Stuck Breaker on WATER1 2 69.000 (533855) 69 kV Bus a. Apply Fault at the WATER1 2 69.000 (533855) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATER1 2 (533855) 69.0 kV to HOOVERN2 (533805) 69.0 kV Transmission Circuit #1 b.2. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0698 | Single Phase Fault with Stuck Breaker on TYLER 2 69.000 (533847) 69 kV Bus a. Apply Fault at the TYLER 2 69.000 (533847) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. TYLER 2 (533847) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0699 | Single Phase Fault with Stuck Breaker on WATER2 2 69.000 (533856) 69 kV Bus a. Apply Fault at the WATER2 2 69.000 (533856) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATER2 2 (533856) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 b.2. WATER2 2 (533856) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0700 | Single Phase Fault with Stuck Breaker on SG8CRAG2 69.000 (533873) 69 kV Bus a. Apply Fault at the SG8CRAG2 69.000 (533873) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SG8CRAG2 (533873) 69.0 kV to LIN 2 (533812) 69.0 kV Transmission Circuit #1 b.2. SG8CRAG2 (533873) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0701 | Single Phase Fault with Stuck Breaker on SENECA 2 69.000 (533839) 69 kV Bus a. Apply Fault at the SENECA 2 69.000 (533839) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SENECA 2 (533839) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.2. SENECA 2 (533839) 69.0 kV to OSAGE 2 (533827) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0702 | Single Phase Fault with Stuck Breaker on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply Fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROLLHLS3 (539643) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0703 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUSSELL3 (539701) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. RUSSELL3 (539701) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0704 | Single Phase Fault with Stuck Breaker on 2ND-KS 3 115.00 (539689) 115 kV Bus a. Apply Fault at the 2ND-KS 3 115.00 (539689) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ND-KS 3 (539689) 115.0 kV to 24-FREY3 (539661) 115.0 kV Transmission Circuit #1 b.2. 2ND-KS 3 (539689) 115.0 kV to GBENDTP3 (539666) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0705 | Single Phase Fault with Stuck Breaker on SSTARTP3 115.00 (539763) 115 kV Bus a. Apply Fault at the SSTARTP3 115.00 (539763) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SSTARTP3 (539763) 115.0 kV to GRNBURG3 (539664) 115.0 kV Transmission Circuit #1 b.2. SSTARTP3 (539763) 115.0 kV to FORD 3 (539758) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0706 | Single Phase Fault with Stuck Breaker on GEN-2019-044115.00 (763758) 115 kV Bus a. Apply Fault at the GEN-2019-044115.00 (763758) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-044 (763758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.2. GEN-2019-044 (763758) 115.0 kV to G19-044-XFM1 (763759) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0707 | Single Phase Fault with Stuck Breaker on GEN-2011-008345.00 (539840) 345 kV Bus a. Apply Fault at the GEN-2011-008345.00 (539840) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2011-008 (539840) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. GEN-2011-008 (539840) 345.0 kV to G-2011-008-3 (539857) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0708 | Single Phase Fault with Stuck Breaker on GEN-2019-058345.00 (763890) 345 kV Bus a. Apply Fault at the GEN-2019-058345.00 (763890) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-058 (763890) 345.0 kV to G19-058-XFM1 (763891) 34.5 kV Two Winding #1 b.2. GEN-2019-058 (763890) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0709 | Single Phase Fault with Stuck Breaker on GEN-2008-124345.00 (579480) 345 kV Bus a. Apply Fault at the GEN-2008-124345.00 (579480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2008-124 (579480) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. GEN-2008-124 (579480) 345.0 kV to G08-124XFMR1 (579481) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0710 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0711 | Single Phase Fault with Stuck Breaker on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply Fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCONGRS5 (541318) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 b.2. NCONGRS5 (541318) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0712 | Single Phase Fault with Stuck Breaker on WESTON 5 161.00 (541351) 161 kV Bus a. Apply Fault at the WESTON 5 161.00 (541351) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTON 5 (541351) 161.0 kV to IATAN5 (541350) 161.0 kV Transmission Circuit #1 b.2. WESTON 5 (541351) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0713 | Single Phase Fault with Stuck Breaker on OAKGRV 5 161.00 (541227) 161 kV Bus a. Apply Fault at the OAKGRV 5 161.00 (541227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKGRV 5 (541227) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 b.2. OAKGRV 5 (541227) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0714 | Single Phase Fault with Stuck Breaker on TIFFANY5 161.00 (543026) 161 kV Bus a. Apply Fault at the TIFFANY5 161.00 (543026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIFFANY5 (543026) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. TIFFANY5 (543026) 161.0 kV to WETHRBY5 (543017) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0715 | Single Phase Fault with Stuck Breaker on FRSTCRK5 161.00 (543039) 161 kV Bus a. Apply Fault at the FRSTCRK5 161.00 (543039) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRSTCRK5 (543039) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. FRSTCRK5 (543039) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0716 | Single Phase Fault with Stuck Breaker on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply Fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0717 | Single Phase Fault with Stuck Breaker on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply Fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LKWOOD 5 (541238) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 b.2. LKWOOD 5 (541238) 161.0 kV to RAYTOWN5 (541219) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0718 | Single Phase Fault with Stuck Breaker on NUCOR5 161.00 (541395) 161 kV Bus a. Apply Fault at the NUCOR5 161.00 (541395) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUCOR5 (541395) 161.0 kV to NUCOR_D1 (541396) 13.8 kV Two Winding #1 b.2. NUCOR5 (541395) 161.0 kV to NUCOR_S1 (541398) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0719 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0720 | Single Phase Fault with Stuck Breaker on WARSAWTP 69.000 (541281) 69 kV Bus a. Apply Fault at the WARSAWTP 69.000 (541281) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARSAWTP (541281) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 b.2. WARSAWTP (541281) 69.0 kV to WARSAW 2 (541277) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0721 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0722 | Single Phase Fault with Stuck Breaker on GEN-2017-195345.00 (762279) 345 kV Bus a. Apply Fault at the GEN-2017-195345.00 (762279) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-195 (762279) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-195 (762279) 345.0 kV to G17-195XFM1 (762280) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0723 | Single Phase Fault with Stuck Breaker on HICKMAN5 161.00 (542994) 161 kV Bus a. Apply Fault at the HICKMAN5 161.00 (542994) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HICKMAN5 (542994) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. HICKMAN5 (542994) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0724 | Single Phase Fault with Stuck Breaker on ANTIOCH5 161.00 (543050) 161 kV Bus a. Apply Fault at the ANTIOCH5 161.00 (543050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. ANTIOCH5 (543050) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0725 | Single Phase Fault with Stuck Breaker on REDEL 5 161.00 (543053) 161 kV Bus a. Apply Fault at the REDEL 5 161.00 (543053) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDEL 5 (543053) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. REDEL 5 (543053) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0726 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0727 | Single Phase Fault with Stuck Breaker on G17-108-TAP 161.00 (761278) 161 kV Bus a. Apply Fault at the G17-108-TAP 161.00 (761278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-108-TAP (761278) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. G17-108-TAP (761278) 161.0 kV to GEN-2021-050 (765750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0728 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #z2 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0729 | Single Phase Fault with Stuck Breaker on G20-007-TAP 345.00 (766261) 345 kV Bus a. Apply Fault at the G20-007-TAP 345.00 (766261) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0730 | Single Phase Fault with Stuck Breaker on TERRACE5 161.00 (542991) 161 kV Bus a. Apply Fault at the TERRACE5 161.00 (542991) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0731 | Single Phase Fault with Stuck Breaker on FOREST 5 161.00 (543001) 161 kV Bus a. Apply Fault at the FOREST 5 161.00 (543001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOREST 5 (543001) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. FOREST 5 (543001) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0732 | Single Phase Fault with Stuck Breaker on ROEPARK5 161.00 (543040) 161 kV Bus a. Apply Fault at the ROEPARK5 161.00 (543040) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROEPARK5 (543040) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 b.2. ROEPARK5 (543040) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0733 | Single Phase Fault with Stuck Breaker on WINJT N5 161.00 (543009) 161 kV Bus a. Apply Fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT N5 (543009) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT N5 (543009) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0734 | Single Phase Fault with Stuck Breaker on WINJT S5 161.00 (543010) 161 kV Bus a. Apply Fault at the WINJT S5 161.00 (543010) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT S5 (543010) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT S5 (543010) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0735 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NKANCTY5 (543018) 161.0 kV to AVONDAL5 (543015) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0736 | Single Phase Fault with Stuck Breaker on LINECRK5 161.00 (543025) 161 kV Bus a. Apply Fault at the LINECRK5 161.00 (543025) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LINECRK5 (543025) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 b.2. LINECRK5 (543025) 161.0 kV to RIVRSID5 (543021) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0737 | Single Phase Fault with Stuck Breaker on GEN-2022-073161.00 (768441) 161 kV Bus a. Apply Fault at the GEN-2022-073161.00 (768441) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-073 (768441) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. GEN-2022-073 (768441) 161.0 kV to G22-073XFMR1 (768442) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0738 | Single Phase Fault with Stuck Breaker on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply Fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTY 2 (543092) 69.0 kV to LAKCTYJ2 (543087) 69.0 kV Transmission Circuit #1 b.2. LAKCTY 2 (543092) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0739 | Single Phase Fault with Stuck Breaker on LAKCTYK2 69.000 (543093) 69 kV Bus a. Apply Fault at the LAKCTYK2 69.000 (543093) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYK2 (543093) 69.0 kV to DUNCNRD2 (543091) 69.0 kV Transmission Circuit #1 b.2. LAKCTYK2 (543093) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0740 | Single Phase Fault with Stuck Breaker on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply Fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 b.2. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0741 | Single Phase Fault with Stuck Breaker on GAT258 2 69.000 (547551) 69 kV Bus a. Apply Fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GAT258 2 (547551) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 b.2. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0742 | Single Phase Fault with Stuck Breaker on JOP430 2 69.000 (547608) 69 kV Bus a. Apply Fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP430 2 (547608) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 b.2. JOP430 2 (547608) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0743 | Single Phase Fault with Stuck Breaker on GAL278T 69.000 (547728) 69 kV Bus a. Apply Fault at the GAL278T 69.000 (547728) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GAL278T (547728) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 b.2. GAL278T (547728) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0744 | Single Phase Fault with Stuck Breaker on RIV406 2 69.000 (547602) 69 kV Bus a. Apply Fault at the RIV406 2 69.000 (547602) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV406 2 (547602) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. RIV406 2 (547602) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0745 | Single Phase Fault with Stuck Breaker on SUB P 69.000 (548827) 69 kV Bus a. Apply Fault at the SUB P 69.000 (548827) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB P (548827) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB P (548827) 69.0 kV to SUB I (548800) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0746 | Single Phase Fault with Stuck Breaker on SUB R 69.000 (548830) 69 kV Bus a. Apply Fault at the SUB R 69.000 (548830) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB R (548830) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SUB R (548830) 69.0 kV to SUB K (548801) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0747 | Single Phase Fault with Stuck Breaker on GEN-2018-031161.00 (762669) 161 kV Bus a. Apply Fault at the GEN-2018-031161.00 (762669) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-031 (762669) 161.0 kV to G18-031XFM1 (762670) 34.5 kV Two Winding #1 b.2. GEN-2018-031 (762669) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0748 | Single Phase Fault with Stuck Breaker on G15052_1 345.00 (562900) 345 kV Bus a. Apply Fault at the G15052_1 345.00 (562900) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15052_1 (562900) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. G15052_1 (562900) 345.0 kV to G15052_2 (562901) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0749 | Single Phase Fault with Stuck Breaker on GEN-2016-046345.00 (587310) 345 kV Bus a. Apply Fault at the GEN-2016-046345.00 (587310) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-046 (587310) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-046 (587310) 345.0 kV to G16-046XFMR1 (587311) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0750 | Single Phase Fault with Stuck Breaker on GEN-2016-050345.00 (587350) 345 kV Bus a. Apply Fault at the GEN-2016-050345.00 (587350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-050 (587350) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-050 (587350) 345.0 kV to G16-050XFMR1 (587351) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0751 | Single Phase Fault with Stuck Breaker on GEN-2017-086345.00 (589240) 345 kV Bus a. Apply Fault at the GEN-2017-086345.00 (589240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-086 (589240) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-086 (589240) 345.0 kV to G17-086XFMR1 (589241) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0752 | Single Phase Fault with Stuck Breaker on GEN-2020-011345.00 (764420) 345 kV Bus a. Apply Fault at the GEN-2020-011345.00 (764420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-011 (764420) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-011 (764420) 345.0 kV to G20-011-SS3 (764433) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0753 | Single Phase Fault with Stuck Breaker on G18-125-TAP 345.00 (763410) 345 kV Bus a. Apply Fault at the G18-125-TAP 345.00 (763410) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0754 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0755 | Single Phase Fault with Stuck Breaker on GEN-2022-054345.00 (768061) 345 kV Bus a. Apply Fault at the GEN-2022-054345.00 (768061) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-054 (768061) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-054 (768061) 345.0 kV to G22-054XFMR1 (768062) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0756 | Single Phase Fault with Stuck Breaker on GEN-2021-030345.00 (765580) 345 kV Bus a. Apply Fault at the GEN-2021-030345.00 (765580) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-030 (765580) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-030 (765580) 345.0 kV to G21-030-XFM1 (765584) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0757 | Single Phase Fault with Stuck Breaker on GEN-2021-069345.00 (765920) 345 kV Bus a. Apply Fault at the GEN-2021-069345.00 (765920) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-069 (765920) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-069 (765920) 345.0 kV to G21-069-XFM1 (765924) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0758 | Single Phase Fault with Stuck Breaker on GEN-2021-070345.00 (765930) 345 kV Bus a. Apply Fault at the GEN-2021-070345.00 (765930) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-070 (765930) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-070 (765930) 345.0 kV to G21-070-XFM1 (765934) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0759 | Single Phase Fault with Stuck Breaker on GEN-2022-007115.00 (767121) 115 kV Bus a. Apply Fault at the GEN-2022-007115.00 (767121) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-007 (767121) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 b.2. GEN-2022-007 (767121) 115.0 kV to G22-007XFMR1 (767122) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0760 | Single Phase Fault with Stuck Breaker on GEN-2022-013345.00 (767241) 345 kV Bus a. Apply Fault at the GEN-2022-013345.00 (767241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-013 (767241) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-013 (767241) 345.0 kV to G22-013XFMR1 (767242) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0761 | Single Phase Fault with Stuck Breaker on GEN-2022-015345.00 (767281) 345 kV Bus a. Apply Fault at the GEN-2022-015345.00 (767281) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-015 (767281) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-015 (767281) 345.0 kV to G22-015XFMR1 (767282) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0762 | Single Phase Fault with Stuck Breaker on GEN-2022-065230.00 (768281) 230 kV Bus a. Apply Fault at the GEN-2022-065230.00 (768281) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-065 (768281) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. GEN-2022-065 (768281) 230.0 kV to G22-065XFMR1 (768282) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0763 | Single Phase Fault with Stuck Breaker on GEN-2022-075345.00 (768481) 345 kV Bus a. Apply Fault at the GEN-2022-075345.00 (768481) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-075 (768481) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-075 (768481) 345.0 kV to G22-075XFMR1 (768482) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0764 | Single Phase Fault with Stuck Breaker on GEN-2022-214138.00 (771261) 138 kV Bus a. Apply Fault at the GEN-2022-214138.00 (771261) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-214 (771261) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 b.2. GEN-2022-214 (771261) 138.0 kV to G22-214XFMR1 (771262) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0765 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0766 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0767 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.2. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0768 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0769 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 7 (531465) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0770 | Single Phase Fault with Stuck Breaker on JEC 6 230.00 (532852) 230 kV Bus a. Apply Fault at the JEC 6 230.00 (532852) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0771 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to RENO 7 (532771) 345.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 b.2. RENO 3 (533416) 115.0 kV to RENO 7 (532771) 345.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0772 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR3 (533268) 115.0 kV to STRANGR7 (532772) 345.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR3 (533268) 115.0 kV to STRANGR7 (532772) 345.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0773 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0774 | Single Phase Fault with Stuck Breaker on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0775 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK3 (533315) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #2 b.2. OTTRCRK3 (533315) 115.0 kV to OTTRCRK4 (532997) 138.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0776 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASO 2 (533793) 69.0 kV to ELPASOE4 (533059) 138.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 b.2. ELPASO 2 (533793) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0777 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0778 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0779 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to PHILL 7 (541200) 345.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0780 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 5 (541202) 161.0 kV to SIBLEY 7 (541201) 345.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0781 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0782 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0783 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. WGARDNR5 (542966) 161.0 kV to W.GRDNR7 (542965) 345.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0784 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTH 7 (542972) 345.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTHN5 (543665) 161.0 kV to HAWTH 7 (542972) 345.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0785 | Single Phase Fault with Stuck Breaker on LAC3_STAR7 345.00 (543667) 345 kV Bus a. Apply Fault at the LAC3_STAR7 345.00 (543667) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC3_STAR7 (543667) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h b.2. LAC3_STAR7 (543667) 345.0 kV to LAC3_Y1 (543662) 6.9 kV Two Winding #y | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0786 | Single Phase Fault with Stuck Breaker on LAC8_STAR7 345.00 (543669) 345 kV Bus a. Apply Fault at the LAC8_STAR7 345.00 (543669) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC8_STAR7 (543669) 345.0 kV to LAC8_Z1 (543672) 4.0 kV Two Winding #z b.2. LAC8_STAR7 (543669) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0787 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 2 (547534) 69.0 kV to ORO110 5 (547467) 161.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 b.2. ORO110 2 (547534) 69.0 kV to WEB436 2 (547527) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0788 | Single Phase Fault with Stuck Breaker on JOP389 2 69.000 (547592) 69 kV Bus a. Apply Fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 b.2. JOP389 2 (547592) 69.0 kV to EXP449T2 (547438) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0789 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 4 (547486) 138.0 kV to VINTAJC4 (510417) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0790 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 2 (547601) 69.0 kV to HOC404 5 (547487) 161.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 b.2. HOC404 2 (547601) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0791 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.2. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0792 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 b.2. KEYSTON3 (640252) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0793 | Single Phase Fault with Stuck Breaker on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply Fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STOCKVL7 (640365) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. STOCKVL7 (640365) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0794 | Single Phase Fault with Stuck Breaker on GILL E 2 (533795) 69 kV Bus a. Apply Fault at the GILL E 2 (533795) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0795 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0796 | Single Phase Fault with Stuck Breaker on GILL W 2 (533796) 69 kV Bus a. Apply Fault at the GILL W 2 (533796) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL W 2 (533796) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0797 | Single Phase Fault with Stuck Breaker on HOOVERS2 (533806) 69 kV Bus a. Apply Fault at the HOOVERS2 (533806) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HOOVERS2 (533806) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0798 | Single Phase Fault with Stuck Breaker on GILL E 4 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 (533044) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0799 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0800 | Single Phase Fault with Stuck Breaker on HOOVERN4 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 (533049) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0801 | Single Phase Fault with Stuck Breaker on ALTOO E2 (533673) 69 kV Bus a. Apply Fault at the ALTOO E2 (533673) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. ALTOO E2 (533673) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0802 | Single Phase Fault with Stuck Breaker on NEOSHON2 (533768) 69 kV Bus a. Apply Fault at the NEOSHON2 (533768) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHON2 (533768) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0803 | Single Phase Fault with Stuck Breaker on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0804 | Single Phase Fault with Stuck Breaker on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0805 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0806 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0807 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0808 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0809 | Single Phase Fault with Stuck Breaker on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0810 | Single Phase Fault with Stuck Breaker on OSAGE J3 (533171) 115 kV Bus a. Apply Fault at the OSAGE J3 (533171) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. OSAGE J3 (533171) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0811 | Single Phase Fault with Stuck Breaker on WEMPORI3 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 (533309) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0812 | Single Phase Fault with Stuck Breaker on MORRIS 7 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 (532770) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MORRIS 7 (532770) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0813 | Single Phase Fault with Stuck Breaker on STILWEL5 (542969) 161 kV Bus a. Apply Fault at the STILWEL5 (542969) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0814 | Single Phase Fault with Stuck Breaker on REDWILO7 (640326) 115 kV Bus a. Apply Fault at the REDWILO7 (640326) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0815 | Single Phase Fault with Stuck Breaker on GENTLMN4 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 (640184) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0816 | Single Phase Fault with Stuck Breaker on SETAB 3 (531464) 115 kV Bus a. Apply Fault at the SETAB 3 (531464) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SETAB 3 (531464) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0817 | Single Phase Fault with Stuck Breaker on MINGO 3 (531429) 115 kV Bus a. Apply Fault at the MINGO 3 (531429) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0818 | Single Phase Fault with Stuck Breaker on SPEARVL3 (539694) 115 kV Bus a. Apply Fault at the SPEARVL3 (539694) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SPEARVL3 (539694) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0819 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0820 | Single Phase Fault with Stuck Breaker on NFTDODG3 (539771) 115 kV Bus a. Apply Fault at the NFTDODG3 (539771) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NFTDODG3 (539771) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0821 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0822 | Single Phase Fault with Stuck Breaker on NASHUA 5 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 (541203) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0823 | Single Phase Fault with Stuck Breaker on PLTCTY 5 (541221) 161 kV Bus a. Apply Fault at the PLTCTY 5 (541221) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. PLTCTY 5 (541221) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0824 | Single Phase Fault with Stuck Breaker on GLADSTN5 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 (543016) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0825 | Single Phase Fault with Stuck Breaker on TWA 5 (541214) 161 kV Bus a. Apply Fault at the TWA 5 (541214) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0826 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0827 | Single Phase Fault with Stuck Breaker on SEDN 2 (541271) 69 kV Bus a. Apply Fault at the SEDN 2 (541271) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SEDN 2 (541271) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0828 | Single Phase Fault with Stuck Breaker on SEDPLT 2 (541275) 69 kV Bus a. Apply Fault at the SEDPLT 2 (541275) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SEDPLT 2 (541275) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0829 | Single Phase Fault with Stuck Breaker on 5GEORGE (300082) 161 kV Bus a. Apply Fault at the 5GEORGE (300082) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0830 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 (344234) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. 5CALIF UE 2 (344234) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0831 | Single Phase Fault with Stuck Breaker on 5MCBAIN T (345071) 161 kV Bus a. Apply Fault at the 5MCBAIN T (345071) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. 5MCBAIN T (345071) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0832 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0833 | Single Phase Fault with Stuck Breaker on FRSTCRK5 (543039) 161 kV Bus a. Apply Fault at the FRSTCRK5 (543039) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. FRSTCRK5 (543039) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0834 | Single Phase Fault with Stuck Breaker on SMTHVL 5 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 (541204) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0835 | Single Phase Fault with Stuck Breaker on BLSPE 5 (541205) 161 kV Bus a. Apply Fault at the BLSPE 5 (541205) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BLSPE 5 (541205) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0836 | Single Phase Fault with Stuck Breaker on NEASTS5 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 (542985) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0837 | Single Phase Fault with Stuck Breaker on GRAND W5 (542988) 161 kV Bus a. Apply Fault at the GRAND W5 (542988) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GRAND W5 (542988) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0838 | Single Phase Fault with Stuck Breaker on NAVY 5 (542989) 161 kV Bus a. Apply Fault at the NAVY 5 (542989) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NAVY 5 (542989) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0839 | Single Phase Fault with Stuck Breaker on AVONDAL5 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 (543015) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0840 | Single Phase Fault with Stuck Breaker on SUB J (548811) 69 kV Bus a. Apply Fault at the SUB J (548811) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SUB J (548811) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0841 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0842 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0843 | Single Phase Fault with Stuck Breaker on LANG 3 (533304) 115 kV Bus a. Apply Fault at the LANG 3 (533304) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. LANG 3 (533304) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0844 | Single Phase Fault with Stuck Breaker on EVANS N4 (533040) 138 kV Bus a. Apply Fault at the EVANS N4 (533040) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0845 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0846 | Single Phase Fault with Stuck Breaker on MILAN_GOAB (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB (539008) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0847 | Single Phase Fault with Stuck Breaker on SUMNER 4 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 (532984) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0848 | Single Phase Fault with Stuck Breaker on GILL W 4 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 (533045) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL W 4 (533045) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0849 | Single Phase Fault with Stuck Breaker on GILL S 4 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 (533046) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL S 4 (533046) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0012 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0013 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0015 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0016 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0017 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0018 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0019 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0020 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0021 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0022 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0023 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0024 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0025 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0026 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0027 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0028 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0029 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0030 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0031 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0032 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0033 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0034 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0035 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0036 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0037 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0038 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0039 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0040 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0041 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0042 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0043 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0044 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0045 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0046 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0047 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0001 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0002 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0003 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0004 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA17-1 (512688) 22.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0005 | Single Phase Fault with Stuck Breaker on GREC TAP7 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 (512865) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRECSTG_1 (512615) 21.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0006 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0007 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0008 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0009 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_OKGE_FAULT_0001 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.3. KAYWNDG1 (515651) 0.7 kV to Generator #1 b.4. KAYWNDG2 (515652) 0.7 kV to Generator #1 b.5. KAYWND11 (515622) 34.5 kV to Load #S1 b.6. KAYWND12 (515623) 34.5 kV to Load #S1 b.7. KAYWIND7 (514825) 345.0 kV to remove bus # b.8. KAYWNDT1 (515619) 12.5 kV to remove bus # b.9. KAYWNDT2 (515620) 12.5 kV to remove bus # b.10. OPENSKY7 (515621) 345.0 kV to remove bus # b.11. KAYWND11 (515622) 34.5 kV to remove bus # b.12. KAYWND12 (515623) 34.5 kV to remove bus # b.13. KAYWNDG1 (515651) 0.7 kV to remove bus # b.14. KAYWNDG2 (515652) 0.7 kV to remove bus # b.15. KAYWNDC1 (515653) 34.5 kV to remove bus # b.16. KAYWNDC2 (515654) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_SPS_FAULT_0001 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DUNES23 (523061) 0.7 kV to Generator #1 b.12. BUFF_DUNES13 (523062) 0.7 kV to Generator #1 b.13. BUFF_DUNES23 (523061) 0.7 kV to remove bus # b.14. BUFF_DUNES13 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNES22 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNES12 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_KACY_FAULT_0001 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_KACY_FAULT_0002 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.3. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 b.4. SHAWNEE5 (543041) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.5. SHAWNEE5 (543041) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_KACY_FAULT_0003 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EDE_FAULT_0001 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.3. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. JOP389 5 (547483) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.7. TIP292 5 (547472) 161.0 kV to Load #1 b.8. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EDE_FAULT_0002 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 7 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Breaker at To Bus #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EDE_FAULT_0003 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 b.3. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EDE_FAULT_0004 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.3. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.6. TIP292 5 (547472) 161.0 kV to Load #1 b.7. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_NPPD_FAULT_0001 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_NPPD_FAULT_0002 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_NPPD_FAULT_0003 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.4. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_NPPD_FAULT_0004 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_SUNC_FAULT_0001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_0001 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_0002 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_0003 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_0004 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_0005 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_0006 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_0007 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_0008 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_0009 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_INDN_FAULT_0010 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0001 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.4. CLBYT1 1 (530645) 13.8 kV to remove bus # b.5. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Load #99 b.12. COLBY 3 (530555) 115.0 kV to Generator #C8 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0002 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. CLBYT1 1 (530645) 13.8 kV to remove bus # b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Generator #C8 b.12. COLBY 3 (530555) 115.0 kV to Load #99 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0003 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0004 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0005 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0006 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.4. GMECG1 1 (530674) 13.8 kV to remove bus # b.5. GMECG2 1 (530675) 13.8 kV to remove bus # b.6. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0007 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMECG1 1 (530674) 13.8 kV to remove bus # b.3. GMECG2 1 (530675) 13.8 kV to remove bus # b.5. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.6. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.7. N HAYS3 (530581) 115.0 kV to remove bus # b.8. VINETAP3 (530693) 115.0 kV to remove bus # b.9. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0008 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to remove bus # b.4. VINETAP3 (530693) 115.0 kV to remove bus # b.5. GMECG1 1 (530674) 13.8 kV to remove bus # b.6. GMECG2 1 (530675) 13.8 kV to remove bus # b.7. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0009 | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 (530553) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. ANGUS 3 (530714) 115.0 kV to GORHAM 3 (530552) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.5. ANGUS 3 (530714) 115.0 kV to Load #1 b.6. PFEIFER 3 (530725) 115.0 kV to Load #1 b.7. ANGUS 3 (530714) 115.0 kV to remove bus # b.8. PFEIFER 3 (530725) 115.0 kV to remove bus # b.9. GORHAM 3 (530552) 115.0 kV to Load #1 b.10. RUSLPMP3 (530684) 115.0 kV to Load #1 b.11. GORHAM 3 (530552) 115.0 kV to remove bus # b.12. RUSLPMP3 (530684) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0010 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0011 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0012 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0013 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0014 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0015 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.4. BUCKE_WTG (530705) 0.7 kV to remove bus # b.5. BUCKW_WTG (530708) 0.7 kV to remove bus # b.6. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.7. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.8. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.9. BUCKW_TERT (530706) 13.8 kV to remove bus # b.10. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.11. BUCKE_TERT (530709) 13.8 kV to remove bus # b.12. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0016 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0017 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0018 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0019 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0020 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0021 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0022 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0023 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0024 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. SMOKYHL6 (530592) 230.0 kV to SMKYP2 6 (530599) 230.0 kV Transmission Circuit #1 b.4. SHG2 34 1 (530715) 34.5 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus # b.6. SMKYP2 6 (530599) 230.0 kV to remove bus # b.7. SHP234 1 (530604) 34.5 kV to remove bus # b.8. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0025 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 38 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus # b.3. SMKYP1 6 (530593) 230.0 kV to remove bus # b.4. SMKYP1G1 (530594) 0.7 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus # b.6. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0026 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.3. SMKYT2 1 (530634) 13.9 kV to Generator #1 b.4. SMKYT2 1 (530634) 13.9 kV to remove bus # b.5. SMKYP1G1 (530594) 0.7 kV to remove bus # b.6. SMKYP1 6 (530593) 230.0 kV to remove bus # b.7. SHP134 1 (530595) 34.5 kV to remove bus # b.8. SMKYT1 1 (530633) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0027 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus # b.3. SMKYP1 6 (530593) 230.0 kV to remove bus # b.4. SMKYP1G1 (530594) 0.7 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0028 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0029 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0030 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0031 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0032 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.3. LACROS 3 (530603) 115.0 kV to remove bus # b.4. NEKOMA 3 (530608) 115.0 kV to remove bus # b.5. ALXNDR 3 (530606) 115.0 kV to remove bus # b.7. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.8. HZRNGPL3 (530609) 115.0 kV to remove bus # b.9. ALEXNDR1 (539702) 34.5 kV to Load #1 b.10. LAXTAP 3 (530602) 115.0 kV to remove bus # b.11. NKMA2 1 (530630) 12.5 kV to remove bus # b.12. ALEXNDR1 (539702) 34.5 kV to remove bus # b.13. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0033 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0034 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.4. LACROS 3 (530603) 115.0 kV to remove bus # b.5. NEKOMA 3 (530608) 115.0 kV to remove bus # b.6. ALXNDR 3 (530606) 115.0 kV to remove bus # b.8. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.9. ALEXNDR1 (539702) 34.5 kV to Load #1 b.10. LAXTAP 3 (530602) 115.0 kV to remove bus # b.11. NKMA2 1 (530630) 12.5 kV to remove bus # b.12. ALEXNDR1 (539702) 34.5 kV to remove bus # b.13. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0035 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0036 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 6 (530686) 230.0 kV to remove bus # b.3. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. PRWINDG1 (530690) 0.7 kV to Generator #1 b.6. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.7. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.8. PRWINDG1 (530690) 0.7 kV to remove bus # b.9. BUFCRKT11 (530691) 12.5 kV to remove bus # b.10. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0037 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0038 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0039 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. COLBY 3 (530555) 115.0 kV to remove bus # b.6. CLBYT1 1 (530645) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0040 | Single Phase Fault with Stuck Breaker on BEACH 3 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 (530557) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HOXIE 3 (530556) 115.0 kV Transmission Circuit #1 b.5. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.6. BEACH 3 (530557) 115.0 kV to remove bus # b.7. HILLCTY3 (531387) 34.5 kV to Generator #1 b.8. HILLCTY3 (531387) 34.5 kV to Generator #2 b.9. HILLCTY3 (531387) 34.5 kV to Generator #3 b.10. HILLCTY3 (531387) 34.5 kV to Generator #4 b.11. HILLCTY3 (531387) 34.5 kV to Generator #5 b.12. HILLCTY3 (531387) 34.5 kV to Generator #6 b.13. HILLCTY3 (531387) 34.5 kV to remove bus # b.14. REDLIN 3 (530605) 115.0 kV to remove bus # b.15. HOXIE 3 (530556) 115.0 kV to remove bus # b.16. REDLIN 3 (530605) 115.0 kV to Load #71 b.17. HOXIE 3 (530556) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0041 | Single Phase Fault with Stuck Breaker on ATWOOD 3 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 (530554) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to remove bus # b.5. ATWOOD 3 (530554) 115.0 kV to Generator #1 b.6. HILLCTY3 (531387) 34.5 kV to Generator #1 b.7. HILLCTY3 (531387) 34.5 kV to Generator #2 b.8. HILLCTY3 (531387) 34.5 kV to Generator #3 b.9. HILLCTY3 (531387) 34.5 kV to Generator #4 b.10. HILLCTY3 (531387) 34.5 kV to Generator #5 b.11. HILLCTY3 (531387) 34.5 kV to Generator #6 b.12. ATWOOD 3 (530554) 115.0 kV to Load #1 b.13. ATWOOD 3 (530554) 115.0 kV to Load #41 b.14. ATWOOD 3 (530554) 115.0 kV to remove bus # b.15. HILLCTY3 (531387) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0042 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0001 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.2. JEC U1 (532651) 26.0 kV to remove bus # b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0002 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.2. JEC U2 (532652) 26.0 kV to remove bus # b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0003 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.2. JEC U3 (532653) 26.0 kV to remove bus # b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0004 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0005 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0006 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0007 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #1 b.4. EMPEC121 (532740) 13.8 kV to Generator #2 b.5. EMPEC121 (532740) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0008 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.2. EMPEC121 (532740) 13.8 kV to Generator #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #2 b.4. EMPEC121 (532740) 13.8 kV to remove bus # b.5. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0009 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0010 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.2. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.3. EMPEC7 1 (532744) 18.0 kV to remove bus # b.4. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0011 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0012 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0013 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0014 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0015 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0016 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0017 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0018 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0019 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0020 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0021 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0022 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0023 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0024 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0025 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0026 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0027 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0028 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to remove bus # b.4. RANDLPH5 (543027) 161.0 kV to Load #1 b.5. RANDLPH5 (543027) 161.0 kV to Load #4 b.6. RANDLPH5 (543027) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0029 | Single Phase Fault with Stuck Breaker on Hawthorn South (542973) 161 kV Bus a. Apply Fault at the Hawthorn South (542973) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0030 | Single Phase Fault with Stuck Breaker on Hawthorn 161 kV (542973) 161 kV Bus a. Apply Fault at the Hawthorn 161 kV (542973) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@1 b.2. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0031 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0032 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0033 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0034 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0035 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0036 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. IAT G1 1 (542957) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0037 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0038 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0039 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0040 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. LAC G2 1 (542956) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0041 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0042 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 b.4. NEASTN5 (543666) 161.0 kV to Load #78 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0043 | Single Phase Fault with Stuck Breaker on Stilwell 345 kV (542968) 345 kV Bus a. Apply Fault at the Stilwell 345 kV (542968) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0044 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0045 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0046 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to JEC N 7 (532766) 345.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0047 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0048 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0049 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0050 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0051 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0052 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0053 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0054 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 5.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0055 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0056 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0057 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0058 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0059 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0060 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0061 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0062 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0063 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0064 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0065 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0066 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0067 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0068 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0069 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0070 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0071 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0072 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@1 b.2. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0073 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0074 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0075 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0076 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0077 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IAT G1 1 (542957) 24.0 kV to remove bus # b.2. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0078 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to remove bus # b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0079 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 b.3. LACYGNE2 (543659) 69.0 kV to remove bus # b.4. LAC_LAKE_2 (541541) 69.0 kV to remove bus # b.5. LAC_LAKE_2 (541541) 69.0 kV to Load #K1 b.6. LAC_LAKE_2 (541541) 69.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0080 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0081 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0082 | Single Phase Fault with Stuck Breaker on Northeast North (543666) 161 kV Bus a. Apply Fault at the Northeast North (543666) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NEASTN5 (543666) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to remove bus # b.4. NE CT14 (542971) 13.8 kV to remove bus # b.5. NEASTN5 (543666) 161.0 kV to Load #56 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0083 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NE CT17 (542983) 13.8 kV to remove bus # b.2. NE CT18 (542984) 13.8 kV to remove bus # b.3. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.4. NEASTS5 (542985) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 b.5. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 b.6. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0084 | Single Phase Fault with Stuck Breaker on Stilwell 345 kV (542968) 345 kV Bus a. Apply Fault at the Stilwell 345 kV (542968) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0085 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0086 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0087 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0001 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0002 | 3 Phase fault on 5ELDON 1 161.00 (344532) 161 kV Bus a. Apply fault at the 5ELDON 1 161.00 (344532) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.2. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.3. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.4. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0003 | 3 Phase fault on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOYMART 1 (344040) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.2. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0004 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0005 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0006 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0007 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0008 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0009 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BOONE (300061) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0010 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0011 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1 (541546) and OUTLAW_G21 (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0012 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0013 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0014 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0015 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0016 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0017 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0018 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0019 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0020 | 3 Phase fault on OAKGRV 5 161.00 (541227) 161 kV Bus a. Apply fault at the OAKGRV 5 161.00 (541227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAINVL5 (541226) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 b.2. OAKGRV 5 (541227) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0021 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0022 | 3 Phase fault on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0023 | 3 Phase fault on STALEY 2 69.000 (541261) 69 kV Bus a. Apply fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0024 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0025 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0026 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0027 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0028 | 3 Phase fault on BRMALL 2 69.000 (541283) 69 kV Bus a. Apply fault at the BRMALL 2 69.000 (541283) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMALL 2 (541283) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0029 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0030 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0031 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0032 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0033 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0034 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0035 | 3 Phase fault on SUB E 69.000 (548804) 69 kV Bus a. Apply fault at the SUB E 69.000 (548804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0036 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0037 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0038 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0039 | 3 Phase fault on SUB B 69.000 (548810) 69 kV Bus a. Apply fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0040 | 3 Phase fault on SUB J 69.000 (548811) 69 kV Bus a. Apply fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0041 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0042 | 3 Phase fault on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0043 | 3 Phase fault on STRLNGRD 69.000 (548826) 69 kV Bus a. Apply fault at the STRLNGRD 69.000 (548826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.3. SUB C (548825) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0044 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0045 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0046 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0047 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0048 | 3 Phase fault on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0049 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0050 | 3 Phase fault on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0051 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0052 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0053 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 b.2. ST JOE_CAP5 (541147) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0054 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.3. RNRIDGE_CAP5 (541145) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0055 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0056 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0057 | 3 Phase fault on NAVY 5 161.00 (542989) 161 kV Bus a. Apply fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0058 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0059 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0060 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. BARRY_CAP 5 (542944) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0061 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0062 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0063 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0064 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0065 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0066 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0067 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0068 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0069 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0070 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0071 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1 (541546) and OUTLAW_G21 (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0072 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1 (541546) and OUTLAW_G21 (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0073 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0074 | 3 Phase fault on MILCKJT2 69.000 (543110) 69 kV Bus a. Apply fault at the MILCKJT2 69.000 (543110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.3. IND WTR2 (543086) 69.0 kV to CEMCITY2 (543090) 69.0 kV Transmission Circuit #1 b.4. IND WTR2 (543086) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.5. TMP LAF2 (543103) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.6. LAFJCT 2 (543104) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.7. MILCKJT2 (543110) 69.0 kV to LAFARGE2 (543111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0075 | 3 Phase fault on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 b.3. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0076 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0077 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0078 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0079 | 3 Phase fault on WPRTTS 2 69.000 (530596) 69 kV Bus a. Apply fault at the WPRTTS 2 69.000 (530596) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.2. GB STH 2 (530569) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.3. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.4. WPRTTS 2 (530596) 69.0 kV to WPRT2 2 (530597) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0080 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0081 | 3 Phase fault on COLLEG 2 69.000 (530574) 69 kV Bus a. Apply fault at the COLLEG 2 69.000 (530574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 b.2. COLLEG 2 (530574) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0082 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0083 | 3 Phase fault on NEKOMA 2 69.000 (530564) 69 kV Bus a. Apply fault at the NEKOMA 2 69.000 (530564) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0084 | 3 Phase fault on BKHLTAP2 69.000 (530589) 69 kV Bus a. Apply fault at the BKHLTAP2 69.000 (530589) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.2. SUSANK 2 (530571) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.3. BNK HL 2 (530572) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.4. HITHMN 2 (530573) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0085 | 3 Phase fault on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0086 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0087 | 3 Phase fault on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0088 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0089 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0090 | 3 Phase fault on SEGNTP 3 115.00 (530682) 115 kV Bus a. Apply fault at the SEGNTP 3 115.00 (530682) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEGNTP 3 (530682) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0091 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0092 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0093 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0094 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0095 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0096 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.2. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.3. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.6. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0097 | 3 Phase fault on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0098 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0099 | 3 Phase fault on HOXIE 3 115.00 (530556) 115 kV Bus a. Apply fault at the HOXIE 3 115.00 (530556) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0100 | 3 Phase fault on ANGELUS 115.00 (530717) 115 kV Bus a. Apply fault at the ANGELUS 115.00 (530717) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.2. SEGNTP 3 (530682) 115.0 kV to SEGUIN 3 (530683) 115.0 kV Transmission Circuit #1 b.3. SEGUIN 3 (530683) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0101 | 3 Phase fault on HUNTSVL3 115.00 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 115.00 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0102 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0103 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0104 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0105 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0106 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0107 | 3 Phase fault on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0108 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0109 | 3 Phase fault on GRHMSUB3 115.00 (531386) 115 kV Bus a. Apply fault at the GRHMSUB3 115.00 (531386) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0110 | 3 Phase fault on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0111 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0112 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0113 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0114 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0115 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0116 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0117 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0118 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0119 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0120 | 3 Phase fault on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0121 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0122 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0123 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0124 | 3 Phase fault on BEACH 3 115.00 (530557) 115 kV Bus a. Apply fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0125 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0126 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0127 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0128 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.2. STOCKVL7 (640365) 115.0 kV to STOCKVL8 (640366) 69.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 b.4. STOCKVLLET19 (643146) 13.8 kV to STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0129 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0130 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0131 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0132 | 3 Phase fault on ATHEY 7 115.00 (641244) 115 kV Bus a. Apply fault at the ATHEY 7 115.00 (641244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 b.2. ATHEY 7 (641244) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 b.3. LAMAR___-TS7 (659804) 115.0 kV to CRETE___-TS7 (659813) 115.0 kV Transmission Circuit #1 b.4. CRETE___-TS7 (659813) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0133 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0134 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0135 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0136 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0137 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0138 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0139 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0140 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0141 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0142 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0143 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0144 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0145 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0146 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0147 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0148 | 3 Phase fault on BEVERLY8 69.000 (640083) 69 kV Bus a. Apply fault at the BEVERLY8 69.000 (640083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0149 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0150 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0151 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0152 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0153 | 3 Phase fault on MCCOOK 8 69.000 (640270) 69 kV Bus a. Apply fault at the MCCOOK 8 69.000 (640270) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0154 | 3 Phase fault on STOCKVL8 69.000 (640366) 69 kV Bus a. Apply fault at the STOCKVL8 69.000 (640366) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKVL8 (640366) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0155 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0156 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0157 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0158 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0159 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0160 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0161 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0162 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0163 | 3 Phase fault on ANTHONY4 138.00 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 138.00 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0164 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0165 | 3 Phase fault on GRINNEL3 115.00 (531412) 115 kV Bus a. Apply fault at the GRINNEL3 115.00 (531412) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 b.2. ARNOLD3 (531409) 115.0 kV to GOVE 3 (531411) 115.0 kV Transmission Circuit #1 b.3. ARNOLD3 (531409) 115.0 kV to RANSOM 3 (531414) 115.0 kV Transmission Circuit #1 b.4. GOVE 3 (531411) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0166 | 3 Phase fault on SETAB 3 115.00 (531464) 115 kV Bus a. Apply fault at the SETAB 3 115.00 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0167 | 3 Phase fault on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0168 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0169 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0170 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0171 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0172 | 3 Phase fault on WILLIAM3 115.00 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 115.00 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0173 | 3 Phase fault on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEOTI 3 (531428) 115.0 kV to SELKIRK3 (531434) 115.0 kV Transmission Circuit #1 b.2. LEOTI 3 (531428) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 b.3. SELKIRK3 (531434) 115.0 kV to TRIB SW3 (531438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0174 | 3 Phase fault on ATWODSW3 115.00 (531364) 115 kV Bus a. Apply fault at the ATWODSW3 115.00 (531364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.2. LUDELLT3 (531220) 115.0 kV to LUDELL 3 (531221) 115.0 kV Transmission Circuit #1 b.3. LUDELLT3 (531220) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.4. LUDELLT3 (531220) 115.0 kV to HERNDON3 (531367) 115.0 kV Transmission Circuit #1 b.5. ATWODSW3 (531364) 115.0 kV to NATWOOD3 (531369) 115.0 kV Transmission Circuit #1 b.6. HERNDON3 (531367) 115.0 kV to JOHNSON3 (531371) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0175 | 3 Phase fault on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.3. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0176 | 3 Phase fault on GANO 3 115.00 (531493) 115 kV Bus a. Apply fault at the GANO 3 115.00 (531493) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.3. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0177 | 3 Phase fault on KSAVWTP3 115.00 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 115.00 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0178 | 3 Phase fault on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0179 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0180 | 3 Phase fault on SUNCITY3 115.00 (539697) 115 kV Bus a. Apply fault at the SUNCITY3 115.00 (539697) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.3. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.4. GRNBURG3 (539664) 115.0 kV to GRNBURG1 (539710) 34.5 kV to GRNBUG-T (539910) 13.8 kV Three Winding #1 b.5. SUNCITY3 (539697) 115.0 kV to SUNCITY1 (539733) 34.5 kV to SUNCT-T (539937) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0181 | 3 Phase fault on FORD 3 115.00 (539758) 115 kV Bus a. Apply fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.3. FORD 3 (539758) 115.0 kV to FORD 1 (539765) 34.5 kV to FORD T (539968) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0182 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0183 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0184 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0185 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0186 | 3 Phase fault on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0187 | 3 Phase fault on DCBEEF3 115.00 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 115.00 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0188 | 3 Phase fault on SPEARVL3 115.00 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 115.00 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0189 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0190 | 3 Phase fault on N-DODGE3 115.00 (539680) 115 kV Bus a. Apply fault at the N-DODGE3 115.00 (539680) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DODG3 (539641) 115.0 kV to N-DODGE3 (539680) 115.0 kV Transmission Circuit #1 b.2. N-DODGE3 (539680) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. N-DODGE3 (539680) 115.0 kV to N-DODGE1 (539720) 34.5 kV to N-DODG-T (539922) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0191 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0192 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0193 | 3 Phase fault on WALDO 3 115.00 (539698) 115 kV Bus a. Apply fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0194 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0195 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0196 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0197 | 3 Phase fault on HARPER 4 138.00 (539668) 138 kV Bus a. Apply fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0198 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0199 | 3 Phase fault on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL3 (539701) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0200 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0201 | 3 Phase fault on BYRONTP4 138.00 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 138.00 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.2. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0202 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0203 | 3 Phase fault on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0204 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0205 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0206 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0207 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0208 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0209 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0210 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0211 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0212 | 3 Phase fault on CARB-KW 3 115.00 (533195) 115 kV Bus a. Apply fault at the CARB-KW 3 115.00 (533195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 b.2. CARB-KW 3 (533195) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0213 | 3 Phase fault on OSAGE J3 115.00 (533171) 115 kV Bus a. Apply fault at the OSAGE J3 115.00 (533171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.2. OSAGE 3 (533170) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 b.3. OSAGE J3 (533171) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.4. OSAGE J3 (533171) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.5. READING3 (533306) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0214 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGCRK3 (533380) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.2. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.4. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0215 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0216 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0217 | 3 Phase fault on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0218 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0219 | 3 Phase fault on MORRIS 3 115.00 (533305) 115 kV Bus a. Apply fault at the MORRIS 3 115.00 (533305) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0220 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0221 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0222 | 3 Phase fault on NW LEAV3 115.00 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 115.00 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0223 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.2. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0224 | 3 Phase fault on STRANGR3 115.00 (533268) 115 kV Bus a. Apply fault at the STRANGR3 115.00 (533268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0225 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0226 | 3 Phase fault on FOWLER 4 138.00 (533043) 138 kV Bus a. Apply fault at the FOWLER 4 138.00 (533043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0227 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0228 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0229 | 3 Phase fault on 47TH ST4 138.00 (533058) 138 kV Bus a. Apply fault at the 47TH ST4 138.00 (533058) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0230 | 3 Phase fault on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0231 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0232 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0233 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0234 | 3 Phase fault on BELAIRE4 138.00 (532988) 138 kV Bus a. Apply fault at the BELAIRE4 138.00 (532988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0235 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0236 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0237 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0238 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0239 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0240 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0241 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0242 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0243 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0244 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0245 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0246 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0247 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0248 | 3 Phase fault on BU11PON4 138.00 (533032) 138 kV Bus a. Apply fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0249 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0250 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0251 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0252 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0253 | 3 Phase fault on BEECHTP4 138.00 (533028) 138 kV Bus a. Apply fault at the BEECHTP4 138.00 (533028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.2. BEECH 4 (533027) 138.0 kV to BEECHTP4 (533028) 138.0 kV Transmission Circuit #1 b.3. BEECHTP4 (533028) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 b.4. BEECHTP4 (533028) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0254 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0255 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0256 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0257 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0258 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0259 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0260 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0261 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0262 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0263 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0264 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0265 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0266 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0267 | 3 Phase fault on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0268 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0269 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0270 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0271 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0272 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0273 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0274 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0275 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0276 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0277 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0278 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1 (541546) and OUTLAW_G21 (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0279 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0280 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0281 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0282 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0283 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0284 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0285 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0286 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0287 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0288 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0289 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0290 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0291 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0292 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0293 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0294 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0295 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0296 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0297 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0298 | 3 Phase fault on MEAD N 2 69.000 (533818) 69 kV Bus a. Apply fault at the MEAD N 2 69.000 (533818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD N 2 (533818) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0299 | 3 Phase fault on 17TH TP2 69.000 (533835) 69 kV Bus a. Apply fault at the 17TH TP2 69.000 (533835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.2. RIVERSD2 (533834) 69.0 kV to 17TH TP2 (533835) 69.0 kV Transmission Circuit #1 b.3. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.4. 17TH TP2 (533835) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.5. 17TH TP2 (533835) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0300 | 3 Phase fault on MOSSMAN2 69.000 (533820) 69 kV Bus a. Apply fault at the MOSSMAN2 69.000 (533820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSSMAN2 (533820) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0301 | 3 Phase fault on MASCOT 2 69.000 (533814) 69 kV Bus a. Apply fault at the MASCOT 2 69.000 (533814) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASCOT 2 (533814) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.2. MASCOT 2 (533814) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0302 | 3 Phase fault on EASTBOR2 69.000 (533792) 69 kV Bus a. Apply fault at the EASTBOR2 69.000 (533792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTBOR2 (533792) 69.0 kV to MINNEHA2 (533817) 69.0 kV Transmission Circuit #1 b.2. EASTBOR2 (533792) 69.0 kV to 64TH 2 (533842) 69.0 kV Transmission Circuit #1 b.3. MINNEHA2 (533817) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0303 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0304 | 3 Phase fault on ARCOTAP2 69.000 (533620) 69 kV Bus a. Apply fault at the ARCOTAP2 69.000 (533620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO 2 (533619) 69.0 kV to ARCOTAP2 (533620) 69.0 kV Transmission Circuit #1 b.2. ARCOTAP2 (533620) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.3. ARCOTAP2 (533620) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.4. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.5. COALCRK2 (533633) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.6. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0305 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0306 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to RA5HIPR2 (533706) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0307 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0308 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0309 | 3 Phase fault on ORCHARD2 69.000 (533643) 69 kV Bus a. Apply fault at the ORCHARD2 69.000 (533643) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.2. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.3. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0310 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0311 | 3 Phase fault on BELL 2 69.000 (533783) 69 kV Bus a. Apply fault at the BELL 2 69.000 (533783) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV to SC9ANSN2 (533866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0312 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 b.2. SC3MILL2 (533552) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 b.3. SC3MILL2 (533552) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 b.4. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0313 | 3 Phase fault on PECK 2 69.000 (533830) 69 kV Bus a. Apply fault at the PECK 2 69.000 (533830) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 b.2. GILL W 2 (533796) 69.0 kV to HAYSVJS2 (533802) 69.0 kV Transmission Circuit #1 b.3. HAYSVJS2 (533802) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0314 | 3 Phase fault on HYDRJS2 69.000 (533810) 69 kV Bus a. Apply fault at the HYDRJS2 69.000 (533810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALN 2 (533790) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 b.2. HYDRA N2 (533807) 69.0 kV to HYDRJS2 (533810) 69.0 kV Transmission Circuit #1 b.3. HYDRJS2 (533810) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 b.4. HYDRJS2 (533810) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0315 | 3 Phase fault on SHERIDN2 69.000 (533841) 69 kV Bus a. Apply fault at the SHERIDN2 69.000 (533841) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0316 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV to RIPLEYE2 (533859) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0317 | 3 Phase fault on BU5FURL2 69.000 (533861) 69 kV Bus a. Apply fault at the BU5FURL2 69.000 (533861) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THUNBRD2 (533603) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 b.2. CHISHLM2 (533786) 69.0 kV to GRANT 2 (533799) 69.0 kV Transmission Circuit #1 b.3. GRANT 2 (533799) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0318 | 3 Phase fault on WESTLNK2 69.000 (533854) 69 kV Bus a. Apply fault at the WESTLNK2 69.000 (533854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.3. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0319 | 3 Phase fault on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0320 | 3 Phase fault on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.2. SUNSET-2 (533844) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0321 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC7CRES2 (533555) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0322 | 3 Phase fault on WILLJCT2 69.000 (533713) 69 kV Bus a. Apply fault at the WILLJCT2 69.000 (533713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 b.2. WILLJCT2 (533713) 69.0 kV to ELKJSS 2 (533718) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0323 | 3 Phase fault on ELPASO 2 69.000 (533793) 69 kV Bus a. Apply fault at the ELPASO 2 69.000 (533793) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 2 (533793) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 b.2. ELPASO 2 (533793) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0324 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0325 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0326 | 3 Phase fault on WATER1 2 69.000 (533855) 69 kV Bus a. Apply fault at the WATER1 2 69.000 (533855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0327 | 3 Phase fault on WATER2 2 69.000 (533856) 69 kV Bus a. Apply fault at the WATER2 2 69.000 (533856) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.2. PLAZA E2 (533829) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0328 | 3 Phase fault on RIPLEYW2 69.000 (533832) 69 kV Bus a. Apply fault at the RIPLEYW2 69.000 (533832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.2. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.3. 21ST 2 (533846) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0329 | 3 Phase fault on INDEPEN2 69.000 (533694) 69 kV Bus a. Apply fault at the INDEPEN2 69.000 (533694) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDEPEN2 (533694) 69.0 kV to MONTGOM2 (533698) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0330 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0331 | 3 Phase fault on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0332 | 3 Phase fault on HYDRJN2 69.000 (533808) 69 kV Bus a. Apply fault at the HYDRJN2 69.000 (533808) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HYDRJN2 (533808) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.2. HYDRJN2 (533808) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0333 | 3 Phase fault on SENECA 2 69.000 (533839) 69 kV Bus a. Apply fault at the SENECA 2 69.000 (533839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.2. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.3. OSAGE 2 (533827) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0334 | 3 Phase fault on MEAD S 2 69.000 (533815) 69 kV Bus a. Apply fault at the MEAD S 2 69.000 (533815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0335 | 3 Phase fault on HAYSVJN2 69.000 (533804) 69 kV Bus a. Apply fault at the HAYSVJN2 69.000 (533804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 b.2. HAYSVJN2 (533804) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0336 | 3 Phase fault on LIN 2 69.000 (533812) 69 kV Bus a. Apply fault at the LIN 2 69.000 (533812) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.2. LIN 2 (533812) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 b.3. SUNSET-2 (533844) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 b.4. SG1CHEN2 (533871) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0337 | 3 Phase fault on MAHANNA2 69.000 (533738) 69 kV Bus a. Apply fault at the MAHANNA2 69.000 (533738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAHANNA2 (533738) 69.0 kV to ADAMS 2 (533746) 69.0 kV Transmission Circuit #1 b.2. MAHANNA2 (533738) 69.0 kV to GRANT J2 (533800) 69.0 kV Transmission Circuit #1 b.3. NEWTON 2 (533745) 69.0 kV to ADAMS 2 (533746) 69.0 kV Transmission Circuit #1 b.4. GRANT J2 (533800) 69.0 kV to RIPLEYW2 (533832) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0338 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0339 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0340 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0341 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0342 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0343 | 3 Phase fault on ASHGRJ22 69.000 (533660) 69 kV Bus a. Apply fault at the ASHGRJ22 69.000 (533660) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.2. ASHGRV22 (533658) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.3. ASHGRJ12 (533659) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #z1 b.4. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0344 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 b.3. EMANHAT6 (532861) 230.0 kV to EMANHAT3 (533326) 115.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0345 | 3 Phase fault on 64TH 4 138.00 (533066) 138 kV Bus a. Apply fault at the 64TH 4 138.00 (533066) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRY 4 (533048) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 b.3. 64TH 4 (533066) 138.0 kV to 64TH 2 (533842) 69.0 kV to 64TH 1 (533113) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0346 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0347 | 3 Phase fault on CANAL 4 138.00 (533033) 138 kV Bus a. Apply fault at the CANAL 4 138.00 (533033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. CANAL 4 (533033) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #1 b.3. CANAL 4 (533033) 138.0 kV to CANALS 2 (533784) 69.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0348 | 3 Phase fault on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0349 | 3 Phase fault on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.3. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.4. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0350 | 3 Phase fault on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0351 | 3 Phase fault on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0352 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.4. MONTGOM1 (533091) 13.2 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0353 | 3 Phase fault on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0354 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0355 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0356 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAUGHN 3 (533308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0357 | 3 Phase fault on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0358 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0359 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0360 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0361 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0362 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0363 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0364 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0365 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0366 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0367 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0368 | 3 Phase fault on BELL 2 69.000 (533783) 69 kV Bus a. Apply fault at the BELL 2 69.000 (533783) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0369 | 3 Phase fault on CANALN 2 69.000 (533790) 69 kV Bus a. Apply fault at the CANALN 2 69.000 (533790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALN 2 (533790) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0370 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0371 | 3 Phase fault on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0372 | 3 Phase fault on MACARTH2 69.000 (533813) 69 kV Bus a. Apply fault at the MACARTH2 69.000 (533813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACARTH2 (533813) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0373 | 3 Phase fault on MONTGOM2 69.000 (533698) 69 kV Bus a. Apply fault at the MONTGOM2 69.000 (533698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0374 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0375 | 3 Phase fault on PARSONS2 69.000 (533704) 69 kV Bus a. Apply fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0376 | 3 Phase fault on TIOGA 2 69.000 (533646) 69 kV Bus a. Apply fault at the TIOGA 2 69.000 (533646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0377 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0378 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0379 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0380 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0381 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0382 | 3 Phase fault on CHELSA4 138.00 (510410) 138 kV Bus a. Apply fault at the CHELSA4 138.00 (510410) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHELSA4 (510410) 138.0 kV to G22-234-TAP (771660) 138.0 kV Transmission Circuit #1 b.2. ALWUETP4 (510429) 138.0 kV to G22-234-TAP (771660) 138.0 kV Transmission Circuit #1 b.3. N.E.S.-4 (510396) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.4. CHELSA4 (510410) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.5. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0383 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0384 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 (510418) 69.0 kV to VINTAJC4 (510417) 138.0 kV to VINJT1-1 (510367) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0385 | 3 Phase fault on TERRACE5 161.00 (542991) 161 kV Bus a. Apply fault at the TERRACE5 161.00 (542991) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0386 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0387 | 3 Phase fault on BARBER 5 161.00 (546651) 161 kV Bus a. Apply fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0388 | 3 Phase fault on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0389 | 3 Phase fault on GIBBS 5 161.00 (546658) 161 kV Bus a. Apply fault at the GIBBS 5 161.00 (546658) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0390 | 3 Phase fault on PIPER 5 161.00 (546668) 161 kV Bus a. Apply fault at the PIPER 5 161.00 (546668) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0391 | 3 Phase fault on KAW 2 69.000 (546678) 69 kV Bus a. Apply fault at the KAW 2 69.000 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to BARBER 2 (546691) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0392 | 3 Phase fault on BARBER 5 161.00 (546651) 161 kV Bus a. Apply fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0393 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0394 | 3 Phase fault on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0395 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0396 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0397 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0398 | 3 Phase fault on 5ELMCRK 161.00 (300993) 161 kV Bus a. Apply fault at the 5ELMCRK 161.00 (300993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit #1 b.2. 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0399 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0400 | 3 Phase fault on NWMAID5 161.00 (512757) 161 kV Bus a. Apply fault at the NWMAID5 161.00 (512757) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0401 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0402 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0403 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0404 | 3 Phase fault on KANSATP5 161.00 (512714) 161 kV Bus a. Apply fault at the KANSATP5 161.00 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 412SUB 5 (512637) 161.0 kV to KANSATP5 (512714) 161.0 kV Transmission Circuit #1 b.2. KANSATP5 (512714) 161.0 kV to KANSAS 5 (512716) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0405 | 3 Phase fault on PENSA 5 161.00 (512654) 161 kV Bus a. Apply fault at the PENSA 5 161.00 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0406 | 3 Phase fault on LOCSTGVKM 5 161.00 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 161.00 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0407 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0408 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0409 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0410 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0411 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0412 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0413 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0414 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0415 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0416 | 3 Phase fault on 2NEWPORT 69.000 (301467) 69 kV Bus a. Apply fault at the 2NEWPORT 69.000 (301467) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MONKEY (301465) 69.0 kV to 2NEWPORT (301467) 69.0 kV Transmission Circuit #1 b.2. 2NEWPORT (301467) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0417 | 3 Phase fault on SAILBOA2 69.000 (510409) 69 kV Bus a. Apply fault at the SAILBOA2 69.000 (510409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAILBOA2 (510409) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0418 | 3 Phase fault on AMERCAST S2 69.000 (512681) 69 kV Bus a. Apply fault at the AMERCAST S2 69.000 (512681) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to AMERCAST S2 (512681) 69.0 kV Transmission Circuit #1 b.2. CPPTAP 2 (512661) 69.0 kV to AMERCAST S2 (512681) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0419 | 3 Phase fault on REDDEN 2 69.000 (512698) 69 kV Bus a. Apply fault at the REDDEN 2 69.000 (512698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to REDDEN 2 (512698) 69.0 kV Transmission Circuit #1 b.2. AMERCAST N2 (512683) 69.0 kV to CASTING TAP2 (512685) 69.0 kV Transmission Circuit #1 b.3. CASTING TAP2 (512685) 69.0 kV to REDDEN 2 (512698) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0420 | 3 Phase fault on CLEORTP2 69.000 (512692) 69 kV Bus a. Apply fault at the CLEORTP2 69.000 (512692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEORA (301460) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 b.2. PENSA 2 (512628) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 b.3. AFTON 2 (512633) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0421 | 3 Phase fault on ESH TP 2 69.000 (512680) 69 kV Bus a. Apply fault at the ESH TP 2 69.000 (512680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2J6 (300829) 69.0 kV to AFTP TP2 (512620) 69.0 kV Transmission Circuit #1 b.2. 2J6 (300829) 69.0 kV to VINEOTP2 (512673) 69.0 kV Transmission Circuit #1 b.3. 2VINITAHQ (300983) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.4. 2ESHOSP (301468) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.5. 2VIN NEO (301478) 69.0 kV to VINEOTP2 (512673) 69.0 kV Transmission Circuit #1 b.6. VINITA-2 (510404) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.7. AFTONTP2 (510415) 69.0 kV to A-CONT 2 (510427) 69.0 kV Transmission Circuit #1 b.8. AFTONTP2 (510415) 69.0 kV to AFTN-EX2 (510428) 69.0 kV Transmission Circuit #1 b.9. AFTONTP2 (510415) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.10. AFTP TP2 (512620) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.11. AFTON 2 (512633) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.12. VINEOTP2 (512673) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0422 | 3 Phase fault on FAIRTAP2 69.000 (512708) 69 kV Bus a. Apply fault at the FAIRTAP2 69.000 (512708) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to FAIRNEO2 (512691) 69.0 kV Transmission Circuit #1 b.2. AFTON 2 (512633) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 b.3. FAIRNEO2 (512691) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 b.4. FAIRTAP2 (512708) 69.0 kV to FRL363 2 (547583) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0423 | 3 Phase fault on MIAMI 2 69.000 (512630) 69 kV Bus a. Apply fault at the MIAMI 2 69.000 (512630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI1 2 (513020) 69.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI3 2 (513024) 69.0 kV Transmission Circuit #1 b.3. MIAMI1 2 (513020) 69.0 kV to MIAMI4 2 (513022) 69.0 kV Transmission Circuit #1 b.4. MIAMI4 2 (513022) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 b.5. MIAMI3 2 (513024) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0424 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0425 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0426 | 3 Phase fault on 2WLKRTP 69.000 (300760) 69 kV Bus a. Apply fault at the 2WLKRTP 69.000 (300760) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSHO (300750) 69.0 kV to 2WLKRTP (300760) 69.0 kV Transmission Circuit #1 b.2. 2WLKRTP (300760) 69.0 kV to 2WLKRVL (300761) 69.0 kV Transmission Circuit #1 b.3. 2WLKRTP (300760) 69.0 kV to 2SENECA (300830) 69.0 kV Transmission Circuit #1 b.4. 2SENECA (300830) 69.0 kV to 2MIAETP (300852) 69.0 kV Transmission Circuit #1 b.5. 2MIAETP (300852) 69.0 kV to MIAMI 2 (512630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0427 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0428 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0429 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0430 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0431 | 3 Phase fault on TONECE7 345.00 (512750) 345 kV Bus a. Apply fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0432 | 3 Phase fault on KERR BRK1 5 161.00 (512770) 161 kV Bus a. Apply fault at the KERR BRK1 5 161.00 (512770) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK1 5 (512770) 161.0 kV to KERR GR3 (512634) 115.0 kV to KERR1 1 (512846) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0433 | 3 Phase fault on KERR BRK4 5 161.00 (512771) 161 kV Bus a. Apply fault at the KERR BRK4 5 161.00 (512771) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK4 5 (512771) 161.0 kV to KERR GR3 (512634) 115.0 kV to KERR2 1 (512847) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0434 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0435 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0436 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0437 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0438 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0439 | 3 Phase fault on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0440 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0441 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0442 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0443 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0444 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. HOC404A1 (547715) 12.5 kV to HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0445 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0446 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0447 | 3 Phase fault on 5MCBAIN T 161.00 (345071) 161 kV Bus a. Apply fault at the 5MCBAIN T 161.00 (345071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0448 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0449 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0450 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0451 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0452 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0453 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0454 | 3 Phase fault on 5APCH TP 161.00 (344026) 161 kV Bus a. Apply fault at the 5APCH TP 161.00 (344026) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0455 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MPLTAP (300036) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 b.3. 5MPLTAP (300036) 161.0 kV to 5LATHROP (344923) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0456 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0457 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0458 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0459 | 3 Phase fault on 5LOYMART 1 161.00 (344040) 161 kV Bus a. Apply fault at the 5LOYMART 1 161.00 (344040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOYMART 1 (344040) 161.0 kV to 5LOYMART 2 (344041) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0460 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0461 | 3 Phase fault on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GUTHRIE 1 (344677) 161.0 kV to 5GUTHRIE 2 (344678) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0462 | 3 Phase fault on 5JC ZION 161.00 (344814) 161 kV Bus a. Apply fault at the 5JC ZION 161.00 (344814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JC ZION (344814) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #z b.2. 2JC ZION (346089) 69.0 kV to 5JC ZION (344814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0463 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0464 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0465 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0466 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0467 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to VSC2_3 (992003) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0468 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0469 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0470 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BOONE (300061) 161.0 kV to 5MCBAINB1 (300501) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0471 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BOONE (300061) 161.0 kV to 5MLRSBGB1 (300519) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0472 | 3 Phase fault on 5CALIF 161.00 (300063) 161 kV Bus a. Apply fault at the 5CALIF 161.00 (300063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF (300063) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0473 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0474 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0475 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0476 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0477 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0478 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0479 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0480 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0481 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0482 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0483 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0484 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0485 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0486 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0487 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0488 | 3 Phase fault on 5OSBORN 161.00 (300107) 161 kV Bus a. Apply fault at the 5OSBORN 161.00 (300107) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSBORN (300107) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0489 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0490 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0491 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0492 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0493 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2MOCITY (300304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0494 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0495 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0496 | 3 Phase fault on 2ASHLND 69.000 (300492) 69 kV Bus a. Apply fault at the 2ASHLND 69.000 (300492) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHLND (300492) 69.0 kV to 2BOONE (300493) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0497 | 3 Phase fault on 2BOONE 69.000 (300493) 69 kV Bus a. Apply fault at the 2BOONE 69.000 (300493) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOONE (300493) 69.0 kV to 2DEERPK (300497) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0498 | 3 Phase fault on 2BOONE 69.000 (300493) 69 kV Bus a. Apply fault at the 2BOONE 69.000 (300493) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOONE (300493) 69.0 kV to 2GRINDSTN (343006) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0499 | 3 Phase fault on 5MCBAINB1 161.00 (300501) 161 kV Bus a. Apply fault at the 5MCBAINB1 161.00 (300501) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB1 (300501) 161.0 kV to 5MCBAINB2 (301489) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0500 | 3 Phase fault on 5MLRSBGB1 161.00 (300519) 161 kV Bus a. Apply fault at the 5MLRSBGB1 161.00 (300519) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MLRSBGB1 (300519) 161.0 kV to 5MLRSBGB2 (301498) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0501 | 3 Phase fault on 2DRESDN 69.000 (300528) 69 kV Bus a. Apply fault at the 2DRESDN 69.000 (300528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DRESDN (300528) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0502 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0503 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0504 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0505 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0506 | 3 Phase fault on 2HUGHSV 69.000 (300533) 69 kV Bus a. Apply fault at the 2HUGHSV 69.000 (300533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HUGHSV (300533) 69.0 kV to 2SWSPJC (300543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0507 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0508 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0509 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0510 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GI91 (99915). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0511 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0512 | 3 Phase fault on 2CALIF 69.000 (300550) 69 kV Bus a. Apply fault at the 2CALIF 69.000 (300550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 2FORTNA (300554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0513 | 3 Phase fault on 2CALIF 69.000 (300550) 69 kV Bus a. Apply fault at the 2CALIF 69.000 (300550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 2PRARIE (300561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0514 | 3 Phase fault on 2CALIF 69.000 (300550) 69 kV Bus a. Apply fault at the 2CALIF 69.000 (300550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 2ST_MARTINS (301442) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0515 | 3 Phase fault on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FORTNA (300554) 69.0 kV to 2NEEDY (300559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0516 | 3 Phase fault on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FORTNA (300554) 69.0 kV to 2SYRACS (300564) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0517 | 3 Phase fault on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FORTNA (300554) 69.0 kV to 2VERSAL (300565) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0518 | 3 Phase fault on 5GRAVOIB1 161.00 (300555) 161 kV Bus a. Apply fault at the 5GRAVOIB1 161.00 (300555) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRAVOIB1 (300555) 161.0 kV to 5GRAVOIB2 (300574) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0519 | 3 Phase fault on 2HIGHPT 69.000 (300556) 69 kV Bus a. Apply fault at the 2HIGHPT 69.000 (300556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HIGHPT (300556) 69.0 kV to 2BARNET (300618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0520 | 3 Phase fault on 2PILOTG 69.000 (300560) 69 kV Bus a. Apply fault at the 2PILOTG 69.000 (300560) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PILOTG (300560) 69.0 kV to 2PRARIE (300561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0521 | 3 Phase fault on 2VERSAL 69.000 (300565) 69 kV Bus a. Apply fault at the 2VERSAL 69.000 (300565) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERSAL (300565) 69.0 kV to 2BARNET (300618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0522 | 3 Phase fault on 2BARNET 69.000 (300618) 69 kV Bus a. Apply fault at the 2BARNET 69.000 (300618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BARNET (300618) 69.0 kV to 2MTPLSTC (300633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0523 | 3 Phase fault on 2SCRUGG 69.000 (300637) 69 kV Bus a. Apply fault at the 2SCRUGG 69.000 (300637) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SCRUGG (300637) 69.0 kV to 2ST_MARTINS (301442) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0524 | 3 Phase fault on 2BLLMYTP 69.000 (300647) 69 kV Bus a. Apply fault at the 2BLLMYTP 69.000 (300647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLLMYTP (300647) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0525 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0526 | 3 Phase fault on 2LAMR 69.000 (300651) 69 kV Bus a. Apply fault at the 2LAMR 69.000 (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0527 | 3 Phase fault on 2LAMR 69.000 (300651) 69 kV Bus a. Apply fault at the 2LAMR 69.000 (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2LAMARPT (300685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0528 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0529 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0530 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0531 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0532 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0533 | 3 Phase fault on 2MIAETP 69.000 (300852) 69 kV Bus a. Apply fault at the 2MIAETP 69.000 (300852) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MIAETP (300852) 69.0 kV to 2MIAENEO (301461) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0534 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0535 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0536 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0537 | 3 Phase fault on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PLATCTY (301552) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0538 | 3 Phase fault on 5REBEL 161.00 (343007) 161 kV Bus a. Apply fault at the 5REBEL 161.00 (343007) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REBEL (343007) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0539 | 3 Phase fault on 2APCH FLT 69.000 (344027) 69 kV Bus a. Apply fault at the 2APCH FLT 69.000 (344027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2APCH FLT (344027) 69.0 kV to 2JC RAINB (346082) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0540 | 3 Phase fault on 2APCH FLT 69.000 (344027) 69 kV Bus a. Apply fault at the 2APCH FLT 69.000 (344027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2APCH FLT (344027) 69.0 kV to 2JC SCRGG (346084) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0541 | 3 Phase fault on 5APCH FLT 161.00 (344028) 161 kV Bus a. Apply fault at the 5APCH FLT 161.00 (344028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0542 | 3 Phase fault on 5JC ZION TP 161.00 (344815) 161 kV Bus a. Apply fault at the 5JC ZION TP 161.00 (344815) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JC ZION TP (344815) 161.0 kV to 5MARIOSA (345027) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0543 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0544 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0545 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2MACON_AM (346096) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0546 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2DUPONT (346169) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0547 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2ROTH TAP (346170) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0548 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2SPRK TAP (346171) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0549 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0550 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0551 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to KERR BRK1 5 (512770) 161.0 kV Transmission Circuit #z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0552 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to KERR BRK4 5 (512771) 161.0 kV Transmission Circuit #z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0553 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0554 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to G21-047-TAP (765721) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0555 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0556 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0557 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0558 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0559 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0560 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0561 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0562 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0563 | 3 Phase fault on N HAYS3 115.00 (530581) 115 kV Bus a. Apply fault at the N HAYS3 115.00 (530581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0564 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0565 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284) and G22-075 (768484). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0566 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0567 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0568 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0569 | 3 Phase fault on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0570 | 3 Phase fault on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0571 | 3 Phase fault on VINETAP3 115.00 (530693) 115 kV Bus a. Apply fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0572 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0573 | 3 Phase fault on GEM_SW 3 115.00 (530713) 115 kV Bus a. Apply fault at the GEM_SW 3 115.00 (530713) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEM_SW 3 (530713) 115.0 kV to COLBY_PUMP3 (530716) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0574 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0575 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284) and G22-075 (768484). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0576 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284) and G22-075 (768484). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0577 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284) and G22-075 (768484). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0578 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284) and G22-075 (768484). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0579 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0580 | 3 Phase fault on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0581 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0582 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0583 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0584 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0585 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0586 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0587 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0588 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0589 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0590 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0591 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0592 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0593 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0594 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0595 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0596 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0597 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to TCBURNS4 (532994) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0598 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0599 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0600 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0601 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0602 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0603 | 3 Phase fault on CENTENN4 138.00 (533034) 138 kV Bus a. Apply fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0604 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0605 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0606 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0607 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0608 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0609 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0610 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0611 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0612 | 3 Phase fault on WACO S 4 138.00 (533071) 138 kV Bus a. Apply fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0613 | 3 Phase fault on WACO 4 138.00 (533072) 138 kV Bus a. Apply fault at the WACO 4 138.00 (533072) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0614 | 3 Phase fault on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0615 | 3 Phase fault on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0616 | 3 Phase fault on LANG 3 115.00 (533304) 115 kV Bus a. Apply fault at the LANG 3 115.00 (533304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0617 | 3 Phase fault on READING3 115.00 (533306) 115 kV Bus a. Apply fault at the READING3 115.00 (533306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. READING3 (533306) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0618 | 3 Phase fault on FLORENC3 115.00 (533366) 115 kV Bus a. Apply fault at the FLORENC3 115.00 (533366) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0619 | 3 Phase fault on SPRGCRK3 115.00 (533380) 115 kV Bus a. Apply fault at the SPRGCRK3 115.00 (533380) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0620 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0621 | 3 Phase fault on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0622 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0623 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0624 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0625 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to BURLIND2 (533625) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0626 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to CC1BURL2 (533628) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0627 | 3 Phase fault on ALTAMNT2 69.000 (533671) 69 kV Bus a. Apply fault at the ALTAMNT2 69.000 (533671) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0628 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODESH2 (533699) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0629 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0630 | 3 Phase fault on YELLOWJ2 69.000 (533692) 69 kV Bus a. Apply fault at the YELLOWJ2 69.000 (533692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YELLOWJ2 (533692) 69.0 kV to NEW ALB2 (533701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0631 | 3 Phase fault on LABETTE2 69.000 (533695) 69 kV Bus a. Apply fault at the LABETTE2 69.000 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0632 | 3 Phase fault on NEODJCT2 69.000 (533700) 69 kV Bus a. Apply fault at the NEODJCT2 69.000 (533700) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEODJCT2 (533700) 69.0 kV to RA6BROO2 (533707) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0633 | 3 Phase fault on NEW ALB2 69.000 (533701) 69 kV Bus a. Apply fault at the NEW ALB2 69.000 (533701) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEW ALB2 (533701) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0634 | 3 Phase fault on ORDNCE 2 69.000 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 69.000 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0635 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0636 | 3 Phase fault on CANALS 2 69.000 (533784) 69 kV Bus a. Apply fault at the CANALS 2 69.000 (533784) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0637 | 3 Phase fault on CANALS 2 69.000 (533784) 69 kV Bus a. Apply fault at the CANALS 2 69.000 (533784) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0638 | 3 Phase fault on CHENEY 2 69.000 (533785) 69 kV Bus a. Apply fault at the CHENEY 2 69.000 (533785) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHENEY 2 (533785) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0639 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0640 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCAN 2 (533850) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0641 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0642 | 3 Phase fault on GLENDAL2 69.000 (533797) 69 kV Bus a. Apply fault at the GLENDAL2 69.000 (533797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL2 (533797) 69.0 kV to OLIVER 2 (533826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0643 | 3 Phase fault on GLENDAL2 69.000 (533797) 69 kV Bus a. Apply fault at the GLENDAL2 69.000 (533797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL2 (533797) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0644 | 3 Phase fault on HAYSV 2 69.000 (533803) 69 kV Bus a. Apply fault at the HAYSV 2 69.000 (533803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYSV 2 (533803) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0645 | 3 Phase fault on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0646 | 3 Phase fault on HOOVERS2 69.000 (533806) 69 kV Bus a. Apply fault at the HOOVERS2 69.000 (533806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0647 | 3 Phase fault on LIN 2 69.000 (533812) 69 kV Bus a. Apply fault at the LIN 2 69.000 (533812) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0648 | 3 Phase fault on OAKLAWN2 69.000 (533824) 69 kV Bus a. Apply fault at the OAKLAWN2 69.000 (533824) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAWN2 (533824) 69.0 kV to OLIVER 2 (533826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0649 | 3 Phase fault on PLAZA E2 69.000 (533829) 69 kV Bus a. Apply fault at the PLAZA E2 69.000 (533829) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0650 | 3 Phase fault on RIPLEYW2 69.000 (533832) 69 kV Bus a. Apply fault at the RIPLEYW2 69.000 (533832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIPLEYW2 (533832) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0651 | 3 Phase fault on GALE TP2 69.000 (533845) 69 kV Bus a. Apply fault at the GALE TP2 69.000 (533845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALE TP2 (533845) 69.0 kV to SG4ANDL2 (533872) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0652 | 3 Phase fault on GALE TP2 69.000 (533845) 69 kV Bus a. Apply fault at the GALE TP2 69.000 (533845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALE TP2 (533845) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0653 | 3 Phase fault on PLAZA M2 69.000 (533857) 69 kV Bus a. Apply fault at the PLAZA M2 69.000 (533857) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0654 | 3 Phase fault on GODDTAP2 69.000 (533879) 69 kV Bus a. Apply fault at the GODDTAP2 69.000 (533879) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GODDTAP2 (533879) 69.0 kV to GODDARD2 (533880) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0655 | 3 Phase fault on RAGO 4 138.00 (539000) 138 kV Bus a. Apply fault at the RAGO 4 138.00 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0656 | 3 Phase fault on NW-DGTP3 115.00 (539628) 115 kV Bus a. Apply fault at the NW-DGTP3 115.00 (539628) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DGTP3 (539628) 115.0 kV to W-DODGE3 (539699) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0657 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0658 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0659 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0660 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0661 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0662 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0663 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0664 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0665 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0666 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0667 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0668 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284) and G22-075 (768484). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0669 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0670 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0671 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0672 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0673 | 3 Phase fault on WBURGE_CAP5 161.00 (541148) 161 kV Bus a. Apply fault at the WBURGE_CAP5 161.00 (541148) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE_CAP5 (541148) 161.0 kV to WBURGE 5 (541228) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0674 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0675 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0676 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0677 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1 (541546) and OUTLAW_G21 (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0678 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1 (541546) and OUTLAW_G21 (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0679 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0680 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0681 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0682 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0683 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0684 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0685 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1 (541546) and OUTLAW_G21 (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0686 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0687 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0688 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0689 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0690 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to POPE (541349) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0691 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0692 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0693 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0694 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0695 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0696 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0697 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0698 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0699 | 3 Phase fault on KCI 5 161.00 (541212) 161 kV Bus a. Apply fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCI 5 (541212) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0700 | 3 Phase fault on KCI 5 161.00 (541212) 161 kV Bus a. Apply fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCI 5 (541212) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0701 | 3 Phase fault on FRLVW 5 161.00 (541213) 161 kV Bus a. Apply fault at the FRLVW 5 161.00 (541213) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRLVW 5 (541213) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0702 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0703 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0704 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0705 | 3 Phase fault on RAYTOWN5 161.00 (541219) 161 kV Bus a. Apply fault at the RAYTOWN5 161.00 (541219) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0706 | 3 Phase fault on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0707 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0708 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0709 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0710 | 3 Phase fault on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 5 (541229) 161.0 kV to LEX161 5 (541232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0711 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0712 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0713 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0714 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0715 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0716 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0717 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0718 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0719 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0720 | 3 Phase fault on EAST 5 161.00 (541254) 161 kV Bus a. Apply fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0721 | 3 Phase fault on IND PRK5 161.00 (541256) 161 kV Bus a. Apply fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0722 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0723 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0724 | 3 Phase fault on KNOSTER2 69.000 (541270) 69 kV Bus a. Apply fault at the KNOSTER2 69.000 (541270) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOSTER2 (541270) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0725 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to KELHYS 2 (541273) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0726 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0727 | 3 Phase fault on SEDS 2 69.000 (541272) 69 kV Bus a. Apply fault at the SEDS 2 69.000 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0728 | 3 Phase fault on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0729 | 3 Phase fault on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0730 | 3 Phase fault on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0731 | 3 Phase fault on COLECMP2 69.000 (541276) 69 kV Bus a. Apply fault at the COLECMP2 69.000 (541276) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLECMP2 (541276) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0732 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0733 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0734 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0735 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBW5 (541336) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0736 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0737 | 3 Phase fault on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161.0 kV to WAFBE5 (541338) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0738 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0739 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0740 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0741 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0742 | 3 Phase fault on IATAN5 161.00 (541350) 161 kV Bus a. Apply fault at the IATAN5 161.00 (541350) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0743 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0744 | 3 Phase fault on MONSERTP 69.000 (541524) 69 kV Bus a. Apply fault at the MONSERTP 69.000 (541524) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONSERTP (541524) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0745 | 3 Phase fault on KNOSTERTP 69.000 (541534) 69 kV Bus a. Apply fault at the KNOSTERTP 69.000 (541534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOSTERTP (541534) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0746 | 3 Phase fault on LAMONTETP 69.000 (541535) 69 kV Bus a. Apply fault at the LAMONTETP 69.000 (541535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMONTETP (541535) 69.0 kV to LAMONTE (541536) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0747 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0748 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0749 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0750 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY_CAP 5 (542944) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0751 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0752 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0753 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0754 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0755 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0756 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0757 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0758 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0759 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1 (541546) and OUTLAW_G21 (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0760 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0761 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0762 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0763 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0764 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0765 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0766 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0767 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0768 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0769 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0770 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0771 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0772 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0773 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0774 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0775 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0776 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0777 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0778 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0779 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 4.75 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 4.75 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0780 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0781 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0782 | 3 Phase fault on TROOST 5 161.00 (542986) 161 kV Bus a. Apply fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0783 | 3 Phase fault on TROOST 5 161.00 (542986) 161 kV Bus a. Apply fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0784 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0785 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0786 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0787 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0788 | 3 Phase fault on CROSTWN5 161.00 (542990) 161 kV Bus a. Apply fault at the CROSTWN5 161.00 (542990) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSTWN5 (542990) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0789 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0790 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0791 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0792 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0793 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to ROEPARK5 (543040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0794 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0795 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0796 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0797 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0798 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0799 | 3 Phase fault on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0800 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0801 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0802 | 3 Phase fault on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0803 | 3 Phase fault on CLAYCM15 161.00 (543022) 161 kV Bus a. Apply fault at the CLAYCM15 161.00 (543022) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLAYCM15 (543022) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0804 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0805 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0806 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0807 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0808 | 3 Phase fault on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to ROEPARK5 (543040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0809 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0810 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0811 | 3 Phase fault on OXFORD 5 161.00 (543046) 161 kV Bus a. Apply fault at the OXFORD 5 161.00 (543046) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 5 (543046) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0812 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0813 | 3 Phase fault on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0814 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0815 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0816 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0817 | 3 Phase fault on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSTVAL5 (543077) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0818 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0819 | 3 Phase fault on SUGRCRK_N2 69.000 (543089) 69 kV Bus a. Apply fault at the SUGRCRK_N2 69.000 (543089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_N2 (543089) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0820 | 3 Phase fault on DUNCNRD2 69.000 (543091) 69 kV Bus a. Apply fault at the DUNCNRD2 69.000 (543091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0821 | 3 Phase fault on LIBRTYS2 69.000 (543095) 69 kV Bus a. Apply fault at the LIBRTYS2 69.000 (543095) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0822 | 3 Phase fault on SUGRCK_TP_W269.000 (543164) 69 kV Bus a. Apply fault at the SUGRCK_TP_W269.000 (543164) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0823 | 3 Phase fault on KAW 5 161.00 (546214) 161 kV Bus a. Apply fault at the KAW 5 161.00 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0824 | 3 Phase fault on KAW 5 161.00 (546214) 161 kV Bus a. Apply fault at the KAW 5 161.00 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0825 | 3 Phase fault on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to MILLST 5 (546224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0826 | 3 Phase fault on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0827 | 3 Phase fault on SCAM66 2 69.000 (547409) 69 kV Bus a. Apply fault at the SCAM66 2 69.000 (547409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCAM66 2 (547409) 69.0 kV to SCM66T 2 (547455) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0828 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0829 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to SEK225 2 (547413) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0830 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to SMN425 2 (547414) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0831 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to SHR444 2 (547415) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0832 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0833 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to CHE299 2 (547417) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0834 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to CHE300 2 (547418) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0835 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0836 | 3 Phase fault on CHE300 2 69.000 (547418) 69 kV Bus a. Apply fault at the CHE300 2 69.000 (547418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE300 2 (547418) 69.0 kV to TWN388 2 (547419) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0837 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0838 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0839 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0840 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0841 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0842 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0843 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0844 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0845 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0846 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0847 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0848 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0849 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0850 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0851 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0852 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0853 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0854 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0855 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0856 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0857 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0858 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0859 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0860 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0861 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0862 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0863 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0864 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0865 | 3 Phase fault on GAT258 2 69.000 (547551) 69 kV Bus a. Apply fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0866 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0867 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0868 | 3 Phase fault on GAL278 2 69.000 (547555) 69 kV Bus a. Apply fault at the GAL278 2 69.000 (547555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAL278 2 (547555) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0869 | 3 Phase fault on COM381T2 69.000 (547579) 69 kV Bus a. Apply fault at the COM381T2 69.000 (547579) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COM381T2 (547579) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0870 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0871 | 3 Phase fault on JOP389 2 69.000 (547592) 69 kV Bus a. Apply fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0872 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0873 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0874 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0875 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0876 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0877 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0878 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0879 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0880 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0881 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0882 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0883 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0884 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0885 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0886 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0887 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0888 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0889 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0890 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0891 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0892 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0893 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0894 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0895 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0896 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0897 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0898 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0899 | 3 Phase fault on MALONEY7 115.00 (640265) 115 kV Bus a. Apply fault at the MALONEY7 115.00 (640265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0900 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0901 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0902 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0903 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0904 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0905 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0906 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0907 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0908 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0909 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0910 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0911 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | The Grand Prairie Wind Units (645065, 645066, 645067 and 645068) become unstable following the fault clearance and protection trips the units. Reducing the critical clearing time to 3.0 cycles mitigates the issue. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0912 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0913 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0914 | 3 Phase fault on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284) and frequency protection trips G19-053 (763849) and G19-055 (763872). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0915 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT11_2 (543663) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0916 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT12_2 (543664) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0917 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5KINGDMB1 (300090) 161.0 kV to 7KINGDM (300043) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0918 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0919 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF3 (301506) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0920 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0921 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BARNET (300618) 69.0 kV to 5BARNET (300057) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0922 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOONE (300493) 69.0 kV to 5BOONE (300061) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0923 | 3 Phase fault on 5CALIF 161.00 (300063) 161 kV Bus a. Apply fault at the 5CALIF 161.00 (300063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 5CALIF (300063) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0924 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLARK (300802) 69.0 kV to 5CLARK (300070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0925 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0926 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0927 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0928 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHRP (300302) 69.0 kV to 5LATHRP (300091) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0929 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0930 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0931 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0932 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0933 | 3 Phase fault on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PLATCTY (300307) 69.0 kV to 5PLATCTY (301552) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0934 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0935 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0936 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0937 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0938 | 3 Phase fault on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PERCHE (343004) 161.0 kV to 2PERCHE (343005) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0939 | 3 Phase fault on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PERCHE (343004) 161.0 kV to 2PERCHE2 (343052) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0940 | 3 Phase fault on 5GRINDSTN 161.00 (343014) 161 kV Bus a. Apply fault at the 5GRINDSTN 161.00 (343014) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GRINDSTN (343006) 69.0 kV to 5GRINDSTN (343014) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0941 | 3 Phase fault on 5APCH FLT 161.00 (344028) 161 kV Bus a. Apply fault at the 5APCH FLT 161.00 (344028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0942 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0943 | 3 Phase fault on 5LATHROP 161.00 (344923) 161 kV Bus a. Apply fault at the 5LATHROP 161.00 (344923) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHROP (346093) 69.0 kV to 5LATHROP (344923) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0944 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0945 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0946 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0947 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0948 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0949 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0950 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0951 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to CATOOSA4 (509790) 138.0 kV to CATTER1 1 (512833) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0952 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to CATOOSA4 (509790) 138.0 kV to CATTER2 1 (512834) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0953 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0954 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0955 | 3 Phase fault on PENSA 5 161.00 (512654) 161 kV Bus a. Apply fault at the PENSA 5 161.00 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to PENSA 2 (512628) 69.0 kV to PENSA 1 (512841) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0956 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0957 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0958 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0959 | 3 Phase fault on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138.0 kV to WAKITA 2 (521085) 69.0 kV to WAKITA_13.8 (520435) 13.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0960 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0961 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0962 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0963 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0964 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0965 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0966 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0967 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0968 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0969 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0970 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0971 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0972 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0973 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0974 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0975 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0976 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0977 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 2X1 (532840) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0978 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0979 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0980 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0981 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0982 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0983 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0984 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0985 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0986 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0987 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0988 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0989 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0990 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0991 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0992 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0993 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MCDOWEL3 (533335) 115.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0994 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0995 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0996 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0997 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0998 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0999 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1000 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1001 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1002 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1003 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1004 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1005 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1006 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1007 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1008 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1009 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1010 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1011 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1012 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1013 | 3 Phase fault on 17TH 4 138.00 (533064) 138 kV Bus a. Apply fault at the 17TH 4 138.00 (533064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1014 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1015 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1016 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1017 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1018 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1019 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1020 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1021 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1022 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1023 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1024 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1025 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN2 (533876) 69.0 kV to FRANKLIN5 (532938) 161.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1026 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284) and G22-075 (768484). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1027 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284) and G22-075 (768484). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1028 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1029 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1 (541546) and OUTLAW_G21 (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1030 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1031 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1032 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1033 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1034 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1035 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1036 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1037 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 2 (541269) 69.0 kV to WBURGE 5 (541228) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1038 | 3 Phase fault on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 2 (541267) 69.0 kV to ODESSA 5 (541229) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1039 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1040 | 3 Phase fault on LEX161 5 161.00 (541232) 161 kV Bus a. Apply fault at the LEX161 5 161.00 (541232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX69 2 (541264) 69.0 kV to LEX161 5 (541232) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1041 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1042 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1043 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1044 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to LBRTYST5 (541248) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1045 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1046 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1047 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1048 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1 (541546) and OUTLAW_G21 (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1049 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to ATLNTIC3 (533279) 115.0 kV to ATLNT2X1 (533916) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1050 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to ATLNTIC3 (533279) 115.0 kV to ATLNT1X1 (533915) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1051 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1052 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1 (541546) and OUTLAW_G21 (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1053 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips OUTLAW_G1 (541546) and OUTLAW_G21 (541549). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1054 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1055 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1056 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1057 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1058 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1059 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1060 | 3 Phase fault on IATAN 7 345.00 (542982) 345 kV Bus a. Apply fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1061 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1062 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1063 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1064 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1065 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1066 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1067 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1068 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1069 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1070 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1071 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1072 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1073 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1074 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1075 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG8 (640101) 69.0 kV to CAMBRIG7 (640100) 115.0 kV to CAMBRIDGET19 (643028) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1076 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 8 (640168) 69.0 kV to ENDERS 7 (640167) 115.0 kV to ENDERS T1 9 (643055) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1077 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1078 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1079 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT8 (640288) 69.0 kV to N.PLATT7 (640287) 115.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1080 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1081 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1082 | 3 Phase fault on VSC2_3 345.00 (992003) 345 kV Bus a. Apply fault at the VSC2_3 345.00 (992003) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VSC2_3 (992003) 345.0 kV to VSC2_2 (992002) 276.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1083 | 3 Phase fault on VSC2_3 345.00 (992003) 345 kV Bus a. Apply fault at the VSC2_3 345.00 (992003) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VSC2_3 (992003) 345.0 kV to VSC2_6 (992006) 276.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1084 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GI91 (99915). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1085 | 3 Phase fault on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1086 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1087 | 3 Phase fault on JOP430 2 69.000 (547608) 69 kV Bus a. Apply fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP430 2 (547608) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1088 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1089 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1090 | 3 Phase fault on SUB M 69.000 (548815) 69 kV Bus a. Apply fault at the SUB M 69.000 (548815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1091 | 3 Phase fault on SUB N 69.000 (548821) 69 kV Bus a. Apply fault at the SUB N 69.000 (548821) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1092 | 3 Phase fault on SUB C 69.000 (548825) 69 kV Bus a. Apply fault at the SUB C 69.000 (548825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB C (548825) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1093 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0001 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0002 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0003 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0004 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0005 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0006 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0007 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0008 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0009 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0010 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0011 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0013 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0014 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0015 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0016 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0017 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0018 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0019 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0020 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0021 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0022 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0023 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0024 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0025 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0026 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0027 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0028 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0029 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0030 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0031 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0032 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0033 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0035 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0036 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0037 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0038 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0039 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0040 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0041 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0042 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0043 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0044 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0045 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0046 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-121 (761841 and 761844) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0048 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G22-065 (768284). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0049 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips ROCKCK units (641514 and 541518) and OUTLAW units (541546, 541549 and 541550). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0051 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0001 | Single Phase Fault with Stuck Breaker on 5GRINDSTN 161.00 (343014) 161 kV Bus a. Apply Fault at the 5GRINDSTN 161.00 (343014) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BOONE (300061) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 b.2. 2GRINDSTN (343006) 69.0 kV to 5GRINDSTN (343014) 161.0 kV Two Winding #1 b.3. 5REBEL (343007) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0002 | Single Phase Fault with Stuck Breaker on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply Fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 b.2. 5PERCHE (343004) 161.0 kV to 2PERCHE (343005) 69.0 kV Two Winding #1 b.3. 5PERCHE (343004) 161.0 kV to 2PERCHE2 (343052) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0003 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0007 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0008 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0010 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 b.3. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0011 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0012 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0013 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0014 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0015 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0016 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-100-TAP (768980) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0017 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0018 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0019 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0020 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0021 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0022 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0023 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0024 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0025 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0026 | Single Phase Fault with Stuck Breaker on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply Fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 b.3. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 b.4. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 b.5. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0027 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-100-TAP (768980) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0028 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0029 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 b.4. SALSBRY5 (543062) 161.0 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0030 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0031 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0032 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0033 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0034 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0035 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NEAST_DG1 (543160) 4.2 kV to NE CT11 (542958) 13.8 kV Two Winding #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 b.6. NEASTN5 (543666) 161.0 kV to Load #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0036 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEAST_DG1 (543160) 4.2 kV to NE CT11 (542958) 13.8 kV Two Winding #1 b.3. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0037 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # b.6. NEASTN5 (543666) 161.0 kV to Load #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0038 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NE CT17 (542983) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT18 (542984) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0039 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NE CT17 (542983) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT18 (542984) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0040 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0041 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0042 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0043 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 b.2. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0044 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0045 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0046 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0047 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0048 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0049 | Single Phase Fault with Stuck Breaker on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply Fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT7 1 (542963) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.2. HAWCT8 1 (542964) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.3. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0050 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to Load #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0051 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NRTHST_B90_1 (543082) 13.8 kV to Load #90 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0052 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NRTHST_B34_1 (543081) 13.8 kV to Load #34 b.3. NEASTN5 (543666) 161.0 kV to Load #78 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0053 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NRTHST_B34_1 (543081) 13.8 kV to Load #34 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0054 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # b.2. NEASTN5 (543666) 161.0 kV to Load #78 b.3. NRTHST_B90_1 (543082) 13.8 kV to Load #90 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0055 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0056 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0057 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0058 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0059 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.4. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0060 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0061 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0062 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0063 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0064 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0065 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0066 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0067 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0068 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 b.2. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0069 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0070 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0071 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0072 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0073 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0074 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0075 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0076 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0077 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0078 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0079 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0080 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0081 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0082 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0083 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0084 | Single Phase Fault with Stuck Breaker on COLBY 3 115.00 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0085 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.3. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0086 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 b.2. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 b.4. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0087 | Single Phase Fault with Stuck Breaker on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply Fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 b.2. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 b.3. ENDERS 7 (640167) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #1 b.4. ENDERS 7 (640167) 115.0 kV to ENDERS 8 (640168) 69.0 kV to ENDERS T1 9 (643055) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0088 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to MCCOOK G (640017) 13.8 kV Two Winding #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.4. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.5. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 b.6. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0089 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.4. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.5. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0090 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.3. N.PLATTG (640018) 13.8 kV to N.PLATT9 (640289) 34.5 kV to N.PLATT7 (640287) 115.0 kV Three Winding #1 b.4. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 b.6. N.PLATT7 (640287) 115.0 kV to N.PLATT8 (640288) 69.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 b.7. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to N.PLATTG (640018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0091 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.3. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.4. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.5. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 b.6. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 b.7. N.PLATT7 (640287) 115.0 kV to N.PLATT8 (640288) 69.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 b.8. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to N.PLATTG (640018) 13.8 kV Three Winding #1 b.9. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to NORTHPLT T79 (643107) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0092 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 b.3. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0093 | Single Phase Fault with Stuck Breaker on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply Fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.6. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.7. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.8. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.9. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 b.10. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.11. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.12. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.13. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.14. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0094 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.4. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.7. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.8. HARPER 4 (539668) 138.0 kV to HARPER 1 (539713) 34.5 kV to HARPER-T (539913) 8.7 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0095 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0096 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0097 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0098 | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply Fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.3. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.4. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.8. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0099 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0100 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.2. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.3. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.4. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.6. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.9. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0101 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.2. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.3. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0102 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 b.4. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0103 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0104 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0105 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0106 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0107 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0108 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0109 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0110 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0111 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0112 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0113 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-065-TAP (768280) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0114 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0115 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0116 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0117 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 b.5. HOLCOMB3 (531448) 115.0 kV to Load #S1 b.6. HOLCOMB3 (531448) 115.0 kV to Load #S2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0118 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0119 | Single Phase Fault with Stuck Breaker on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply Fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. FTDODGP1 (539670) 15.0 kV to FTDODGE3 (539671) 115.0 kV Two Winding #1 b.4. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.5. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 b.6. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. FTDODGE3 (539671) 115.0 kV to FTDDGDV1 (539715) 34.5 kV to FTDODG-T (539915) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0120 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0121 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0122 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0123 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0124 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0125 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0126 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0127 | Single Phase Fault with Stuck Breaker on SPRINGH3 115.00 (533267) 115 kV Bus a. Apply Fault at the SPRINGH3 115.00 (533267) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.4. SPRINGH3 (533267) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0128 | Single Phase Fault with Stuck Breaker on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply Fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.4. SPRINGH3 (533267) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0129 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 b.4. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 2X1 (532840) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0130 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0131 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0132 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0133 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0134 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0135 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC6 1 (532743) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0136 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0137 | Single Phase Fault with Stuck Breaker on GEARY 7 345.00 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.3. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0138 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.3. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0139 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0140 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0141 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0142 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0143 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0144 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0145 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0146 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0147 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0148 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0149 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0150 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0151 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0152 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0153 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0154 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0155 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0156 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0157 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to GEN-2016-174 (588250) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0158 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0159 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0160 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0161 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0162 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0163 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0164 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0165 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0166 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0167 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0168 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0169 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. BLUMILS5 (543004) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0170 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0171 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0172 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY (548806) 69.0 kV to Load #T2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0173 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0174 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0175 | Single Phase Fault with Stuck Breaker on BLUVLY 69.000 (548806) 69 kV Bus a. Apply Fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.3. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.4. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.5. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 b.6. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 b.7. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 b.8. BLUVLY (548806) 69.0 kV to Load #T1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0176 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.3. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0177 | Single Phase Fault with Stuck Breaker on SUB N-161 161.00 (548820) 161 kV Bus a. Apply Fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0178 | Single Phase Fault with Stuck Breaker on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply Fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 b.2. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0179 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0181 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0182 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0183 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0184 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0185 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0186 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0187 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0188 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0189 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0190 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0191 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0192 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0193 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0194 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0195 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0196 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP5 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0197 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0198 | Single Phase Fault with Stuck Breaker on AFTON 5 161.00 (512632) 161 kV Bus a. Apply Fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.4. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0199 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.2. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.3. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0200 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.2. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.3. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.6. 1CHOTCT2 (300033) 16.0 kV to Load #P2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0201 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.2. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.3. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0202 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.5. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.6. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.7. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.8. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.9. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0203 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0204 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.6. 1CHOTCT4 (300020) 16.0 kV to Load #P1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0205 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.6. 1CHOTCT5 (300021) 16.0 kV to Load #P2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0206 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0207 | Single Phase Fault with Stuck Breaker on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply Fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.5. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0208 | Single Phase Fault with Stuck Breaker on 5APCH FLT 161.00 (344028) 161 kV Bus a. Apply Fault at the 5APCH FLT 161.00 (344028) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.2. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.4. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.5. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0209 | Single Phase Fault with Stuck Breaker on 5BARNET 161.00 (300057) 161 kV Bus a. Apply Fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.3. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.4. 2BARNET (300618) 69.0 kV to 5BARNET (300057) 161.0 kV Two Winding #1 b.5. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.6. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0210 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 161.00 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 161.00 (344234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5CALIF (300063) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.4. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.5. 1CALIF (346027) 34.5 kV to 5CALIF UE 2 (344234) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0211 | Single Phase Fault with Stuck Breaker on 5JC ZION 161.00 (344814) 161 kV Bus a. Apply Fault at the 5JC ZION 161.00 (344814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.2. 5MARIOSA (345027) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.3. 5JC ZION (344814) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #z b.4. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.5. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.6. 2JC ZION (346089) 69.0 kV to 5JC ZION (344814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0212 | Single Phase Fault with Stuck Breaker on 5ELDON 2 161.00 (344533) 161 kV Bus a. Apply Fault at the 5ELDON 2 161.00 (344533) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.3. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.4. 2BARNET (300618) 69.0 kV to 5BARNET (300057) 161.0 kV Two Winding #1 b.5. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.6. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.7. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.8. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 b.9. 1ELDON 2 (346045) 34.5 kV to 5ELDON 2 (344533) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0213 | Single Phase Fault with Stuck Breaker on 5ELDON 2 161.00 (344533) 161 kV Bus a. Apply Fault at the 5ELDON 2 161.00 (344533) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.2. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.3. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.4. 4OSAGE (345400) 138.0 kV to 4OSG_1&2TAP (345401) 138.0 kV Transmission Circuit #z b.5. 4OSAGE (345400) 138.0 kV to 4OSG_5&6TAP (345406) 138.0 kV Transmission Circuit #1 b.6. 4OSAGE (345400) 138.0 kV to 4OSG_7&8TAP (345407) 138.0 kV Transmission Circuit #1 b.7. 4OSAGE (345400) 138.0 kV to 1OSAGE (346116) 34.5 kV Two Winding #1 b.8. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.9. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 b.10. 1ELDON 2 (346045) 34.5 kV to 5ELDON 2 (344533) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0214 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 161.00 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 161.00 (344234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CALIF (300063) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.2. 2CALIF (300550) 69.0 kV to 5CALIF (300063) 161.0 kV Two Winding #2 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.4. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z b.5. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.6. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 b.7. 1CALIF (346027) 34.5 kV to 5CALIF UE 2 (344234) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0215 | Single Phase Fault with Stuck Breaker on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply Fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0216 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.4. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.5. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0217 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0218 | Single Phase Fault with Stuck Breaker on RIV167 5 161.00 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0219 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0220 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.4. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0221 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0222 | Single Phase Fault with Stuck Breaker on FIR417 5 161.00 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 161.00 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0223 | Single Phase Fault with Stuck Breaker on OAK432 5 161.00 (547494) 161 kV Bus a. Apply Fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0224 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. OAK432 5 (547494) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0225 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0226 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0227 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0228 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0229 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0230 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0231 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0232 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0233 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0234 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0235 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0236 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0237 | Single Phase Fault with Stuck Breaker on 5APCH TP 161.00 (344026) 161 kV Bus a. Apply Fault at the 5APCH TP 161.00 (344026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.4. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.5. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0238 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0239 | Single Phase Fault with Stuck Breaker on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply Fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5LOYMART 1 (344040) 161.0 kV to 5LOYMART 2 (344041) 161.0 kV Transmission Circuit #z b.3. 5LOYMART 1 (344040) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.4. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.5. 5J994 SUB (344656) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.6. 5GUTHRIE 1 (344677) 161.0 kV to 5GUTHRIE 2 (344678) 161.0 kV Transmission Circuit #z b.7. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.8. 1LOYMART 1 (346010) 12.5 kV to 5LOYMART 1 (344040) 161.0 kV Two Winding #1 b.9. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0240 | Single Phase Fault with Stuck Breaker on 5ELDON 2 161.00 (344533) 161 kV Bus a. Apply Fault at the 5ELDON 2 161.00 (344533) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.2. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.3. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.4. 4OSAGE (345400) 138.0 kV to 4OSG_1&2TAP (345401) 138.0 kV Transmission Circuit #z b.5. 4OSAGE (345400) 138.0 kV to 4OSG_3&4TAP (345404) 138.0 kV Transmission Circuit #z b.6. 4OSAGE (345400) 138.0 kV to 4OSG_5&6TAP (345406) 138.0 kV Transmission Circuit #1 b.7. 4OSAGE (345400) 138.0 kV to 4OSG_7&8TAP (345407) 138.0 kV Transmission Circuit #1 b.8. 4OSAGE (345400) 138.0 kV to 1OSAGE (346116) 34.5 kV Two Winding #1 b.9. 4OSAGE (345400) 138.0 kV to 1OSAGE (346116) 34.5 kV Two Winding #2 b.10. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.11. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 b.12. 1ELDON 2 (346045) 34.5 kV to 5ELDON 2 (344533) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0241 | Single Phase Fault with Stuck Breaker on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply Fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LOYMART 1 (344040) 161.0 kV to 5LOYMART 2 (344041) 161.0 kV Transmission Circuit #z b.2. 5LOYMART 1 (344040) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.3. 5J994 SUB (344656) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.4. 5GUTHRIE 1 (344677) 161.0 kV to 5GUTHRIE 2 (344678) 161.0 kV Transmission Circuit #z b.5. 5GUTHRIE 2 (344678) 161.0 kV to 5MONTGMRY 1 (345231) 161.0 kV Transmission Circuit #1 b.6. 5GUTHRIE 2 (344678) 161.0 kV to 5MOREAU 1 (345239) 161.0 kV Transmission Circuit #1 b.7. 1LOYMART 1 (346010) 12.5 kV to 5LOYMART 1 (344040) 161.0 kV Two Winding #1 b.8. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0242 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.6. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.7. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0243 | Single Phase Fault with Stuck Breaker on 5JC ZION 161.00 (344814) 161 kV Bus a. Apply Fault at the 5JC ZION 161.00 (344814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.2. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.3. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.4. 5JC ZION (344814) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #z b.5. 2JC ZION (346089) 69.0 kV to 5JC ZION (344814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0244 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0245 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.4. NE CT17 (542983) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT18 (542984) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0246 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0247 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0248 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0249 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0250 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0251 | Single Phase Fault with Stuck Breaker on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply Fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.6. NKMA2 1 (530630) 12.5 kV to NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0252 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0253 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.4. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.5. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0254 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0255 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.4. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.5. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0256 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0257 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0258 | Single Phase Fault with Stuck Breaker on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply Fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0259 | Single Phase Fault with Stuck Breaker on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. RULETON3 (531357) 115.0 kV to LAWNRID3 (531368) 115.0 kV Transmission Circuit #1 b.5. BIRDCTY3 (531365) 115.0 kV to STFRAN 3 (531370) 115.0 kV Transmission Circuit #1 b.6. BIRDCTY3 (531365) 115.0 kV to MCDONLD3 (531487) 115.0 kV Transmission Circuit #1 b.7. LAWNRID3 (531368) 115.0 kV to STFRANT3 (531471) 115.0 kV Transmission Circuit #1 b.8. STFRAN 3 (531370) 115.0 kV to STFRANT3 (531471) 115.0 kV Transmission Circuit #1 b.9. CSTFRAN3 (531441) 115.0 kV to STFRANT3 (531471) 115.0 kV Transmission Circuit #1 b.10. MCDONLD3 (531487) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.11. BVERVLLY (531488) 115.0 kV to ONEOK 3 (531489) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0260 | Single Phase Fault with Stuck Breaker on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. LUDELLT3 (531220) 115.0 kV to LUDELL 3 (531221) 115.0 kV Transmission Circuit #1 b.5. LUDELLT3 (531220) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.6. LUDELLT3 (531220) 115.0 kV to HERNDON3 (531367) 115.0 kV Transmission Circuit #1 b.7. ATWODSW3 (531364) 115.0 kV to NATWOOD3 (531369) 115.0 kV Transmission Circuit #1 b.8. HERNDON3 (531367) 115.0 kV to JOHNSON3 (531371) 115.0 kV Transmission Circuit #1 b.9. JOHNSON3 (531371) 115.0 kV to OBER T 3 (531457) 115.0 kV Transmission Circuit #1 b.10. NORCATR3 (531372) 115.0 kV to RHOADES3 (531373) 115.0 kV Transmission Circuit #1 b.11. NORCATR3 (531372) 115.0 kV to OBER T 3 (531457) 115.0 kV Transmission Circuit #1 b.12. OBER T 3 (531457) 115.0 kV to OBERLIN3 (531458) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0261 | Single Phase Fault with Stuck Breaker on GEM_SW 3 115.00 (530713) 115 kV Bus a. Apply Fault at the GEM_SW 3 115.00 (530713) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. SEGNTP 3 (530682) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.3. GEM_SW 3 (530713) 115.0 kV to COLBY_PUMP3 (530716) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0262 | Single Phase Fault with Stuck Breaker on SEGNTP 3 115.00 (530682) 115 kV Bus a. Apply Fault at the SEGNTP 3 115.00 (530682) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.3. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.4. SEGNTP 3 (530682) 115.0 kV to SEGUIN 3 (530683) 115.0 kV Transmission Circuit #1 b.5. SEGNTP 3 (530682) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.6. SEGUIN 3 (530683) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0263 | Single Phase Fault with Stuck Breaker on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply Fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.2. PH RUN 3 (530559) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 b.3. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. SEGNTP 3 (530682) 115.0 kV to SEGUIN 3 (530683) 115.0 kV Transmission Circuit #1 b.5. SEGUIN 3 (530683) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0264 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.5. BEACH 3 (530557) 115.0 kV to HILLCTY3 (531387) 34.5 kV Two Winding #1 b.6. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.7. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0265 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0266 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0267 | Single Phase Fault with Stuck Breaker on GMEC 3 115.00 (530676) 115 kV Bus a. Apply Fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0268 | Single Phase Fault with Stuck Breaker on SALINE 3 115.00 (530551) 115 kV Bus a. Apply Fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0269 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.5. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.6. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.7. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0270 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0271 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0272 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0273 | Single Phase Fault with Stuck Breaker on NESCTY 3 115.00 (530607) 115 kV Bus a. Apply Fault at the NESCTY 3 115.00 (530607) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NESCTY 3 (530607) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NESCTY 3 (530607) 115.0 kV to NESS-CT1 (539722) 34.5 kV to NES-CT-T (539924) 13.8 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0274 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.9. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0275 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.10. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0276 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0277 | Single Phase Fault with Stuck Breaker on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply Fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.2. PH RUN 3 (530559) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 b.3. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. ARNOLD3 (531409) 115.0 kV to GOVE 3 (531411) 115.0 kV Transmission Circuit #1 b.5. ARNOLD3 (531409) 115.0 kV to RANSOM 3 (531414) 115.0 kV Transmission Circuit #1 b.6. GOVE 3 (531411) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0278 | Single Phase Fault with Stuck Breaker on GODLNDT3 115.00 (531443) 115 kV Bus a. Apply Fault at the GODLNDT3 115.00 (531443) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. BREWSTR3 (531351) 115.0 kV to GOODLND3 (531353) 115.0 kV Transmission Circuit #1 b.3. BREWSTR3 (531351) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. GOODLND3 (531353) 115.0 kV to GODLNDT3 (531443) 115.0 kV Transmission Circuit #1 b.5. RULETON3 (531357) 115.0 kV to GODLNDT3 (531443) 115.0 kV Transmission Circuit #1 b.6. GODLNDT3 (531443) 115.0 kV to GOODCTY3 (531444) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0279 | Single Phase Fault with Stuck Breaker on MINGO 3 115.00 (531429) 115 kV Bus a. Apply Fault at the MINGO 3 115.00 (531429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0280 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.5. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0281 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.5. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.7. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0282 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0283 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0284 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0285 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0286 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0287 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0288 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0289 | Single Phase Fault with Stuck Breaker on SHAYS_230 230.00 (530610) 230 kV Bus a. Apply Fault at the SHAYS_230 230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0290 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 b.8. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0291 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-065-TAP (768280) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0292 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0293 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0294 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0295 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0296 | Single Phase Fault with Stuck Breaker on BUFLOCRK6 230.00 (530688) 230 kV Bus a. Apply Fault at the BUFLOCRK6 230.00 (530688) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.3. BUFLOCRK1 (530689) 34.5 kV to PRWNDCL1 (530701) 34.5 kV Transmission Circuit #1 b.4. PRWINDG1 (530690) 0.7 kV to PRWNDCL1 (530701) 34.5 kV Two Winding #1 b.5. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.8. BUFLOCRK6 (530688) 230.0 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0297 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0298 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0299 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0300 | Single Phase Fault with Stuck Breaker on COLBY 3 115.00 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to Load #1 b.2. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0301 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0302 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0303 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0304 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0305 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0306 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLM1G (640010) 23.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0307 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0308 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.3. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0309 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0310 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0311 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0312 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0313 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0314 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.3. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0315 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0316 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0317 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0318 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0319 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0320 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0321 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0322 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0323 | Single Phase Fault with Stuck Breaker on BARBER 5 161.00 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.3. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.4. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.5. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.6. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0324 | Single Phase Fault with Stuck Breaker on WOLCOTT5 161.00 (546669) 161 kV Bus a. Apply Fault at the WOLCOTT5 161.00 (546669) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.2. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.3. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0325 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0326 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.4. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 b.7. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0327 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0328 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0329 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0330 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0331 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0332 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0333 | Single Phase Fault with Stuck Breaker on J1490_POI 345.00 (44888) 345 kV Bus a. Apply Fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1490_POI (44888) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 b.2. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0334 | Single Phase Fault with Stuck Breaker on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply Fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 b.2. 7KINGDM (300043) 345.0 kV to 5KINGDMB1 (300090) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0335 | Single Phase Fault with Stuck Breaker on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply Fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to VSC2_3 (992003) 345.0 kV Transmission Circuit #1 b.2. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0336 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to 5MORGANXF2 (301622) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0337 | Single Phase Fault with Stuck Breaker on 5BOONE 161.00 (300061) 161 kV Bus a. Apply Fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BOONE (300061) 161.0 kV to 5MLRSBGB1 (300519) 161.0 kV Transmission Circuit #1 b.2. 5BOONE (300061) 161.0 kV to 2BOONE (300493) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0338 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 b.2. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0339 | Single Phase Fault with Stuck Breaker on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply Fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LATHRP (300091) 161.0 kV to 5MPLTAP (300036) 161.0 kV Transmission Circuit #1 b.2. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0340 | Single Phase Fault with Stuck Breaker on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply Fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 b.2. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0341 | Single Phase Fault with Stuck Breaker on 5NORTON 161.00 (300105) 161 kV Bus a. Apply Fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 b.2. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0342 | Single Phase Fault with Stuck Breaker on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply Fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 b.2. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0343 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to 2SEDALI (300541) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0344 | Single Phase Fault with Stuck Breaker on 5MCBAINB1 161.00 (300501) 161 kV Bus a. Apply Fault at the 5MCBAINB1 161.00 (300501) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB1 (300501) 161.0 kV to 5MCBAINB2 (301489) 161.0 kV Transmission Circuit #z1 b.2. 5MCBAINB1 (300501) 161.0 kV to 5BOONE (300061) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0345 | Single Phase Fault with Stuck Breaker on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply Fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0346 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0347 | Single Phase Fault with Stuck Breaker on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply Fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0348 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 b.2. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0349 | Single Phase Fault with Stuck Breaker on 5CALIF 161.00 (300063) 161 kV Bus a. Apply Fault at the 5CALIF 161.00 (300063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CALIF (300550) 69.0 kV to 5CALIF (300063) 161.0 kV Two Winding #2 b.2. 2CALIF (300550) 69.0 kV to 2FORTNA (300554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0350 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0351 | Single Phase Fault with Stuck Breaker on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply Fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 b.2. 5LAMAR (300794) 161.0 kV to 2LAMR (300651) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0352 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to 5JASPER (300950) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0353 | Single Phase Fault with Stuck Breaker on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply Fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PLATCTY (301552) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #z1 b.2. 5PLATCTY (301552) 161.0 kV to 2PLATCTY (300307) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0354 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0355 | Single Phase Fault with Stuck Breaker on MIDLTNT4 138.00 (514804) 138 kV Bus a. Apply Fault at the MIDLTNT4 138.00 (514804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.2. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0356 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0357 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0358 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0359 | Single Phase Fault with Stuck Breaker on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0360 | Single Phase Fault with Stuck Breaker on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply Fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to JAGGER 3 (531360) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0361 | Single Phase Fault with Stuck Breaker on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply Fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEOTI 3 (531428) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 b.2. LEOTI 3 (531428) 115.0 kV to SELKIRK3 (531434) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0362 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 b.2. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0363 | Single Phase Fault with Stuck Breaker on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply Fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 b.2. SCOTCTY3 (531433) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0364 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0365 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 b.2. SETAB 3 (531464) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0366 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #2 b.2. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0367 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0368 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0369 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0370 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0371 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0372 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0373 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0374 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0375 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0376 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0377 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0378 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0379 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0380 | Single Phase Fault with Stuck Breaker on BURNS 7 345.00 (532803) 345 kV Bus a. Apply Fault at the BURNS 7 345.00 (532803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURNS 7 (532803) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. BURNS 7 (532803) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0381 | Single Phase Fault with Stuck Breaker on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0382 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 7 (532770) 345.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 b.2. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0383 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 b.2. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0384 | Single Phase Fault with Stuck Breaker on BAKER 2 69.000 (532926) 69 kV Bus a. Apply Fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0385 | Single Phase Fault with Stuck Breaker on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 b.2. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0386 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. MARMTNW5 (532935) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0387 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.2. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0388 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to LITCH 5 (532932) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0389 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to MIDLTNT4 (514804) 138.0 kV Transmission Circuit #1 b.2. CRESWLN4 (532981) 138.0 kV to CRESWLS2 (533573) 69.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0390 | Single Phase Fault with Stuck Breaker on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply Fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 4 (532982) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0391 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0392 | Single Phase Fault with Stuck Breaker on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply Fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.2. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0393 | Single Phase Fault with Stuck Breaker on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0394 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 4 (532996) 138.0 kV to TIOGA 2 (533646) 69.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0395 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK4 (532997) 138.0 kV to BUTLER 4 (532987) 138.0 kV Transmission Circuit #1 b.2. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0396 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. ALTOONA4 (533001) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0397 | Single Phase Fault with Stuck Breaker on DEARING4 138.00 (533002) 138 kV Bus a. Apply Fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0398 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0399 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONTGOM4 (533004) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0400 | Single Phase Fault with Stuck Breaker on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply Fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0401 | Single Phase Fault with Stuck Breaker on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply Fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0402 | Single Phase Fault with Stuck Breaker on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply Fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to HALSTD 4 (533011) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0403 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.2. NEOSHOS4 (533020) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0404 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.2. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0405 | Single Phase Fault with Stuck Breaker on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply Fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0406 | Single Phase Fault with Stuck Breaker on BU11PON4 138.00 (533032) 138 kV Bus a. Apply Fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BU11PON4 (533032) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0407 | Single Phase Fault with Stuck Breaker on CENTENN4 138.00 (533034) 138 kV Bus a. Apply Fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0408 | Single Phase Fault with Stuck Breaker on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0409 | Single Phase Fault with Stuck Breaker on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply Fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0410 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0411 | Single Phase Fault with Stuck Breaker on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply Fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0412 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0413 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to EVANS N4 (533040) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0414 | Single Phase Fault with Stuck Breaker on FARBER 4 138.00 (533042) 138 kV Bus a. Apply Fault at the FARBER 4 138.00 (533042) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0415 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0416 | Single Phase Fault with Stuck Breaker on GILL W 4 138.00 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.2. GILL W 4 (533045) 138.0 kV to GILL E 4 (533044) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0417 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.2. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0418 | Single Phase Fault with Stuck Breaker on GILL 4 138.00 (533047) 138 kV Bus a. Apply Fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL 4 (533047) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0419 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0420 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERS4 (533050) 138.0 kV to HOOVERN4 (533049) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0421 | Single Phase Fault with Stuck Breaker on 47TH ST4 138.00 (533058) 138 kV Bus a. Apply Fault at the 47TH ST4 138.00 (533058) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0422 | Single Phase Fault with Stuck Breaker on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. ROSEHIL4 (533062) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0423 | Single Phase Fault with Stuck Breaker on WACO S 4 138.00 (533071) 138 kV Bus a. Apply Fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WACO S 4 (533071) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #1 b.2. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0424 | Single Phase Fault with Stuck Breaker on WACO 4 138.00 (533072) 138 kV Bus a. Apply Fault at the WACO 4 138.00 (533072) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 b.2. WACO 4 (533072) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0425 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0426 | Single Phase Fault with Stuck Breaker on 4CORNER3 115.00 (533158) 115 kV Bus a. Apply Fault at the 4CORNER3 115.00 (533158) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CORNER3 (533158) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.2. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0427 | Single Phase Fault with Stuck Breaker on OSAGE J3 115.00 (533171) 115 kV Bus a. Apply Fault at the OSAGE J3 115.00 (533171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE J3 (533171) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.2. OSAGE J3 (533171) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0428 | Single Phase Fault with Stuck Breaker on EAST ST3 115.00 (533301) 115 kV Bus a. Apply Fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.2. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0429 | Single Phase Fault with Stuck Breaker on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply Fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0430 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LANG 3 (533304) 115.0 kV to LANG 7 (532769) 345.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 b.2. LANG 3 (533304) 115.0 kV to EAST ST3 (533301) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0431 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 3 (533305) 115.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 b.2. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0432 | Single Phase Fault with Stuck Breaker on READING3 115.00 (533306) 115 kV Bus a. Apply Fault at the READING3 115.00 (533306) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. READING3 (533306) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 b.2. READING3 (533306) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0433 | Single Phase Fault with Stuck Breaker on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply Fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (533307) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0434 | Single Phase Fault with Stuck Breaker on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply Fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0435 | Single Phase Fault with Stuck Breaker on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.2. WEMPORI3 (533309) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0436 | Single Phase Fault with Stuck Breaker on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply Fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WMBROSJ3 (533311) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0437 | Single Phase Fault with Stuck Breaker on BURLJCT2 69.000 (533626) 69 kV Bus a. Apply Fault at the BURLJCT2 69.000 (533626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0438 | Single Phase Fault with Stuck Breaker on CC2SHAR2 69.000 (533629) 69 kV Bus a. Apply Fault at the CC2SHAR2 69.000 (533629) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC2SHAR2 (533629) 69.0 kV to CC5SHAR1 (533888) 12.5 kV Two Winding #1 b.2. CC2SHAR2 (533629) 69.0 kV to CC6SHAR1 (533889) 12.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0439 | Single Phase Fault with Stuck Breaker on CC3WEST2 69.000 (533630) 69 kV Bus a. Apply Fault at the CC3WEST2 69.000 (533630) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC3WEST2 (533630) 69.0 kV to BURLJCT2 (533626) 69.0 kV Transmission Circuit #1 b.2. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0440 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0441 | Single Phase Fault with Stuck Breaker on UN1ELSM2 69.000 (533647) 69 kV Bus a. Apply Fault at the UN1ELSM2 69.000 (533647) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UN1ELSM2 (533647) 69.0 kV to MARMATN2 (533639) 69.0 kV Transmission Circuit #1 b.2. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0442 | Single Phase Fault with Stuck Breaker on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply Fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0443 | Single Phase Fault with Stuck Breaker on LABETTS2 69.000 (533696) 69 kV Bus a. Apply Fault at the LABETTS2 69.000 (533696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0444 | Single Phase Fault with Stuck Breaker on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply Fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0445 | Single Phase Fault with Stuck Breaker on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply Fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0446 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 b.2. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0447 | Single Phase Fault with Stuck Breaker on BELL 2 69.000 (533783) 69 kV Bus a. Apply Fault at the BELL 2 69.000 (533783) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELL 2 (533783) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 b.2. BELL 2 (533783) 69.0 kV to SC3MILL2 (533552) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0448 | Single Phase Fault with Stuck Breaker on CANAL 4 138.00 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 138.00 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALS 2 (533784) 69.0 kV to CANAL 4 (533033) 138.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 b.2. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0449 | Single Phase Fault with Stuck Breaker on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply Fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0450 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.2. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0451 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL W 2 (533796) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 b.2. GILL W 2 (533796) 69.0 kV to GILL E 4 (533044) 138.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0452 | Single Phase Fault with Stuck Breaker on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply Fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILLJCT2 (533798) 69.0 kV to GILL E 2 (533795) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0453 | Single Phase Fault with Stuck Breaker on HAYSVJS2 69.000 (533802) 69 kV Bus a. Apply Fault at the HAYSVJS2 69.000 (533802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYSVJS2 (533802) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #1 b.2. HAYSVJS2 (533802) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0454 | Single Phase Fault with Stuck Breaker on HAYSVJN2 69.000 (533804) 69 kV Bus a. Apply Fault at the HAYSVJN2 69.000 (533804) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYSVJN2 (533804) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #1 b.2. HAYSVJN2 (533804) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0455 | Single Phase Fault with Stuck Breaker on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply Fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0456 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERS2 (533806) 69.0 kV to HOOVERS4 (533050) 138.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 b.2. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0457 | Single Phase Fault with Stuck Breaker on HYDRJN2 69.000 (533808) 69 kV Bus a. Apply Fault at the HYDRJN2 69.000 (533808) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDRJN2 (533808) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 b.2. HYDRJN2 (533808) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0458 | Single Phase Fault with Stuck Breaker on HYDRJS2 69.000 (533810) 69 kV Bus a. Apply Fault at the HYDRJS2 69.000 (533810) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDRJS2 (533810) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 b.2. HYDRJS2 (533810) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0459 | Single Phase Fault with Stuck Breaker on LIN 2 69.000 (533812) 69 kV Bus a. Apply Fault at the LIN 2 69.000 (533812) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.2. LIN 2 (533812) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0460 | Single Phase Fault with Stuck Breaker on MACARTH2 69.000 (533813) 69 kV Bus a. Apply Fault at the MACARTH2 69.000 (533813) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MACARTH2 (533813) 69.0 kV to GILL E 2 (533795) 69.0 kV Transmission Circuit #1 b.2. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0461 | Single Phase Fault with Stuck Breaker on BLF-CRK4 138.00 (539002) 138 kV Bus a. Apply Fault at the BLF-CRK4 138.00 (539002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLF-CRK4 (539002) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0462 | Single Phase Fault with Stuck Breaker on CLDWELL4 138.00 (539003) 138 kV Bus a. Apply Fault at the CLDWELL4 138.00 (539003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLDWELL4 (539003) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0463 | Single Phase Fault with Stuck Breaker on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. MILAN_GOAB (539008) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0464 | Single Phase Fault with Stuck Breaker on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply Fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0465 | Single Phase Fault with Stuck Breaker on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply Fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0466 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to GRTBEND3 (539678) 115.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0467 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.2. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0468 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0469 | Single Phase Fault with Stuck Breaker on FORD 3 115.00 (539758) 115 kV Bus a. Apply Fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0470 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.2. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0471 | Single Phase Fault with Stuck Breaker on NFTDODG3 115.00 (539771) 115 kV Bus a. Apply Fault at the NFTDODG3 115.00 (539771) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NFTDODG3 (539771) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #2 b.2. NFTDODG3 (539771) 115.0 kV to SPRVL 3 (539759) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0472 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0473 | Single Phase Fault with Stuck Breaker on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply Fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345.0 kV to GEN-2008-124 (579480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0474 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0475 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0476 | Single Phase Fault with Stuck Breaker on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 b.2. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0477 | Single Phase Fault with Stuck Breaker on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. SMTHVL 5 (541204) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0478 | Single Phase Fault with Stuck Breaker on KCI 5 161.00 (541212) 161 kV Bus a. Apply Fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KCI 5 (541212) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. KCI 5 (541212) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0479 | Single Phase Fault with Stuck Breaker on FRLVW 5 161.00 (541213) 161 kV Bus a. Apply Fault at the FRLVW 5 161.00 (541213) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRLVW 5 (541213) 161.0 kV to KCI 5 (541212) 161.0 kV Transmission Circuit #1 b.2. FRLVW 5 (541213) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0480 | Single Phase Fault with Stuck Breaker on TWA 5 161.00 (541214) 161 kV Bus a. Apply Fault at the TWA 5 161.00 (541214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 b.2. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0481 | Single Phase Fault with Stuck Breaker on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply Fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 b.2. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0482 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0483 | Single Phase Fault with Stuck Breaker on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply Fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. PLTCTY 5 (541221) 161.0 kV to KCI 5 (541212) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0484 | Single Phase Fault with Stuck Breaker on GRAINVL5 161.00 (541226) 161 kV Bus a. Apply Fault at the GRAINVL5 161.00 (541226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAINVL5 (541226) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 b.2. GRAINVL5 (541226) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0485 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRIDGE5 (541230) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0486 | Single Phase Fault with Stuck Breaker on LEX161 5 161.00 (541232) 161 kV Bus a. Apply Fault at the LEX161 5 161.00 (541232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. LEX161 5 (541232) 161.0 kV to LEX69 2 (541264) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0487 | Single Phase Fault with Stuck Breaker on RICHMND5 161.00 (541236) 161 kV Bus a. Apply Fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to LEX161 5 (541232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0488 | Single Phase Fault with Stuck Breaker on BLSPW 5 161.00 (541237) 161 kV Bus a. Apply Fault at the BLSPW 5 161.00 (541237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPW 5 (541237) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0489 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDEAST5 (541241) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 b.2. SEDEAST5 (541241) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0490 | Single Phase Fault with Stuck Breaker on LBRTYWT5 161.00 (541247) 161 kV Bus a. Apply Fault at the LBRTYWT5 161.00 (541247) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYWT5 (541247) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 b.2. LBRTYWT5 (541247) 161.0 kV to HLLMRK 5 (541215) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0491 | Single Phase Fault with Stuck Breaker on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply Fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. LBRTYST5 (541248) 161.0 kV to LIBRTYS2 (543095) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0492 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 b.2. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0493 | Single Phase Fault with Stuck Breaker on STALEY 2 69.000 (541261) 69 kV Bus a. Apply Fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STALEY 2 (541261) 69.0 kV to RNRDGE 2 (541260) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0494 | Single Phase Fault with Stuck Breaker on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply Fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY2 (541262) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 b.2. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0495 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 b.2. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0496 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0497 | Single Phase Fault with Stuck Breaker on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply Fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDN 2 (541271) 69.0 kV Transmission Circuit #1 b.2. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0498 | Single Phase Fault with Stuck Breaker on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply Fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDS 2 (541272) 69.0 kV Transmission Circuit #1 b.2. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0499 | Single Phase Fault with Stuck Breaker on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply Fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDPLT 2 (541275) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 b.2. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0500 | Single Phase Fault with Stuck Breaker on COLECMP2 69.000 (541276) 69 kV Bus a. Apply Fault at the COLECMP2 69.000 (541276) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLECMP2 (541276) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 b.2. COLECMP2 (541276) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0501 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAFBE_SW5 (541337) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. WAFBE_SW5 (541337) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0502 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 b.2. S.HARP 5 (541341) 161.0 kV to ARCHIE 5 (541207) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0503 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0504 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0505 | Single Phase Fault with Stuck Breaker on KNOSTERTP 69.000 (541534) 69 kV Bus a. Apply Fault at the KNOSTERTP 69.000 (541534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOSTERTP (541534) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 b.2. KNOSTERTP (541534) 69.0 kV to MONSERTP (541524) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0506 | Single Phase Fault with Stuck Breaker on LAMONTETP 69.000 (541535) 69 kV Bus a. Apply Fault at the LAMONTETP 69.000 (541535) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMONTETP (541535) 69.0 kV to SEDN 2 (541271) 69.0 kV Transmission Circuit #1 b.2. LAMONTETP (541535) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0507 | Single Phase Fault with Stuck Breaker on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply Fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0508 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to ATLNTIC7 (542940) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0509 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0510 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 b.2. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0511 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0512 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0513 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LAC G1 1 (542955) 22.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0514 | Single Phase Fault with Stuck Breaker on TROOST 5 161.00 (542986) 161 kV Bus a. Apply Fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 b.2. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0515 | Single Phase Fault with Stuck Breaker on GRAND 5 161.00 (542987) 161 kV Bus a. Apply Fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0516 | Single Phase Fault with Stuck Breaker on GRAND W5 161.00 (542988) 161 kV Bus a. Apply Fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0517 | Single Phase Fault with Stuck Breaker on NAVY 5 161.00 (542989) 161 kV Bus a. Apply Fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NAVY 5 (542989) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0518 | Single Phase Fault with Stuck Breaker on CROSTWN5 161.00 (542990) 161 kV Bus a. Apply Fault at the CROSTWN5 161.00 (542990) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSTWN5 (542990) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. CROSTWN5 (542990) 161.0 kV to TROOST 5 (542986) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0519 | Single Phase Fault with Stuck Breaker on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply Fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDTOWN5 (542996) 161.0 kV to TROOST 5 (542986) 161.0 kV Transmission Circuit #1 b.2. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0520 | Single Phase Fault with Stuck Breaker on LEEDS 5 161.00 (542997) 161 kV Bus a. Apply Fault at the LEEDS 5 161.00 (542997) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEEDS 5 (542997) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0521 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0522 | Single Phase Fault with Stuck Breaker on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0523 | Single Phase Fault with Stuck Breaker on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to AVONDAL5 (543015) 161.0 kV Transmission Circuit #1 b.2. GLADSTN5 (543016) 161.0 kV to GLADSTN_CAP5 (542946) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0524 | Single Phase Fault with Stuck Breaker on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply Fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 b.2. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0525 | Single Phase Fault with Stuck Breaker on BARRY 5 161.00 (543019) 161 kV Bus a. Apply Fault at the BARRY 5 161.00 (543019) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRY 5 (543019) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. BARRY 5 (543019) 161.0 kV to BARRY_CAP 5 (542944) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0526 | Single Phase Fault with Stuck Breaker on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply Fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMGHAM5 (543020) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.2. BRMGHAM5 (543020) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0527 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV to NASHUA 7 (542980) 345.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 b.2. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0528 | Single Phase Fault with Stuck Breaker on SHOLCRK5 161.00 (543029) 161 kV Bus a. Apply Fault at the SHOLCRK5 161.00 (543029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHOLCRK5 (543029) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. SHOLCRK5 (543029) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0529 | Single Phase Fault with Stuck Breaker on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply Fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 b.2. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0530 | Single Phase Fault with Stuck Breaker on COURTNY2 69.000 (543085) 69 kV Bus a. Apply Fault at the COURTNY2 69.000 (543085) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0531 | Single Phase Fault with Stuck Breaker on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply Fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0532 | Single Phase Fault with Stuck Breaker on BLUSPRG2 69.000 (543088) 69 kV Bus a. Apply Fault at the BLUSPRG2 69.000 (543088) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0533 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 b.2. DUNCNRD2 (543091) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0534 | Single Phase Fault with Stuck Breaker on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply Fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUGRCK_TP_E2 (543165) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 b.2. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0535 | Single Phase Fault with Stuck Breaker on DAKOTA_5 161.00 (543650) 161 kV Bus a. Apply Fault at the DAKOTA_5 161.00 (543650) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAKOTA_5 (543650) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #1 b.2. DAKOTA_5 (543650) 161.0 kV to CNTRVIL5 (543065) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0536 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0537 | Single Phase Fault with Stuck Breaker on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply Fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0538 | Single Phase Fault with Stuck Breaker on COL 94 2 69.000 (547530) 69 kV Bus a. Apply Fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0539 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 2 (547539) 69.0 kV to JOP145 5 (547470) 161.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 b.2. JOP145 2 (547539) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0540 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to RIV4525 (547469) 161.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 b.2. RIV167 2 (547541) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0541 | Single Phase Fault with Stuck Breaker on BAX271 2 69.000 (547554) 69 kV Bus a. Apply Fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.2. BAX271 2 (547554) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0542 | Single Phase Fault with Stuck Breaker on GLF339 2 69.000 (547690) 69 kV Bus a. Apply Fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLF339 2 (547690) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0543 | Single Phase Fault with Stuck Breaker on SUB I 69.000 (548800) 69 kV Bus a. Apply Fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 b.2. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0544 | Single Phase Fault with Stuck Breaker on SUB K 69.000 (548801) 69 kV Bus a. Apply Fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0545 | Single Phase Fault with Stuck Breaker on SUB H 69.000 (548802) 69 kV Bus a. Apply Fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB H (548802) 69.0 kV to COURTNY2 (543085) 69.0 kV Transmission Circuit #1 b.2. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0546 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0547 | Single Phase Fault with Stuck Breaker on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply Fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0548 | Single Phase Fault with Stuck Breaker on SUB B 69.000 (548810) 69 kV Bus a. Apply Fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 b.2. SUB B (548810) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0549 | Single Phase Fault with Stuck Breaker on SUB J 69.000 (548811) 69 kV Bus a. Apply Fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB J (548811) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0550 | Single Phase Fault with Stuck Breaker on G15052_T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15052_T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15052_T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15052_T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0551 | Single Phase Fault with Stuck Breaker on G16-046-TAP 345.00 (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP 345.00 (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0552 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0553 | Single Phase Fault with Stuck Breaker on GEN-2022-161345.00 (562477) 345 kV Bus a. Apply Fault at the GEN-2022-161345.00 (562477) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-161 (562477) 345.0 kV to GEN-2014-001 (583850) 345.0 kV Transmission Circuit #z1 b.2. GEN-2022-161 (562477) 345.0 kV to G22-161XFMR2 (770205) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0554 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583850) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583850) 345.0 kV to GEN-2014-001 (583859) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583850) 345.0 kV to GEN-2022-161 (562477) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0555 | Single Phase Fault with Stuck Breaker on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply Fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-074 (587680) 345.0 kV to G16-074XFMR1 (587681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0556 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR1 (588361) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0557 | Single Phase Fault with Stuck Breaker on G16-153-TAP 345.00 (588364) 345 kV Bus a. Apply Fault at the G16-153-TAP 345.00 (588364) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-153-TAP (588364) 345.0 kV to GEN-2016-153 (588360) 345.0 kV Transmission Circuit #1 b.2. G16-153-TAP (588364) 345.0 kV to GEN-2017-086 (589240) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0558 | Single Phase Fault with Stuck Breaker on GEN-2017-005161.00 (588500) 161 kV Bus a. Apply Fault at the GEN-2017-005161.00 (588500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-005 (588500) 161.0 kV to G17-005XFMR1 (588501) 34.5 kV Two Winding #1 b.2. GEN-2017-005 (588500) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0559 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0560 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0561 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0562 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0563 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0564 | Single Phase Fault with Stuck Breaker on GI-95_POI 345.00 (709500) 345 kV Bus a. Apply Fault at the GI-95_POI 345.00 (709500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI-95_POI (709500) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. GI-95_POI (709500) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0565 | Single Phase Fault with Stuck Breaker on GEN-2017-183345.00 (761376) 345 kV Bus a. Apply Fault at the GEN-2017-183345.00 (761376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-183 (761376) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-183 (761376) 345.0 kV to G17-184XFMR2 (761401) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0566 | Single Phase Fault with Stuck Breaker on GEN-2018-125345.00 (763406) 345 kV Bus a. Apply Fault at the GEN-2018-125345.00 (763406) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-125 (763406) 345.0 kV to G18-125-XFM1 (763407) 34.5 kV Two Winding #1 b.2. GEN-2018-125 (763406) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0567 | Single Phase Fault with Stuck Breaker on GEN-2018-128345.00 (763417) 345 kV Bus a. Apply Fault at the GEN-2018-128345.00 (763417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-128 (763417) 345.0 kV to G18-128-XFM1 (763418) 34.5 kV Two Winding #1 b.2. GEN-2018-128 (763417) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0568 | Single Phase Fault with Stuck Breaker on GEN-2019-030345.00 (763670) 345 kV Bus a. Apply Fault at the GEN-2019-030345.00 (763670) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-030 (763670) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 b.2. GEN-2019-030 (763670) 345.0 kV to G19-030-XFM1 (763671) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0569 | Single Phase Fault with Stuck Breaker on G19-053/055 230.00 (763846) 230 kV Bus a. Apply Fault at the G19-053/055 230.00 (763846) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-053/055 (763846) 230.0 kV to G19-055-XFM1 (763869) 34.5 kV Two Winding #1 b.2. G19-053/055 (763846) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0570 | Single Phase Fault with Stuck Breaker on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply Fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0571 | Single Phase Fault with Stuck Breaker on G19-054/068 230.00 (763857) 230 kV Bus a. Apply Fault at the G19-054/068 230.00 (763857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054/068 (763857) 230.0 kV to G19-054-XFM1 (763858) 34.5 kV Two Winding #1 b.2. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0572 | Single Phase Fault with Stuck Breaker on GEN-2020-072161.00 (764345) 161 kV Bus a. Apply Fault at the GEN-2020-072161.00 (764345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-072 (764345) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-072 (764345) 161.0 kV to G20-072-XFM1 (764348) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0573 | Single Phase Fault with Stuck Breaker on GEN-2020-090345.00 (765190) 345 kV Bus a. Apply Fault at the GEN-2020-090345.00 (765190) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-090 (765190) 345.0 kV to G20-090-XFM1 (765193) 34.5 kV Two Winding #1 b.2. GEN-2020-090 (765190) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0574 | Single Phase Fault with Stuck Breaker on G20-090-TAP 345.00 (765200) 345 kV Bus a. Apply Fault at the G20-090-TAP 345.00 (765200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-090-TAP (765200) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. G20-090-TAP (765200) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0575 | Single Phase Fault with Stuck Breaker on GEN-2021-029345.00 (765570) 345 kV Bus a. Apply Fault at the GEN-2021-029345.00 (765570) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-029 (765570) 345.0 kV to G21-029-XFM1 (765574) 34.5 kV Two Winding #1 b.2. GEN-2021-029 (765570) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0576 | Single Phase Fault with Stuck Breaker on G21-029-TAP 345.00 (765571) 345 kV Bus a. Apply Fault at the G21-029-TAP 345.00 (765571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. G21-029-TAP (765571) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0577 | Single Phase Fault with Stuck Breaker on GEN-2021-068345.00 (765910) 345 kV Bus a. Apply Fault at the GEN-2021-068345.00 (765910) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-068 (765910) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-068 (765910) 345.0 kV to G21-068-XFM1 (765914) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0578 | Single Phase Fault with Stuck Breaker on G21-068-TAP 345.00 (765911) 345 kV Bus a. Apply Fault at the G21-068-TAP 345.00 (765911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-068-TAP (765911) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. G21-068-TAP (765911) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0579 | Single Phase Fault with Stuck Breaker on GEN-2020-007345.00 (766260) 345 kV Bus a. Apply Fault at the GEN-2020-007345.00 (766260) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-007 (766260) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-007 (766260) 345.0 kV to G20-007-XFM1 (766264) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0580 | Single Phase Fault with Stuck Breaker on G22-007-TAP 115.00 (767120) 115 kV Bus a. Apply Fault at the G22-007-TAP 115.00 (767120) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-007-TAP (767120) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.2. G22-007-TAP (767120) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0581 | Single Phase Fault with Stuck Breaker on G22-013-TAP 345.00 (767240) 345 kV Bus a. Apply Fault at the G22-013-TAP 345.00 (767240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-013-TAP (767240) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G22-013-TAP (767240) 345.0 kV to GEN-2022-013 (767241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0582 | Single Phase Fault with Stuck Breaker on G22-015-TAP 345.00 (767280) 345 kV Bus a. Apply Fault at the G22-015-TAP 345.00 (767280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. G22-015-TAP (767280) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0583 | Single Phase Fault with Stuck Breaker on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply Fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-065-TAP (768280) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. G22-065-TAP (768280) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0584 | Single Phase Fault with Stuck Breaker on G22-075-TAP 345.00 (768480) 345 kV Bus a. Apply Fault at the G22-075-TAP 345.00 (768480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-075-TAP (768480) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G22-075-TAP (768480) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0585 | Single Phase Fault with Stuck Breaker on G22-100-TAP 161.00 (768980) 161 kV Bus a. Apply Fault at the G22-100-TAP 161.00 (768980) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-100-TAP (768980) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. G22-100-TAP (768980) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0586 | Single Phase Fault with Stuck Breaker on G22-214-TAP 138.00 (771260) 138 kV Bus a. Apply Fault at the G22-214-TAP 138.00 (771260) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-214-TAP (771260) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 b.2. G22-214-TAP (771260) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0587 | Single Phase Fault with Stuck Breaker on 5BOONE 161.00 (300061) 161 kV Bus a. Apply Fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BOONE (300493) 69.0 kV to 5BOONE (300061) 161.0 kV Two Winding #1 b.2. 2BOONE (300493) 69.0 kV to 2DEERPK (300497) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0588 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEORGE (300531) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 b.2. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0589 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 b.2. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0590 | Single Phase Fault with Stuck Breaker on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply Fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PLATCTY (300307) 69.0 kV to 5PLATCTY (301552) 161.0 kV Two Winding #1 b.2. 2PLATCTY (300307) 69.0 kV to 2HOOVER (300298) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0591 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.2. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0592 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 b.2. 5JASPER (300950) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0593 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0594 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0595 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0596 | Single Phase Fault with Stuck Breaker on COLBY 3 115.00 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0597 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0598 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0599 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0600 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0601 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LANG 7 (532769) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0602 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 7 (532770) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0603 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0604 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.2. NEOSHON4 (533022) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0605 | Single Phase Fault with Stuck Breaker on CANAL 4 138.00 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 138.00 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANAL 4 (533033) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #1 b.2. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0606 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASOE4 (533059) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #z1 b.2. ELPASOE4 (533059) 138.0 kV to 47TH ST4 (533058) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0607 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 b.2. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0608 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 b.2. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0609 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 b.2. CRESWLS2 (533573) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0610 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 2 (533646) 69.0 kV to COALCRK2 (533633) 69.0 kV Transmission Circuit #1 b.2. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0611 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.2. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0612 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0613 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0614 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0615 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0616 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0617 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0618 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0619 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0620 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0621 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0622 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0623 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 b.2. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0624 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0625 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0626 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 b.2. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0627 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO7 (640326) 115.0 kV to BEVERLY7 (640082) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0628 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD7 (640381) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0629 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0630 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT4 (532992) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0631 | Single Phase Fault with Stuck Breaker on SHERIDN2 69.000 (533841) 69 kV Bus a. Apply Fault at the SHERIDN2 69.000 (533841) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHERIDN2 (533841) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0632 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0633 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 b.2. SUB M (548815) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0634 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOK 7 (640269) 115.0 kV to CAMBRIG7 (640100) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0635 | Single Phase Fault with Stuck Breaker on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply Fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7THOMHL (300049) 345.0 kV to 5THOMHLXF4 (301510) 161.0 kV Two Winding #4 b.2. 7THOMHL (300049) 345.0 kV to 5THOMHLXF3 (301506) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0636 | Single Phase Fault with Stuck Breaker on VSC2_3 345.00 (992003) 345 kV Bus a. Apply Fault at the VSC2_3 345.00 (992003) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VSC2_3 (992003) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 b.2. VSC2_3 (992003) 345.0 kV to VSC2_6 (992006) 276.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0637 | Single Phase Fault with Stuck Breaker on 5MLRSBGB1 161.00 (300519) 161 kV Bus a. Apply Fault at the 5MLRSBGB1 161.00 (300519) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MLRSBGB1 (300519) 161.0 kV to 5MLRSBGB2 (301498) 161.0 kV Transmission Circuit #z1 b.2. 5MLRSBGB1 (300519) 161.0 kV to 5BOONE (300061) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0638 | Single Phase Fault with Stuck Breaker on 5NORTONTP 161.00 (301567) 161 kV Bus a. Apply Fault at the 5NORTONTP 161.00 (301567) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTONTP (301567) 161.0 kV to 5GEORGE (300082) 161.0 kV Transmission Circuit #1 b.2. 5NORTONTP (301567) 161.0 kV to 5NORTON (300105) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0639 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0640 | Single Phase Fault with Stuck Breaker on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply Fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to 5PITTSV (300110) 161.0 kV Transmission Circuit #1 b.2. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0641 | Single Phase Fault with Stuck Breaker on G20-072-TAP 161.00 (764355) 161 kV Bus a. Apply Fault at the G20-072-TAP 161.00 (764355) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-072-TAP (764355) 161.0 kV to 5SEDALA (300117) 161.0 kV Transmission Circuit #1 b.2. G20-072-TAP (764355) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0642 | Single Phase Fault with Stuck Breaker on 5MCBAINB2 161.00 (301489) 161 kV Bus a. Apply Fault at the 5MCBAINB2 161.00 (301489) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5MCBAINB2 (301489) 161.0 kV to 5MCBAINB1 (300501) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0643 | Single Phase Fault with Stuck Breaker on 2SYLVAN 69.000 (300545) 69 kV Bus a. Apply Fault at the 2SYLVAN 69.000 (300545) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SYLVAN (300545) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2SYLVAN (300545) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0644 | Single Phase Fault with Stuck Breaker on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply Fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2FORTNA (300554) 69.0 kV to 2CALIF (300550) 69.0 kV Transmission Circuit #1 b.2. 2FORTNA (300554) 69.0 kV to 2SYRACS (300564) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0645 | Single Phase Fault with Stuck Breaker on 2PRARIE 69.000 (300561) 69 kV Bus a. Apply Fault at the 2PRARIE 69.000 (300561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PRARIE (300561) 69.0 kV to 2CALIF (300550) 69.0 kV Transmission Circuit #1 b.2. 2PRARIE (300561) 69.0 kV to 2PILOTG (300560) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0646 | Single Phase Fault with Stuck Breaker on 2ST_MARTINS 69.000 (301442) 69 kV Bus a. Apply Fault at the 2ST_MARTINS 69.000 (301442) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ST_MARTINS (301442) 69.0 kV to 2CALIF (300550) 69.0 kV Transmission Circuit #1 b.2. 2ST_MARTINS (301442) 69.0 kV to 2SCRUGG (300637) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0647 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0648 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0649 | Single Phase Fault with Stuck Breaker on G18-128-TAP 345.00 (763421) 345 kV Bus a. Apply Fault at the G18-128-TAP 345.00 (763421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-128-TAP (763421) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. G18-128-TAP (763421) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0650 | Single Phase Fault with Stuck Breaker on GEN-2021-076345.00 (765990) 345 kV Bus a. Apply Fault at the GEN-2021-076345.00 (765990) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-076 (765990) 345.0 kV to G21-076-XFM1 (765994) 34.5 kV Two Winding #1 b.2. GEN-2021-076 (765990) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0651 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 7 (532773) 345.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0652 | Single Phase Fault with Stuck Breaker on CNTRLPL3 115.00 (531485) 115 kV Bus a. Apply Fault at the CNTRLPL3 115.00 (531485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRLPL3 (531485) 115.0 kV to LEOTI 3 (531428) 115.0 kV Transmission Circuit #1 b.2. CNTRLPL3 (531485) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0653 | Single Phase Fault with Stuck Breaker on G19-030-TAP 345.00 (763677) 345 kV Bus a. Apply Fault at the G19-030-TAP 345.00 (763677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-030-TAP (763677) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G19-030-TAP (763677) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0654 | Single Phase Fault with Stuck Breaker on GEN-2021-107345.00 (766240) 345 kV Bus a. Apply Fault at the GEN-2021-107345.00 (766240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-107 (766240) 345.0 kV to G21-107-XFM1 (766244) 34.5 kV Two Winding #1 b.2. GEN-2021-107 (766240) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0655 | Single Phase Fault with Stuck Breaker on G16-111-TAP 345.00 (587884) 345 kV Bus a. Apply Fault at the G16-111-TAP 345.00 (587884) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-111-TAP (587884) 345.0 kV to RENO 7 (532771) 345.0 kV Transmission Circuit #1 b.2. G16-111-TAP (587884) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0656 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0657 | Single Phase Fault with Stuck Breaker on GEN-2017-220345.00 (760284) 345 kV Bus a. Apply Fault at the GEN-2017-220345.00 (760284) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-220 (760284) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-220 (760284) 345.0 kV to G17-220-XFM1 (760285) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0658 | Single Phase Fault with Stuck Breaker on G21-096-TAP 345.00 (766141) 345 kV Bus a. Apply Fault at the G21-096-TAP 345.00 (766141) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-096-TAP (766141) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. G21-096-TAP (766141) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0659 | Single Phase Fault with Stuck Breaker on GEN-2018-032345.00 (762680) 345 kV Bus a. Apply Fault at the GEN-2018-032345.00 (762680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-032 (762680) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-032 (762680) 345.0 kV to G18-032XFM1 (762681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0660 | Single Phase Fault with Stuck Breaker on GEN-2021-006345.00 (765350) 345 kV Bus a. Apply Fault at the GEN-2021-006345.00 (765350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-006 (765350) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-006 (765350) 345.0 kV to G21-006-XFM2 (765357) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0661 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583859) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583859) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583859) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583859) 345.0 kV to GEN-2014-001 (583850) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0662 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. UNIONRG6 (532874) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0663 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0664 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. G19-054-TAP (763862) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0665 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 b.2. NEOSHOS2 (533778) 69.0 kV to BAKER 2 (532926) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0666 | Single Phase Fault with Stuck Breaker on G17-005-TAP 161.00 (588504) 161 kV Bus a. Apply Fault at the G17-005-TAP 161.00 (588504) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-005-TAP (588504) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. G17-005-TAP (588504) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0667 | Single Phase Fault with Stuck Breaker on G20-079-TAP 161.00 (764310) 161 kV Bus a. Apply Fault at the G20-079-TAP 161.00 (764310) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-079-TAP (764310) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. G20-079-TAP (764310) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0668 | Single Phase Fault with Stuck Breaker on GEN-2022-006161.00 (767101) 161 kV Bus a. Apply Fault at the GEN-2022-006161.00 (767101) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-006 (767101) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. GEN-2022-006 (767101) 161.0 kV to G22-006XFMR1 (767102) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0669 | Single Phase Fault with Stuck Breaker on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply Fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SC10BEL4 (533063) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. SC10BEL4 (533063) 138.0 kV to FARBER 4 (533042) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0670 | Single Phase Fault with Stuck Breaker on GEN-2017-121138.00 (761838) 138 kV Bus a. Apply Fault at the GEN-2017-121138.00 (761838) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-121 (761838) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. GEN-2017-121 (761838) 138.0 kV to G17-121XFM2 (761842) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0671 | Single Phase Fault with Stuck Breaker on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply Fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TAYLOR 4 (533006) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. TAYLOR 4 (533006) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0672 | Single Phase Fault with Stuck Breaker on SG12COL4 138.00 (533065) 138 kV Bus a. Apply Fault at the SG12COL4 138.00 (533065) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SG12COL4 (533065) 138.0 kV to EVANS N4 (533040) 138.0 kV Transmission Circuit #1 b.2. SG12COL4 (533065) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0673 | Single Phase Fault with Stuck Breaker on WACO N 4 138.00 (533073) 138 kV Bus a. Apply Fault at the WACO N 4 138.00 (533073) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WACO N 4 (533073) 138.0 kV to CENTENN4 (533034) 138.0 kV Transmission Circuit #1 b.2. WACO N 4 (533073) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0674 | Single Phase Fault with Stuck Breaker on MAIZE 4 138.00 (533054) 138 kV Bus a. Apply Fault at the MAIZE 4 138.00 (533054) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAIZE 4 (533054) 138.0 kV to EVANS N4 (533040) 138.0 kV Transmission Circuit #1 b.2. MAIZE 4 (533054) 138.0 kV to CHISHLM4 (533035) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0675 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 45TH ST4 (533074) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #1 b.2. 45TH ST4 (533074) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0676 | Single Phase Fault with Stuck Breaker on STEARMN4 138.00 (533068) 138 kV Bus a. Apply Fault at the STEARMN4 138.00 (533068) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEARMN4 (533068) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. STEARMN4 (533068) 138.0 kV to BOEINGE4 (533030) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0677 | Single Phase Fault with Stuck Breaker on GEN-2017-226138.00 (760641) 138 kV Bus a. Apply Fault at the GEN-2017-226138.00 (760641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-226 (760641) 138.0 kV to G17-226XFMR1 (760642) 34.5 kV Two Winding #1 b.2. GEN-2017-226 (760641) 138.0 kV to G17-227XFMR1 (760662) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0678 | Single Phase Fault with Stuck Breaker on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply Fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKERDG4 (533053) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #1 b.2. LAKERDG4 (533053) 138.0 kV to HOOVERN4 (533049) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0679 | Single Phase Fault with Stuck Breaker on INTERST4 138.00 (533051) 138 kV Bus a. Apply Fault at the INTERST4 138.00 (533051) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTERST4 (533051) 138.0 kV to GILL E 4 (533044) 138.0 kV Transmission Circuit #1 b.2. INTERST4 (533051) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0680 | Single Phase Fault with Stuck Breaker on GEN-2022-004138.00 (767061) 138 kV Bus a. Apply Fault at the GEN-2022-004138.00 (767061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-004 (767061) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #1 b.2. GEN-2022-004 (767061) 138.0 kV to G22-004XFMR1 (767062) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0681 | Single Phase Fault with Stuck Breaker on 64TH 4 138.00 (533066) 138 kV Bus a. Apply Fault at the 64TH 4 138.00 (533066) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 64TH 4 (533066) 138.0 kV to 47TH ST4 (533058) 138.0 kV Transmission Circuit #1 b.2. 64TH 4 (533066) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0682 | Single Phase Fault with Stuck Breaker on SCRANTN3 115.00 (533173) 115 kV Bus a. Apply Fault at the SCRANTN3 115.00 (533173) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCRANTN3 (533173) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 b.2. SCRANTN3 (533173) 115.0 kV to 4CORNER3 (533158) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0683 | Single Phase Fault with Stuck Breaker on FLORENC3 115.00 (533366) 115 kV Bus a. Apply Fault at the FLORENC3 115.00 (533366) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLORENC3 (533366) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0684 | Single Phase Fault with Stuck Breaker on GREEN 2 69.000 (533636) 69 kV Bus a. Apply Fault at the GREEN 2 69.000 (533636) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREEN 2 (533636) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.2. GREEN 2 (533636) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0685 | Single Phase Fault with Stuck Breaker on MCKEE 2 69.000 (533640) 69 kV Bus a. Apply Fault at the MCKEE 2 69.000 (533640) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCKEE 2 (533640) 69.0 kV to MARMATN2 (533639) 69.0 kV Transmission Circuit #1 b.2. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0686 | Single Phase Fault with Stuck Breaker on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply Fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ZILAJCT2 (533654) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.2. ZILAJCT2 (533654) 69.0 kV to ALLEN 2 (533621) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0687 | Single Phase Fault with Stuck Breaker on PARSONS2 69.000 (533704) 69 kV Bus a. Apply Fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARSONS2 (533704) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 b.2. PARSONS2 (533704) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0688 | Single Phase Fault with Stuck Breaker on PECK 2 69.000 (533830) 69 kV Bus a. Apply Fault at the PECK 2 69.000 (533830) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECK 2 (533830) 69.0 kV to HAYSVJS2 (533802) 69.0 kV Transmission Circuit #1 b.2. PECK 2 (533830) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0689 | Single Phase Fault with Stuck Breaker on CANALN 2 69.000 (533790) 69 kV Bus a. Apply Fault at the CANALN 2 69.000 (533790) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALN 2 (533790) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #z1 b.2. CANALN 2 (533790) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0690 | Single Phase Fault with Stuck Breaker on RUTAN 2 69.000 (533838) 69 kV Bus a. Apply Fault at the RUTAN 2 69.000 (533838) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUTAN 2 (533838) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #1 b.2. RUTAN 2 (533838) 69.0 kV to GLENDAL2 (533797) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0691 | Single Phase Fault with Stuck Breaker on WESTLNK2 69.000 (533854) 69 kV Bus a. Apply Fault at the WESTLNK2 69.000 (533854) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTLNK2 (533854) 69.0 kV to COWSKIN2 (533788) 69.0 kV Transmission Circuit #1 b.2. WESTLNK2 (533854) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0692 | Single Phase Fault with Stuck Breaker on GODDTAP2 69.000 (533879) 69 kV Bus a. Apply Fault at the GODDTAP2 69.000 (533879) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GODDTAP2 (533879) 69.0 kV to COWSKIN2 (533788) 69.0 kV Transmission Circuit #1 b.2. GODDTAP2 (533879) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0693 | Single Phase Fault with Stuck Breaker on VULCTP 2 69.000 (533851) 69 kV Bus a. Apply Fault at the VULCTP 2 69.000 (533851) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VULCTP 2 (533851) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #1 b.2. VULCTP 2 (533851) 69.0 kV to LIN 2 (533812) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0694 | Single Phase Fault with Stuck Breaker on OATVILL2 69.000 (533825) 69 kV Bus a. Apply Fault at the OATVILL2 69.000 (533825) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OATVILL2 (533825) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. OATVILL2 (533825) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0695 | Single Phase Fault with Stuck Breaker on MIDLAND2 69.000 (533816) 69 kV Bus a. Apply Fault at the MIDLAND2 69.000 (533816) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDLAND2 (533816) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 b.2. MIDLAND2 (533816) 69.0 kV to HYDRJS2 (533810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0696 | Single Phase Fault with Stuck Breaker on VISTAPK2 69.000 (533849) 69 kV Bus a. Apply Fault at the VISTAPK2 69.000 (533849) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VISTAPK2 (533849) 69.0 kV to HOOVERN2 (533805) 69.0 kV Transmission Circuit #1 b.2. VISTAPK2 (533849) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0697 | Single Phase Fault with Stuck Breaker on WATER1 2 69.000 (533855) 69 kV Bus a. Apply Fault at the WATER1 2 69.000 (533855) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATER1 2 (533855) 69.0 kV to HOOVERN2 (533805) 69.0 kV Transmission Circuit #1 b.2. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0698 | Single Phase Fault with Stuck Breaker on TYLER 2 69.000 (533847) 69 kV Bus a. Apply Fault at the TYLER 2 69.000 (533847) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. TYLER 2 (533847) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0699 | Single Phase Fault with Stuck Breaker on WATER2 2 69.000 (533856) 69 kV Bus a. Apply Fault at the WATER2 2 69.000 (533856) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATER2 2 (533856) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 b.2. WATER2 2 (533856) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0700 | Single Phase Fault with Stuck Breaker on SG8CRAG2 69.000 (533873) 69 kV Bus a. Apply Fault at the SG8CRAG2 69.000 (533873) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SG8CRAG2 (533873) 69.0 kV to LIN 2 (533812) 69.0 kV Transmission Circuit #1 b.2. SG8CRAG2 (533873) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0701 | Single Phase Fault with Stuck Breaker on SENECA 2 69.000 (533839) 69 kV Bus a. Apply Fault at the SENECA 2 69.000 (533839) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SENECA 2 (533839) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.2. SENECA 2 (533839) 69.0 kV to OSAGE 2 (533827) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0702 | Single Phase Fault with Stuck Breaker on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply Fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROLLHLS3 (539643) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0703 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUSSELL3 (539701) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. RUSSELL3 (539701) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0704 | Single Phase Fault with Stuck Breaker on 2ND-KS 3 115.00 (539689) 115 kV Bus a. Apply Fault at the 2ND-KS 3 115.00 (539689) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ND-KS 3 (539689) 115.0 kV to 24-FREY3 (539661) 115.0 kV Transmission Circuit #1 b.2. 2ND-KS 3 (539689) 115.0 kV to GBENDTP3 (539666) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0705 | Single Phase Fault with Stuck Breaker on SSTARTP3 115.00 (539763) 115 kV Bus a. Apply Fault at the SSTARTP3 115.00 (539763) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SSTARTP3 (539763) 115.0 kV to GRNBURG3 (539664) 115.0 kV Transmission Circuit #1 b.2. SSTARTP3 (539763) 115.0 kV to FORD 3 (539758) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0706 | Single Phase Fault with Stuck Breaker on GEN-2019-044115.00 (763758) 115 kV Bus a. Apply Fault at the GEN-2019-044115.00 (763758) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-044 (763758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.2. GEN-2019-044 (763758) 115.0 kV to G19-044-XFM1 (763759) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0707 | Single Phase Fault with Stuck Breaker on GEN-2011-008345.00 (539840) 345 kV Bus a. Apply Fault at the GEN-2011-008345.00 (539840) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2011-008 (539840) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. GEN-2011-008 (539840) 345.0 kV to G-2011-008-3 (539857) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0708 | Single Phase Fault with Stuck Breaker on GEN-2019-058345.00 (763890) 345 kV Bus a. Apply Fault at the GEN-2019-058345.00 (763890) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-058 (763890) 345.0 kV to G19-058-XFM1 (763891) 34.5 kV Two Winding #1 b.2. GEN-2019-058 (763890) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0709 | Single Phase Fault with Stuck Breaker on GEN-2008-124345.00 (579480) 345 kV Bus a. Apply Fault at the GEN-2008-124345.00 (579480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2008-124 (579480) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. GEN-2008-124 (579480) 345.0 kV to G08-124XFMR1 (579481) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0710 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0711 | Single Phase Fault with Stuck Breaker on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply Fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCONGRS5 (541318) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 b.2. NCONGRS5 (541318) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0712 | Single Phase Fault with Stuck Breaker on WESTON 5 161.00 (541351) 161 kV Bus a. Apply Fault at the WESTON 5 161.00 (541351) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTON 5 (541351) 161.0 kV to IATAN5 (541350) 161.0 kV Transmission Circuit #1 b.2. WESTON 5 (541351) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0713 | Single Phase Fault with Stuck Breaker on OAKGRV 5 161.00 (541227) 161 kV Bus a. Apply Fault at the OAKGRV 5 161.00 (541227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKGRV 5 (541227) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 b.2. OAKGRV 5 (541227) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0714 | Single Phase Fault with Stuck Breaker on TIFFANY5 161.00 (543026) 161 kV Bus a. Apply Fault at the TIFFANY5 161.00 (543026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIFFANY5 (543026) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. TIFFANY5 (543026) 161.0 kV to WETHRBY5 (543017) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0715 | Single Phase Fault with Stuck Breaker on FRSTCRK5 161.00 (543039) 161 kV Bus a. Apply Fault at the FRSTCRK5 161.00 (543039) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRSTCRK5 (543039) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. FRSTCRK5 (543039) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0716 | Single Phase Fault with Stuck Breaker on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply Fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0717 | Single Phase Fault with Stuck Breaker on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply Fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LKWOOD 5 (541238) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 b.2. LKWOOD 5 (541238) 161.0 kV to RAYTOWN5 (541219) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0718 | Single Phase Fault with Stuck Breaker on NUCOR5 161.00 (541395) 161 kV Bus a. Apply Fault at the NUCOR5 161.00 (541395) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUCOR5 (541395) 161.0 kV to NUCOR_D1 (541396) 13.8 kV Two Winding #1 b.2. NUCOR5 (541395) 161.0 kV to NUCOR_S1 (541398) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0719 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0720 | Single Phase Fault with Stuck Breaker on WARSAWTP 69.000 (541281) 69 kV Bus a. Apply Fault at the WARSAWTP 69.000 (541281) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARSAWTP (541281) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 b.2. WARSAWTP (541281) 69.0 kV to WARSAW 2 (541277) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0721 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0722 | Single Phase Fault with Stuck Breaker on GEN-2017-195345.00 (762279) 345 kV Bus a. Apply Fault at the GEN-2017-195345.00 (762279) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-195 (762279) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-195 (762279) 345.0 kV to G17-195XFM1 (762280) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0723 | Single Phase Fault with Stuck Breaker on HICKMAN5 161.00 (542994) 161 kV Bus a. Apply Fault at the HICKMAN5 161.00 (542994) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HICKMAN5 (542994) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. HICKMAN5 (542994) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0724 | Single Phase Fault with Stuck Breaker on ANTIOCH5 161.00 (543050) 161 kV Bus a. Apply Fault at the ANTIOCH5 161.00 (543050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. ANTIOCH5 (543050) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0725 | Single Phase Fault with Stuck Breaker on REDEL 5 161.00 (543053) 161 kV Bus a. Apply Fault at the REDEL 5 161.00 (543053) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDEL 5 (543053) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. REDEL 5 (543053) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0726 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0727 | Single Phase Fault with Stuck Breaker on G17-108-TAP 161.00 (761278) 161 kV Bus a. Apply Fault at the G17-108-TAP 161.00 (761278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-108-TAP (761278) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. G17-108-TAP (761278) 161.0 kV to GEN-2021-050 (765750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0728 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #z2 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0729 | Single Phase Fault with Stuck Breaker on G20-007-TAP 345.00 (766261) 345 kV Bus a. Apply Fault at the G20-007-TAP 345.00 (766261) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0730 | Single Phase Fault with Stuck Breaker on TERRACE5 161.00 (542991) 161 kV Bus a. Apply Fault at the TERRACE5 161.00 (542991) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0731 | Single Phase Fault with Stuck Breaker on FOREST 5 161.00 (543001) 161 kV Bus a. Apply Fault at the FOREST 5 161.00 (543001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOREST 5 (543001) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. FOREST 5 (543001) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0732 | Single Phase Fault with Stuck Breaker on ROEPARK5 161.00 (543040) 161 kV Bus a. Apply Fault at the ROEPARK5 161.00 (543040) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROEPARK5 (543040) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 b.2. ROEPARK5 (543040) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0733 | Single Phase Fault with Stuck Breaker on WINJT N5 161.00 (543009) 161 kV Bus a. Apply Fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT N5 (543009) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT N5 (543009) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0734 | Single Phase Fault with Stuck Breaker on WINJT S5 161.00 (543010) 161 kV Bus a. Apply Fault at the WINJT S5 161.00 (543010) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT S5 (543010) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT S5 (543010) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0735 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NKANCTY5 (543018) 161.0 kV to AVONDAL5 (543015) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0736 | Single Phase Fault with Stuck Breaker on LINECRK5 161.00 (543025) 161 kV Bus a. Apply Fault at the LINECRK5 161.00 (543025) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LINECRK5 (543025) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 b.2. LINECRK5 (543025) 161.0 kV to RIVRSID5 (543021) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0737 | Single Phase Fault with Stuck Breaker on GEN-2022-073161.00 (768441) 161 kV Bus a. Apply Fault at the GEN-2022-073161.00 (768441) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-073 (768441) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. GEN-2022-073 (768441) 161.0 kV to G22-073XFMR1 (768442) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0738 | Single Phase Fault with Stuck Breaker on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply Fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTY 2 (543092) 69.0 kV to LAKCTYJ2 (543087) 69.0 kV Transmission Circuit #1 b.2. LAKCTY 2 (543092) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0739 | Single Phase Fault with Stuck Breaker on LAKCTYK2 69.000 (543093) 69 kV Bus a. Apply Fault at the LAKCTYK2 69.000 (543093) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYK2 (543093) 69.0 kV to DUNCNRD2 (543091) 69.0 kV Transmission Circuit #1 b.2. LAKCTYK2 (543093) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0740 | Single Phase Fault with Stuck Breaker on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply Fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 b.2. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0741 | Single Phase Fault with Stuck Breaker on GAT258 2 69.000 (547551) 69 kV Bus a. Apply Fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GAT258 2 (547551) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 b.2. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0742 | Single Phase Fault with Stuck Breaker on JOP430 2 69.000 (547608) 69 kV Bus a. Apply Fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP430 2 (547608) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 b.2. JOP430 2 (547608) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0743 | Single Phase Fault with Stuck Breaker on GAL278T 69.000 (547728) 69 kV Bus a. Apply Fault at the GAL278T 69.000 (547728) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GAL278T (547728) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 b.2. GAL278T (547728) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0744 | Single Phase Fault with Stuck Breaker on RIV406 2 69.000 (547602) 69 kV Bus a. Apply Fault at the RIV406 2 69.000 (547602) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV406 2 (547602) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. RIV406 2 (547602) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0745 | Single Phase Fault with Stuck Breaker on SUB P 69.000 (548827) 69 kV Bus a. Apply Fault at the SUB P 69.000 (548827) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB P (548827) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB P (548827) 69.0 kV to SUB I (548800) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0746 | Single Phase Fault with Stuck Breaker on SUB R 69.000 (548830) 69 kV Bus a. Apply Fault at the SUB R 69.000 (548830) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB R (548830) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SUB R (548830) 69.0 kV to SUB K (548801) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0747 | Single Phase Fault with Stuck Breaker on GEN-2018-031161.00 (762669) 161 kV Bus a. Apply Fault at the GEN-2018-031161.00 (762669) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-031 (762669) 161.0 kV to G18-031XFM1 (762670) 34.5 kV Two Winding #1 b.2. GEN-2018-031 (762669) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0748 | Single Phase Fault with Stuck Breaker on G15052_1 345.00 (562900) 345 kV Bus a. Apply Fault at the G15052_1 345.00 (562900) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15052_1 (562900) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. G15052_1 (562900) 345.0 kV to G15052_2 (562901) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0749 | Single Phase Fault with Stuck Breaker on GEN-2016-046345.00 (587310) 345 kV Bus a. Apply Fault at the GEN-2016-046345.00 (587310) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-046 (587310) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-046 (587310) 345.0 kV to G16-046XFMR1 (587311) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0750 | Single Phase Fault with Stuck Breaker on GEN-2016-050345.00 (587350) 345 kV Bus a. Apply Fault at the GEN-2016-050345.00 (587350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-050 (587350) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-050 (587350) 345.0 kV to G16-050XFMR1 (587351) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0751 | Single Phase Fault with Stuck Breaker on GEN-2017-086345.00 (589240) 345 kV Bus a. Apply Fault at the GEN-2017-086345.00 (589240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-086 (589240) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-086 (589240) 345.0 kV to G17-086XFMR1 (589241) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0752 | Single Phase Fault with Stuck Breaker on GEN-2020-011345.00 (764420) 345 kV Bus a. Apply Fault at the GEN-2020-011345.00 (764420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-011 (764420) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-011 (764420) 345.0 kV to G20-011-SS3 (764433) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0753 | Single Phase Fault with Stuck Breaker on G18-125-TAP 345.00 (763410) 345 kV Bus a. Apply Fault at the G18-125-TAP 345.00 (763410) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0754 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0755 | Single Phase Fault with Stuck Breaker on GEN-2022-054345.00 (768061) 345 kV Bus a. Apply Fault at the GEN-2022-054345.00 (768061) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-054 (768061) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-054 (768061) 345.0 kV to G22-054XFMR1 (768062) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0756 | Single Phase Fault with Stuck Breaker on GEN-2021-030345.00 (765580) 345 kV Bus a. Apply Fault at the GEN-2021-030345.00 (765580) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-030 (765580) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-030 (765580) 345.0 kV to G21-030-XFM1 (765584) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0757 | Single Phase Fault with Stuck Breaker on GEN-2021-069345.00 (765920) 345 kV Bus a. Apply Fault at the GEN-2021-069345.00 (765920) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-069 (765920) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-069 (765920) 345.0 kV to G21-069-XFM1 (765924) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0758 | Single Phase Fault with Stuck Breaker on GEN-2021-070345.00 (765930) 345 kV Bus a. Apply Fault at the GEN-2021-070345.00 (765930) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-070 (765930) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-070 (765930) 345.0 kV to G21-070-XFM1 (765934) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0759 | Single Phase Fault with Stuck Breaker on GEN-2022-007115.00 (767121) 115 kV Bus a. Apply Fault at the GEN-2022-007115.00 (767121) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-007 (767121) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 b.2. GEN-2022-007 (767121) 115.0 kV to G22-007XFMR1 (767122) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0760 | Single Phase Fault with Stuck Breaker on GEN-2022-013345.00 (767241) 345 kV Bus a. Apply Fault at the GEN-2022-013345.00 (767241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-013 (767241) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-013 (767241) 345.0 kV to G22-013XFMR1 (767242) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0761 | Single Phase Fault with Stuck Breaker on GEN-2022-015345.00 (767281) 345 kV Bus a. Apply Fault at the GEN-2022-015345.00 (767281) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-015 (767281) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-015 (767281) 345.0 kV to G22-015XFMR1 (767282) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0762 | Single Phase Fault with Stuck Breaker on GEN-2022-065230.00 (768281) 230 kV Bus a. Apply Fault at the GEN-2022-065230.00 (768281) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-065 (768281) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. GEN-2022-065 (768281) 230.0 kV to G22-065XFMR1 (768282) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0763 | Single Phase Fault with Stuck Breaker on GEN-2022-075345.00 (768481) 345 kV Bus a. Apply Fault at the GEN-2022-075345.00 (768481) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-075 (768481) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-075 (768481) 345.0 kV to G22-075XFMR1 (768482) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0764 | Single Phase Fault with Stuck Breaker on GEN-2022-214138.00 (771261) 138 kV Bus a. Apply Fault at the GEN-2022-214138.00 (771261) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-214 (771261) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 b.2. GEN-2022-214 (771261) 138.0 kV to G22-214XFMR1 (771262) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0765 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0766 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0767 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.2. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0768 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0769 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 7 (531465) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0770 | Single Phase Fault with Stuck Breaker on JEC 6 230.00 (532852) 230 kV Bus a. Apply Fault at the JEC 6 230.00 (532852) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0771 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to RENO 7 (532771) 345.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 b.2. RENO 3 (533416) 115.0 kV to RENO 7 (532771) 345.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0772 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR3 (533268) 115.0 kV to STRANGR7 (532772) 345.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR3 (533268) 115.0 kV to STRANGR7 (532772) 345.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0773 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0774 | Single Phase Fault with Stuck Breaker on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0775 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK3 (533315) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #2 b.2. OTTRCRK3 (533315) 115.0 kV to OTTRCRK4 (532997) 138.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0776 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASO 2 (533793) 69.0 kV to ELPASOE4 (533059) 138.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 b.2. ELPASO 2 (533793) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0777 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0778 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0779 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to PHILL 7 (541200) 345.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0780 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 5 (541202) 161.0 kV to SIBLEY 7 (541201) 345.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0781 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0782 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0783 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. WGARDNR5 (542966) 161.0 kV to W.GRDNR7 (542965) 345.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0784 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTH 7 (542972) 345.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTHN5 (543665) 161.0 kV to HAWTH 7 (542972) 345.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0785 | Single Phase Fault with Stuck Breaker on LAC3_STAR7 345.00 (543667) 345 kV Bus a. Apply Fault at the LAC3_STAR7 345.00 (543667) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC3_STAR7 (543667) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h b.2. LAC3_STAR7 (543667) 345.0 kV to LAC3_Y1 (543662) 6.9 kV Two Winding #y | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0786 | Single Phase Fault with Stuck Breaker on LAC8_STAR7 345.00 (543669) 345 kV Bus a. Apply Fault at the LAC8_STAR7 345.00 (543669) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC8_STAR7 (543669) 345.0 kV to LAC8_Z1 (543672) 4.0 kV Two Winding #z b.2. LAC8_STAR7 (543669) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0787 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 2 (547534) 69.0 kV to ORO110 5 (547467) 161.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 b.2. ORO110 2 (547534) 69.0 kV to WEB436 2 (547527) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0788 | Single Phase Fault with Stuck Breaker on JOP389 2 69.000 (547592) 69 kV Bus a. Apply Fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 b.2. JOP389 2 (547592) 69.0 kV to EXP449T2 (547438) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0789 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 4 (547486) 138.0 kV to VINTAJC4 (510417) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0790 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 2 (547601) 69.0 kV to HOC404 5 (547487) 161.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 b.2. HOC404 2 (547601) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0791 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.2. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0792 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 b.2. KEYSTON3 (640252) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0793 | Single Phase Fault with Stuck Breaker on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply Fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STOCKVL7 (640365) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. STOCKVL7 (640365) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0794 | Single Phase Fault with Stuck Breaker on GILL E 2 (533795) 69 kV Bus a. Apply Fault at the GILL E 2 (533795) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0795 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0796 | Single Phase Fault with Stuck Breaker on GILL W 2 (533796) 69 kV Bus a. Apply Fault at the GILL W 2 (533796) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL W 2 (533796) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0797 | Single Phase Fault with Stuck Breaker on HOOVERS2 (533806) 69 kV Bus a. Apply Fault at the HOOVERS2 (533806) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HOOVERS2 (533806) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0798 | Single Phase Fault with Stuck Breaker on GILL E 4 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 (533044) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0799 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0800 | Single Phase Fault with Stuck Breaker on HOOVERN4 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 (533049) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0801 | Single Phase Fault with Stuck Breaker on ALTOO E2 (533673) 69 kV Bus a. Apply Fault at the ALTOO E2 (533673) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. ALTOO E2 (533673) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0802 | Single Phase Fault with Stuck Breaker on NEOSHON2 (533768) 69 kV Bus a. Apply Fault at the NEOSHON2 (533768) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHON2 (533768) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0803 | Single Phase Fault with Stuck Breaker on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0804 | Single Phase Fault with Stuck Breaker on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0805 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0806 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0807 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0808 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0809 | Single Phase Fault with Stuck Breaker on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0810 | Single Phase Fault with Stuck Breaker on OSAGE J3 (533171) 115 kV Bus a. Apply Fault at the OSAGE J3 (533171) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. OSAGE J3 (533171) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0811 | Single Phase Fault with Stuck Breaker on WEMPORI3 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 (533309) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0812 | Single Phase Fault with Stuck Breaker on MORRIS 7 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 (532770) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MORRIS 7 (532770) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0813 | Single Phase Fault with Stuck Breaker on STILWEL5 (542969) 161 kV Bus a. Apply Fault at the STILWEL5 (542969) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0814 | Single Phase Fault with Stuck Breaker on REDWILO7 (640326) 115 kV Bus a. Apply Fault at the REDWILO7 (640326) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0815 | Single Phase Fault with Stuck Breaker on GENTLMN4 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 (640184) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0816 | Single Phase Fault with Stuck Breaker on SETAB 3 (531464) 115 kV Bus a. Apply Fault at the SETAB 3 (531464) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SETAB 3 (531464) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0817 | Single Phase Fault with Stuck Breaker on MINGO 3 (531429) 115 kV Bus a. Apply Fault at the MINGO 3 (531429) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0818 | Single Phase Fault with Stuck Breaker on SPEARVL3 (539694) 115 kV Bus a. Apply Fault at the SPEARVL3 (539694) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SPEARVL3 (539694) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0819 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0820 | Single Phase Fault with Stuck Breaker on NFTDODG3 (539771) 115 kV Bus a. Apply Fault at the NFTDODG3 (539771) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NFTDODG3 (539771) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0821 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0822 | Single Phase Fault with Stuck Breaker on NASHUA 5 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 (541203) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0823 | Single Phase Fault with Stuck Breaker on PLTCTY 5 (541221) 161 kV Bus a. Apply Fault at the PLTCTY 5 (541221) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. PLTCTY 5 (541221) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0824 | Single Phase Fault with Stuck Breaker on GLADSTN5 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 (543016) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0825 | Single Phase Fault with Stuck Breaker on TWA 5 (541214) 161 kV Bus a. Apply Fault at the TWA 5 (541214) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0826 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0827 | Single Phase Fault with Stuck Breaker on SEDN 2 (541271) 69 kV Bus a. Apply Fault at the SEDN 2 (541271) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SEDN 2 (541271) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0828 | Single Phase Fault with Stuck Breaker on SEDPLT 2 (541275) 69 kV Bus a. Apply Fault at the SEDPLT 2 (541275) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SEDPLT 2 (541275) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0829 | Single Phase Fault with Stuck Breaker on 5GEORGE (300082) 161 kV Bus a. Apply Fault at the 5GEORGE (300082) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0830 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 (344234) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. 5CALIF UE 2 (344234) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0831 | Single Phase Fault with Stuck Breaker on 5MCBAIN T (345071) 161 kV Bus a. Apply Fault at the 5MCBAIN T (345071) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. 5MCBAIN T (345071) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0832 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0833 | Single Phase Fault with Stuck Breaker on FRSTCRK5 (543039) 161 kV Bus a. Apply Fault at the FRSTCRK5 (543039) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. FRSTCRK5 (543039) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0834 | Single Phase Fault with Stuck Breaker on SMTHVL 5 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 (541204) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0835 | Single Phase Fault with Stuck Breaker on BLSPE 5 (541205) 161 kV Bus a. Apply Fault at the BLSPE 5 (541205) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BLSPE 5 (541205) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0836 | Single Phase Fault with Stuck Breaker on NEASTS5 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 (542985) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0837 | Single Phase Fault with Stuck Breaker on GRAND W5 (542988) 161 kV Bus a. Apply Fault at the GRAND W5 (542988) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GRAND W5 (542988) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0838 | Single Phase Fault with Stuck Breaker on NAVY 5 (542989) 161 kV Bus a. Apply Fault at the NAVY 5 (542989) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NAVY 5 (542989) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0839 | Single Phase Fault with Stuck Breaker on AVONDAL5 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 (543015) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0840 | Single Phase Fault with Stuck Breaker on SUB J (548811) 69 kV Bus a. Apply Fault at the SUB J (548811) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SUB J (548811) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0841 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0842 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0843 | Single Phase Fault with Stuck Breaker on LANG 3 (533304) 115 kV Bus a. Apply Fault at the LANG 3 (533304) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. LANG 3 (533304) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0844 | Single Phase Fault with Stuck Breaker on EVANS N4 (533040) 138 kV Bus a. Apply Fault at the EVANS N4 (533040) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0845 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0846 | Single Phase Fault with Stuck Breaker on MILAN_GOAB (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB (539008) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0847 | Single Phase Fault with Stuck Breaker on SUMNER 4 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 (532984) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0848 | Single Phase Fault with Stuck Breaker on GILL W 4 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 (533045) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL W 4 (533045) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0849 | Single Phase Fault with Stuck Breaker on GILL S 4 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 (533046) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL S 4 (533046) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0012 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0013 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0015 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0016 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0017 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0018 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0019 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0020 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0021 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0022 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0023 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0024 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0025 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0026 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0027 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0028 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0029 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0030 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0031 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0032 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0033 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0034 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0035 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0036 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0037 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0038 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0039 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0040 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0041 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0042 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0043 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0044 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0045 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0046 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0047 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0001 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0002 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0003 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0004 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA17-1 (512688) 22.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0005 | Single Phase Fault with Stuck Breaker on GREC TAP7 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 (512865) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRECSTG_1 (512615) 21.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0006 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0007 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0008 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0009 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_OKGE_FAULT_0001 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.3. KAYWNDG1 (515651) 0.7 kV to Generator #1 b.4. KAYWNDG2 (515652) 0.7 kV to Generator #1 b.5. KAYWND11 (515622) 34.5 kV to Load #S1 b.6. KAYWND12 (515623) 34.5 kV to Load #S1 b.7. KAYWIND7 (514825) 345.0 kV to remove bus # b.8. KAYWNDT1 (515619) 12.5 kV to remove bus # b.9. KAYWNDT2 (515620) 12.5 kV to remove bus # b.10. OPENSKY7 (515621) 345.0 kV to remove bus # b.11. KAYWND11 (515622) 34.5 kV to remove bus # b.12. KAYWND12 (515623) 34.5 kV to remove bus # b.13. KAYWNDG1 (515651) 0.7 kV to remove bus # b.14. KAYWNDG2 (515652) 0.7 kV to remove bus # b.15. KAYWNDC1 (515653) 34.5 kV to remove bus # b.16. KAYWNDC2 (515654) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_SPS_FAULT_0001 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DUNES23 (523061) 0.7 kV to Generator #1 b.12. BUFF_DUNES13 (523062) 0.7 kV to Generator #1 b.13. BUFF_DUNES23 (523061) 0.7 kV to remove bus # b.14. BUFF_DUNES13 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNES22 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNES12 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_KACY_FAULT_0001 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_KACY_FAULT_0002 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.3. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 b.4. SHAWNEE5 (543041) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.5. SHAWNEE5 (543041) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_KACY_FAULT_0003 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EDE_FAULT_0001 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.3. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. JOP389 5 (547483) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.7. TIP292 5 (547472) 161.0 kV to Load #1 b.8. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EDE_FAULT_0002 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 7 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Breaker at To Bus #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EDE_FAULT_0003 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 b.3. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EDE_FAULT_0004 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.3. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.6. TIP292 5 (547472) 161.0 kV to Load #1 b.7. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_NPPD_FAULT_0001 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_NPPD_FAULT_0002 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_NPPD_FAULT_0003 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.4. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_NPPD_FAULT_0004 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_SUNC_FAULT_0001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_0001 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_0002 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_0003 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_0004 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_0005 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_0006 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_0007 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_0008 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_0009 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_INDN_FAULT_0010 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0001 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.4. CLBYT1 1 (530645) 13.8 kV to remove bus # b.5. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Load #99 b.12. COLBY 3 (530555) 115.0 kV to Generator #C8 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0002 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. CLBYT1 1 (530645) 13.8 kV to remove bus # b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Generator #C8 b.12. COLBY 3 (530555) 115.0 kV to Load #99 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0003 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0004 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0005 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0006 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.4. GMECG1 1 (530674) 13.8 kV to remove bus # b.5. GMECG2 1 (530675) 13.8 kV to remove bus # b.6. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0007 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMECG1 1 (530674) 13.8 kV to remove bus # b.3. GMECG2 1 (530675) 13.8 kV to remove bus # b.5. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.6. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.7. N HAYS3 (530581) 115.0 kV to remove bus # b.8. VINETAP3 (530693) 115.0 kV to remove bus # b.9. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0008 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to remove bus # b.4. VINETAP3 (530693) 115.0 kV to remove bus # b.5. GMECG1 1 (530674) 13.8 kV to remove bus # b.6. GMECG2 1 (530675) 13.8 kV to remove bus # b.7. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0009 | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 (530553) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. ANGUS 3 (530714) 115.0 kV to GORHAM 3 (530552) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.5. ANGUS 3 (530714) 115.0 kV to Load #1 b.6. PFEIFER 3 (530725) 115.0 kV to Load #1 b.7. ANGUS 3 (530714) 115.0 kV to remove bus # b.8. PFEIFER 3 (530725) 115.0 kV to remove bus # b.9. GORHAM 3 (530552) 115.0 kV to Load #1 b.10. RUSLPMP3 (530684) 115.0 kV to Load #1 b.11. GORHAM 3 (530552) 115.0 kV to remove bus # b.12. RUSLPMP3 (530684) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0010 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0011 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0012 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0013 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0014 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0015 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.4. BUCKE_WTG (530705) 0.7 kV to remove bus # b.5. BUCKW_WTG (530708) 0.7 kV to remove bus # b.6. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.7. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.8. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.9. BUCKW_TERT (530706) 13.8 kV to remove bus # b.10. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.11. BUCKE_TERT (530709) 13.8 kV to remove bus # b.12. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0016 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0017 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0018 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0019 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0020 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0021 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0022 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0023 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0024 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. SMOKYHL6 (530592) 230.0 kV to SMKYP2 6 (530599) 230.0 kV Transmission Circuit #1 b.4. SHG2 34 1 (530715) 34.5 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus # b.6. SMKYP2 6 (530599) 230.0 kV to remove bus # b.7. SHP234 1 (530604) 34.5 kV to remove bus # b.8. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0025 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 38 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus # b.3. SMKYP1 6 (530593) 230.0 kV to remove bus # b.4. SMKYP1G1 (530594) 0.7 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus # b.6. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0026 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.3. SMKYT2 1 (530634) 13.9 kV to Generator #1 b.4. SMKYT2 1 (530634) 13.9 kV to remove bus # b.5. SMKYP1G1 (530594) 0.7 kV to remove bus # b.6. SMKYP1 6 (530593) 230.0 kV to remove bus # b.7. SHP134 1 (530595) 34.5 kV to remove bus # b.8. SMKYT1 1 (530633) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0027 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus # b.3. SMKYP1 6 (530593) 230.0 kV to remove bus # b.4. SMKYP1G1 (530594) 0.7 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0028 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0029 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0030 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0031 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0032 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.3. LACROS 3 (530603) 115.0 kV to remove bus # b.4. NEKOMA 3 (530608) 115.0 kV to remove bus # b.5. ALXNDR 3 (530606) 115.0 kV to remove bus # b.7. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.8. HZRNGPL3 (530609) 115.0 kV to remove bus # b.9. ALEXNDR1 (539702) 34.5 kV to Load #1 b.10. LAXTAP 3 (530602) 115.0 kV to remove bus # b.11. NKMA2 1 (530630) 12.5 kV to remove bus # b.12. ALEXNDR1 (539702) 34.5 kV to remove bus # b.13. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0033 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0034 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.4. LACROS 3 (530603) 115.0 kV to remove bus # b.5. NEKOMA 3 (530608) 115.0 kV to remove bus # b.6. ALXNDR 3 (530606) 115.0 kV to remove bus # b.8. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.9. ALEXNDR1 (539702) 34.5 kV to Load #1 b.10. LAXTAP 3 (530602) 115.0 kV to remove bus # b.11. NKMA2 1 (530630) 12.5 kV to remove bus # b.12. ALEXNDR1 (539702) 34.5 kV to remove bus # b.13. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0035 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0036 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 6 (530686) 230.0 kV to remove bus # b.3. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. PRWINDG1 (530690) 0.7 kV to Generator #1 b.6. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.7. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.8. PRWINDG1 (530690) 0.7 kV to remove bus # b.9. BUFCRKT11 (530691) 12.5 kV to remove bus # b.10. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0037 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0038 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0039 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. COLBY 3 (530555) 115.0 kV to remove bus # b.6. CLBYT1 1 (530645) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0040 | Single Phase Fault with Stuck Breaker on BEACH 3 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 (530557) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HOXIE 3 (530556) 115.0 kV Transmission Circuit #1 b.5. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.6. BEACH 3 (530557) 115.0 kV to remove bus # b.7. HILLCTY3 (531387) 34.5 kV to Generator #1 b.8. HILLCTY3 (531387) 34.5 kV to Generator #2 b.9. HILLCTY3 (531387) 34.5 kV to Generator #3 b.10. HILLCTY3 (531387) 34.5 kV to Generator #4 b.11. HILLCTY3 (531387) 34.5 kV to Generator #5 b.12. HILLCTY3 (531387) 34.5 kV to Generator #6 b.13. HILLCTY3 (531387) 34.5 kV to remove bus # b.14. REDLIN 3 (530605) 115.0 kV to remove bus # b.15. HOXIE 3 (530556) 115.0 kV to remove bus # b.16. REDLIN 3 (530605) 115.0 kV to Load #71 b.17. HOXIE 3 (530556) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0041 | Single Phase Fault with Stuck Breaker on ATWOOD 3 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 (530554) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to remove bus # b.5. ATWOOD 3 (530554) 115.0 kV to Generator #1 b.6. HILLCTY3 (531387) 34.5 kV to Generator #1 b.7. HILLCTY3 (531387) 34.5 kV to Generator #2 b.8. HILLCTY3 (531387) 34.5 kV to Generator #3 b.9. HILLCTY3 (531387) 34.5 kV to Generator #4 b.10. HILLCTY3 (531387) 34.5 kV to Generator #5 b.11. HILLCTY3 (531387) 34.5 kV to Generator #6 b.12. ATWOOD 3 (530554) 115.0 kV to Load #1 b.13. ATWOOD 3 (530554) 115.0 kV to Load #41 b.14. ATWOOD 3 (530554) 115.0 kV to remove bus # b.15. HILLCTY3 (531387) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0042 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0001 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.2. JEC U1 (532651) 26.0 kV to remove bus # b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0002 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.2. JEC U2 (532652) 26.0 kV to remove bus # b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0003 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.2. JEC U3 (532653) 26.0 kV to remove bus # b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0004 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0005 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0006 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0007 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #1 b.4. EMPEC121 (532740) 13.8 kV to Generator #2 b.5. EMPEC121 (532740) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0008 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.2. EMPEC121 (532740) 13.8 kV to Generator #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #2 b.4. EMPEC121 (532740) 13.8 kV to remove bus # b.5. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0009 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0010 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.2. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.3. EMPEC7 1 (532744) 18.0 kV to remove bus # b.4. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0011 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0012 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0013 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0014 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0015 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0016 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0017 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0018 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0019 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0020 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0021 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0022 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0023 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0024 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0025 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0026 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0027 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0028 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to remove bus # b.4. RANDLPH5 (543027) 161.0 kV to Load #1 b.5. RANDLPH5 (543027) 161.0 kV to Load #4 b.6. RANDLPH5 (543027) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0029 | Single Phase Fault with Stuck Breaker on Hawthorn South (542973) 161 kV Bus a. Apply Fault at the Hawthorn South (542973) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0030 | Single Phase Fault with Stuck Breaker on Hawthorn 161 kV (542973) 161 kV Bus a. Apply Fault at the Hawthorn 161 kV (542973) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@1 b.2. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0031 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0032 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0033 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0034 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0035 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0036 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. IAT G1 1 (542957) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0037 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0038 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0039 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0040 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. LAC G2 1 (542956) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0041 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0042 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 b.4. NEASTN5 (543666) 161.0 kV to Load #78 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0043 | Single Phase Fault with Stuck Breaker on Stilwell 345 kV (542968) 345 kV Bus a. Apply Fault at the Stilwell 345 kV (542968) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0044 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0045 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0046 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to JEC N 7 (532766) 345.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0047 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0048 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0049 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0050 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0051 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0052 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0053 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0054 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 5.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0055 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0056 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0057 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0058 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0059 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0060 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0061 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0062 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0063 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0064 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0065 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0066 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0067 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0068 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0069 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0070 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0071 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0072 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@1 b.2. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0073 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0074 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0075 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0076 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0077 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IAT G1 1 (542957) 24.0 kV to remove bus # b.2. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0078 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to remove bus # b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0079 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 b.3. LACYGNE2 (543659) 69.0 kV to remove bus # b.4. LAC_LAKE_2 (541541) 69.0 kV to remove bus # b.5. LAC_LAKE_2 (541541) 69.0 kV to Load #K1 b.6. LAC_LAKE_2 (541541) 69.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0080 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0081 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0082 | Single Phase Fault with Stuck Breaker on Northeast North (543666) 161 kV Bus a. Apply Fault at the Northeast North (543666) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NEASTN5 (543666) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to remove bus # b.4. NE CT14 (542971) 13.8 kV to remove bus # b.5. NEASTN5 (543666) 161.0 kV to Load #56 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0083 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NE CT17 (542983) 13.8 kV to remove bus # b.2. NE CT18 (542984) 13.8 kV to remove bus # b.3. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.4. NEASTS5 (542985) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 b.5. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 b.6. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0084 | Single Phase Fault with Stuck Breaker on Stilwell 345 kV (542968) 345 kV Bus a. Apply Fault at the Stilwell 345 kV (542968) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0085 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0086 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0087 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Base | GROUP3_P1_LOCAL_FAULT_0779 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 4.75 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 4.75 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25S | Base | GROUP3_P1_LOCAL_FAULT_0911 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | The Grand Prairie Wind Units (645065, 645066, 645067 and 645068) become unstable following the fault clearance and protection trips the units. Reducing the critical clearing time to 2.7 cycles mitigates the issue. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
03 CENTRAL | DISIS-2022-001 | 25S | Base | GROUP3_P4_LOCAL_FAULT_0067 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_0779 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 4.75 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 4.75 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 | 25W | Base | GROUP3_P1_LOCAL_FAULT_0911 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | The Grand Prairie Wind Units (645065, 645066, 645067 and 645068) become unstable following the fault clearance and protection trips the units. Reducing the critical clearing time to 3.0 cycles mitigates the issue. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
03 CENTRAL | DISIS-2022-001 | 25W | Base | GROUP3_P4_LOCAL_FAULT_0067 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0001 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0002 | 3 Phase fault on 5ELDON 1 161.00 (344532) 161 kV Bus a. Apply fault at the 5ELDON 1 161.00 (344532) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.2. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.3. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.4. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0003 | 3 Phase fault on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOYMART 1 (344040) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.2. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0004 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0005 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0006 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0007 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0008 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0009 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BOONE (300061) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0010 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0011 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0012 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0013 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0014 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0015 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0016 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0017 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0018 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0019 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0020 | 3 Phase fault on OAKGRV 5 161.00 (541227) 161 kV Bus a. Apply fault at the OAKGRV 5 161.00 (541227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAINVL5 (541226) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 b.2. OAKGRV 5 (541227) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0021 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0022 | 3 Phase fault on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0023 | 3 Phase fault on STALEY 2 69.000 (541261) 69 kV Bus a. Apply fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0024 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0025 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0026 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0027 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0028 | 3 Phase fault on BRMALL 2 69.000 (541283) 69 kV Bus a. Apply fault at the BRMALL 2 69.000 (541283) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMALL 2 (541283) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0029 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0030 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0031 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0032 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0033 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0034 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0035 | 3 Phase fault on SUB E 69.000 (548804) 69 kV Bus a. Apply fault at the SUB E 69.000 (548804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0036 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0037 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0038 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0039 | 3 Phase fault on SUB B 69.000 (548810) 69 kV Bus a. Apply fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0040 | 3 Phase fault on SUB J 69.000 (548811) 69 kV Bus a. Apply fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0041 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0042 | 3 Phase fault on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0043 | 3 Phase fault on STRLNGRD 69.000 (548826) 69 kV Bus a. Apply fault at the STRLNGRD 69.000 (548826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.3. SUB C (548825) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0044 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0045 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0046 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0047 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0048 | 3 Phase fault on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0049 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0050 | 3 Phase fault on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0051 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0052 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0053 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 b.2. ST JOE_CAP5 (541147) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0054 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.3. RNRIDGE_CAP5 (541145) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0055 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0056 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0057 | 3 Phase fault on NAVY 5 161.00 (542989) 161 kV Bus a. Apply fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0058 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0059 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0060 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. BARRY_CAP 5 (542944) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0061 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0062 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0063 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0064 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0065 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0066 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0067 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0068 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0069 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0070 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0071 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0072 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0073 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0074 | 3 Phase fault on MILCKJT2 69.000 (543110) 69 kV Bus a. Apply fault at the MILCKJT2 69.000 (543110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.3. IND WTR2 (543086) 69.0 kV to CEMCITY2 (543090) 69.0 kV Transmission Circuit #1 b.4. IND WTR2 (543086) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.5. TMP LAF2 (543103) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.6. LAFJCT 2 (543104) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.7. MILCKJT2 (543110) 69.0 kV to LAFARGE2 (543111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0075 | 3 Phase fault on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 b.3. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0076 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0077 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0078 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0079 | 3 Phase fault on WPRTTS 2 69.000 (530596) 69 kV Bus a. Apply fault at the WPRTTS 2 69.000 (530596) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.2. GB STH 2 (530569) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.3. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.4. WPRTTS 2 (530596) 69.0 kV to WPRT2 2 (530597) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0080 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0081 | 3 Phase fault on COLLEG 2 69.000 (530574) 69 kV Bus a. Apply fault at the COLLEG 2 69.000 (530574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 b.2. COLLEG 2 (530574) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0082 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0083 | 3 Phase fault on NEKOMA 2 69.000 (530564) 69 kV Bus a. Apply fault at the NEKOMA 2 69.000 (530564) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0084 | 3 Phase fault on BKHLTAP2 69.000 (530589) 69 kV Bus a. Apply fault at the BKHLTAP2 69.000 (530589) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.2. SUSANK 2 (530571) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.3. BNK HL 2 (530572) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.4. HITHMN 2 (530573) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0085 | 3 Phase fault on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0086 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0087 | 3 Phase fault on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0088 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0089 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0090 | 3 Phase fault on SEGNTP 3 115.00 (530682) 115 kV Bus a. Apply fault at the SEGNTP 3 115.00 (530682) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEGNTP 3 (530682) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0091 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0092 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0093 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0094 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0095 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0096 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.2. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.3. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.6. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0097 | 3 Phase fault on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0098 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0099 | 3 Phase fault on HOXIE 3 115.00 (530556) 115 kV Bus a. Apply fault at the HOXIE 3 115.00 (530556) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0100 | 3 Phase fault on ANGELUS 115.00 (530717) 115 kV Bus a. Apply fault at the ANGELUS 115.00 (530717) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.2. SEGNTP 3 (530682) 115.0 kV to SEGUIN 3 (530683) 115.0 kV Transmission Circuit #1 b.3. SEGUIN 3 (530683) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0101 | 3 Phase fault on HUNTSVL3 115.00 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 115.00 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0102 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0103 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0104 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0105 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0106 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0107 | 3 Phase fault on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0108 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0109 | 3 Phase fault on GRHMSUB3 115.00 (531386) 115 kV Bus a. Apply fault at the GRHMSUB3 115.00 (531386) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0110 | 3 Phase fault on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0111 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0112 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0113 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0114 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0115 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0116 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0117 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0118 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0119 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0120 | 3 Phase fault on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0121 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0122 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0123 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0124 | 3 Phase fault on BEACH 3 115.00 (530557) 115 kV Bus a. Apply fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0125 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0126 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0127 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0128 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.2. STOCKVL7 (640365) 115.0 kV to STOCKVL8 (640366) 69.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 b.4. STOCKVLLET19 (643146) 13.8 kV to STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0129 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0130 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0131 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0132 | 3 Phase fault on ATHEY 7 115.00 (641244) 115 kV Bus a. Apply fault at the ATHEY 7 115.00 (641244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 b.2. ATHEY 7 (641244) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 b.3. LAMAR___-TS7 (659804) 115.0 kV to CRETE___-TS7 (659813) 115.0 kV Transmission Circuit #1 b.4. CRETE___-TS7 (659813) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0133 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0134 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0135 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0136 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0137 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0138 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0139 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0140 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0141 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0142 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0143 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0144 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0145 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0146 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0147 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0148 | 3 Phase fault on BEVERLY8 69.000 (640083) 69 kV Bus a. Apply fault at the BEVERLY8 69.000 (640083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0149 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0150 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0151 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0152 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0153 | 3 Phase fault on MCCOOK 8 69.000 (640270) 69 kV Bus a. Apply fault at the MCCOOK 8 69.000 (640270) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0154 | 3 Phase fault on STOCKVL8 69.000 (640366) 69 kV Bus a. Apply fault at the STOCKVL8 69.000 (640366) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKVL8 (640366) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0155 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0156 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0157 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0158 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0159 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0160 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0161 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0162 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0163 | 3 Phase fault on ANTHONY4 138.00 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 138.00 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0164 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0165 | 3 Phase fault on GRINNEL3 115.00 (531412) 115 kV Bus a. Apply fault at the GRINNEL3 115.00 (531412) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 b.2. ARNOLD3 (531409) 115.0 kV to GOVE 3 (531411) 115.0 kV Transmission Circuit #1 b.3. ARNOLD3 (531409) 115.0 kV to RANSOM 3 (531414) 115.0 kV Transmission Circuit #1 b.4. GOVE 3 (531411) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0166 | 3 Phase fault on SETAB 3 115.00 (531464) 115 kV Bus a. Apply fault at the SETAB 3 115.00 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0167 | 3 Phase fault on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0168 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0169 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0170 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0171 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0172 | 3 Phase fault on WILLIAM3 115.00 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 115.00 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0173 | 3 Phase fault on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEOTI 3 (531428) 115.0 kV to SELKIRK3 (531434) 115.0 kV Transmission Circuit #1 b.2. LEOTI 3 (531428) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 b.3. SELKIRK3 (531434) 115.0 kV to TRIB SW3 (531438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0174 | 3 Phase fault on ATWODSW3 115.00 (531364) 115 kV Bus a. Apply fault at the ATWODSW3 115.00 (531364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.2. LUDELLT3 (531220) 115.0 kV to LUDELL 3 (531221) 115.0 kV Transmission Circuit #1 b.3. LUDELLT3 (531220) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.4. LUDELLT3 (531220) 115.0 kV to HERNDON3 (531367) 115.0 kV Transmission Circuit #1 b.5. ATWODSW3 (531364) 115.0 kV to NATWOOD3 (531369) 115.0 kV Transmission Circuit #1 b.6. HERNDON3 (531367) 115.0 kV to JOHNSON3 (531371) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0175 | 3 Phase fault on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.3. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0176 | 3 Phase fault on GANO 3 115.00 (531493) 115 kV Bus a. Apply fault at the GANO 3 115.00 (531493) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.3. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0177 | 3 Phase fault on KSAVWTP3 115.00 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 115.00 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0178 | 3 Phase fault on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0179 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0180 | 3 Phase fault on SUNCITY3 115.00 (539697) 115 kV Bus a. Apply fault at the SUNCITY3 115.00 (539697) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.3. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.4. GRNBURG3 (539664) 115.0 kV to GRNBURG1 (539710) 34.5 kV to GRNBUG-T (539910) 13.8 kV Three Winding #1 b.5. SUNCITY3 (539697) 115.0 kV to SUNCITY1 (539733) 34.5 kV to SUNCT-T (539937) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0181 | 3 Phase fault on FORD 3 115.00 (539758) 115 kV Bus a. Apply fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.3. FORD 3 (539758) 115.0 kV to FORD 1 (539765) 34.5 kV to FORD T (539968) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0182 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0183 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0184 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0185 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0186 | 3 Phase fault on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0187 | 3 Phase fault on DCBEEF3 115.00 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 115.00 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0188 | 3 Phase fault on SPEARVL3 115.00 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 115.00 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0189 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0190 | 3 Phase fault on N-DODGE3 115.00 (539680) 115 kV Bus a. Apply fault at the N-DODGE3 115.00 (539680) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DODG3 (539641) 115.0 kV to N-DODGE3 (539680) 115.0 kV Transmission Circuit #1 b.2. N-DODGE3 (539680) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. N-DODGE3 (539680) 115.0 kV to N-DODGE1 (539720) 34.5 kV to N-DODG-T (539922) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0191 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0192 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0193 | 3 Phase fault on WALDO 3 115.00 (539698) 115 kV Bus a. Apply fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0194 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0195 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0196 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0197 | 3 Phase fault on HARPER 4 138.00 (539668) 138 kV Bus a. Apply fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0198 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-058 (763895) andG19-063 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0199 | 3 Phase fault on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL3 (539701) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G20-056 (765011). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0200 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0201 | 3 Phase fault on BYRONTP4 138.00 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 138.00 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.2. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0202 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0203 | 3 Phase fault on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0204 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0205 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0206 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0207 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0208 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0209 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0210 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0211 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0212 | 3 Phase fault on CARB-KW 3 115.00 (533195) 115 kV Bus a. Apply fault at the CARB-KW 3 115.00 (533195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 b.2. CARB-KW 3 (533195) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0213 | 3 Phase fault on OSAGE J3 115.00 (533171) 115 kV Bus a. Apply fault at the OSAGE J3 115.00 (533171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.2. OSAGE 3 (533170) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 b.3. OSAGE J3 (533171) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.4. OSAGE J3 (533171) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.5. READING3 (533306) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0214 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGCRK3 (533380) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.2. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.4. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0215 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0216 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0217 | 3 Phase fault on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0218 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0219 | 3 Phase fault on MORRIS 3 115.00 (533305) 115 kV Bus a. Apply fault at the MORRIS 3 115.00 (533305) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0220 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0221 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0222 | 3 Phase fault on NW LEAV3 115.00 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 115.00 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0223 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.2. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0224 | 3 Phase fault on STRANGR3 115.00 (533268) 115 kV Bus a. Apply fault at the STRANGR3 115.00 (533268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0225 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0226 | 3 Phase fault on FOWLER 4 138.00 (533043) 138 kV Bus a. Apply fault at the FOWLER 4 138.00 (533043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0227 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0228 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0229 | 3 Phase fault on 47TH ST4 138.00 (533058) 138 kV Bus a. Apply fault at the 47TH ST4 138.00 (533058) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0230 | 3 Phase fault on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0231 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0232 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0233 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0234 | 3 Phase fault on BELAIRE4 138.00 (532988) 138 kV Bus a. Apply fault at the BELAIRE4 138.00 (532988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0235 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0236 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0237 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0238 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0239 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0240 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0241 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0242 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0243 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0244 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0245 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0246 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0247 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0248 | 3 Phase fault on BU11PON4 138.00 (533032) 138 kV Bus a. Apply fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0249 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0250 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0251 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G17-068 (589063). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0252 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0253 | 3 Phase fault on BEECHTP4 138.00 (533028) 138 kV Bus a. Apply fault at the BEECHTP4 138.00 (533028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.2. BEECH 4 (533027) 138.0 kV to BEECHTP4 (533028) 138.0 kV Transmission Circuit #1 b.3. BEECHTP4 (533028) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 b.4. BEECHTP4 (533028) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0254 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0255 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0256 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0257 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0258 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0259 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0260 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0261 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0262 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0263 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0264 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0265 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0266 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0267 | 3 Phase fault on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0268 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0269 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0270 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0271 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0272 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0273 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0274 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0275 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0276 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0277 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0278 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0279 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0280 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0281 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0282 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0283 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0284 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0285 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0286 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0287 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0288 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0289 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0290 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0291 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0292 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0293 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0294 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0295 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0296 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0297 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0298 | 3 Phase fault on MEAD N 2 69.000 (533818) 69 kV Bus a. Apply fault at the MEAD N 2 69.000 (533818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD N 2 (533818) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0299 | 3 Phase fault on 17TH TP2 69.000 (533835) 69 kV Bus a. Apply fault at the 17TH TP2 69.000 (533835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.2. RIVERSD2 (533834) 69.0 kV to 17TH TP2 (533835) 69.0 kV Transmission Circuit #1 b.3. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.4. 17TH TP2 (533835) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.5. 17TH TP2 (533835) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0300 | 3 Phase fault on MOSSMAN2 69.000 (533820) 69 kV Bus a. Apply fault at the MOSSMAN2 69.000 (533820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSSMAN2 (533820) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0301 | 3 Phase fault on MASCOT 2 69.000 (533814) 69 kV Bus a. Apply fault at the MASCOT 2 69.000 (533814) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASCOT 2 (533814) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.2. MASCOT 2 (533814) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0302 | 3 Phase fault on EASTBOR2 69.000 (533792) 69 kV Bus a. Apply fault at the EASTBOR2 69.000 (533792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTBOR2 (533792) 69.0 kV to MINNEHA2 (533817) 69.0 kV Transmission Circuit #1 b.2. EASTBOR2 (533792) 69.0 kV to 64TH 2 (533842) 69.0 kV Transmission Circuit #1 b.3. MINNEHA2 (533817) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0303 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0304 | 3 Phase fault on ARCOTAP2 69.000 (533620) 69 kV Bus a. Apply fault at the ARCOTAP2 69.000 (533620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO 2 (533619) 69.0 kV to ARCOTAP2 (533620) 69.0 kV Transmission Circuit #1 b.2. ARCOTAP2 (533620) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.3. ARCOTAP2 (533620) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.4. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.5. COALCRK2 (533633) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.6. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0305 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0306 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to RA5HIPR2 (533706) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0307 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0308 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0309 | 3 Phase fault on ORCHARD2 69.000 (533643) 69 kV Bus a. Apply fault at the ORCHARD2 69.000 (533643) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.2. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.3. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0310 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0311 | 3 Phase fault on BELL 2 69.000 (533783) 69 kV Bus a. Apply fault at the BELL 2 69.000 (533783) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV to SC9ANSN2 (533866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0312 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 b.2. SC3MILL2 (533552) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 b.3. SC3MILL2 (533552) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 b.4. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0313 | 3 Phase fault on PECK 2 69.000 (533830) 69 kV Bus a. Apply fault at the PECK 2 69.000 (533830) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 b.2. GILL W 2 (533796) 69.0 kV to HAYSVJS2 (533802) 69.0 kV Transmission Circuit #1 b.3. HAYSVJS2 (533802) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0314 | 3 Phase fault on HYDRJS2 69.000 (533810) 69 kV Bus a. Apply fault at the HYDRJS2 69.000 (533810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALN 2 (533790) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 b.2. HYDRA N2 (533807) 69.0 kV to HYDRJS2 (533810) 69.0 kV Transmission Circuit #1 b.3. HYDRJS2 (533810) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 b.4. HYDRJS2 (533810) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0315 | 3 Phase fault on SHERIDN2 69.000 (533841) 69 kV Bus a. Apply fault at the SHERIDN2 69.000 (533841) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0316 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV to RIPLEYE2 (533859) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0317 | 3 Phase fault on BU5FURL2 69.000 (533861) 69 kV Bus a. Apply fault at the BU5FURL2 69.000 (533861) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THUNBRD2 (533603) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 b.2. CHISHLM2 (533786) 69.0 kV to GRANT 2 (533799) 69.0 kV Transmission Circuit #1 b.3. GRANT 2 (533799) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0318 | 3 Phase fault on WESTLNK2 69.000 (533854) 69 kV Bus a. Apply fault at the WESTLNK2 69.000 (533854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.3. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0319 | 3 Phase fault on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0320 | 3 Phase fault on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.2. SUNSET-2 (533844) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0321 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC7CRES2 (533555) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0322 | 3 Phase fault on WILLJCT2 69.000 (533713) 69 kV Bus a. Apply fault at the WILLJCT2 69.000 (533713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 b.2. WILLJCT2 (533713) 69.0 kV to ELKJSS 2 (533718) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0323 | 3 Phase fault on ELPASO 2 69.000 (533793) 69 kV Bus a. Apply fault at the ELPASO 2 69.000 (533793) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 2 (533793) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 b.2. ELPASO 2 (533793) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0324 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0325 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0326 | 3 Phase fault on WATER1 2 69.000 (533855) 69 kV Bus a. Apply fault at the WATER1 2 69.000 (533855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0327 | 3 Phase fault on WATER2 2 69.000 (533856) 69 kV Bus a. Apply fault at the WATER2 2 69.000 (533856) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.2. PLAZA E2 (533829) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0328 | 3 Phase fault on RIPLEYW2 69.000 (533832) 69 kV Bus a. Apply fault at the RIPLEYW2 69.000 (533832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.2. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.3. 21ST 2 (533846) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0329 | 3 Phase fault on INDEPEN2 69.000 (533694) 69 kV Bus a. Apply fault at the INDEPEN2 69.000 (533694) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDEPEN2 (533694) 69.0 kV to MONTGOM2 (533698) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0330 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0331 | 3 Phase fault on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0332 | 3 Phase fault on HYDRJN2 69.000 (533808) 69 kV Bus a. Apply fault at the HYDRJN2 69.000 (533808) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HYDRJN2 (533808) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.2. HYDRJN2 (533808) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0333 | 3 Phase fault on SENECA 2 69.000 (533839) 69 kV Bus a. Apply fault at the SENECA 2 69.000 (533839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.2. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.3. OSAGE 2 (533827) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0334 | 3 Phase fault on MEAD S 2 69.000 (533815) 69 kV Bus a. Apply fault at the MEAD S 2 69.000 (533815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0335 | 3 Phase fault on HAYSVJN2 69.000 (533804) 69 kV Bus a. Apply fault at the HAYSVJN2 69.000 (533804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 b.2. HAYSVJN2 (533804) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0336 | 3 Phase fault on LIN 2 69.000 (533812) 69 kV Bus a. Apply fault at the LIN 2 69.000 (533812) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.2. LIN 2 (533812) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 b.3. SUNSET-2 (533844) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 b.4. SG1CHEN2 (533871) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0337 | 3 Phase fault on MAHANNA2 69.000 (533738) 69 kV Bus a. Apply fault at the MAHANNA2 69.000 (533738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAHANNA2 (533738) 69.0 kV to ADAMS 2 (533746) 69.0 kV Transmission Circuit #1 b.2. MAHANNA2 (533738) 69.0 kV to GRANT J2 (533800) 69.0 kV Transmission Circuit #1 b.3. NEWTON 2 (533745) 69.0 kV to ADAMS 2 (533746) 69.0 kV Transmission Circuit #1 b.4. GRANT J2 (533800) 69.0 kV to RIPLEYW2 (533832) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0338 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0339 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0340 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0341 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0342 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0343 | 3 Phase fault on ASHGRJ22 69.000 (533660) 69 kV Bus a. Apply fault at the ASHGRJ22 69.000 (533660) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.2. ASHGRV22 (533658) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.3. ASHGRJ12 (533659) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #z1 b.4. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0344 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 b.3. EMANHAT6 (532861) 230.0 kV to EMANHAT3 (533326) 115.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0345 | 3 Phase fault on 64TH 4 138.00 (533066) 138 kV Bus a. Apply fault at the 64TH 4 138.00 (533066) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRY 4 (533048) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 b.3. 64TH 4 (533066) 138.0 kV to 64TH 2 (533842) 69.0 kV to 64TH 1 (533113) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0346 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0347 | 3 Phase fault on CANAL 4 138.00 (533033) 138 kV Bus a. Apply fault at the CANAL 4 138.00 (533033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. CANAL 4 (533033) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #1 b.3. CANAL 4 (533033) 138.0 kV to CANALS 2 (533784) 69.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0348 | 3 Phase fault on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0349 | 3 Phase fault on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.3. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.4. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0350 | 3 Phase fault on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0351 | 3 Phase fault on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0352 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.4. MONTGOM1 (533091) 13.2 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0353 | 3 Phase fault on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0354 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0355 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0356 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAUGHN 3 (533308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0357 | 3 Phase fault on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0358 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0359 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0360 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0361 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0362 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0363 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0364 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0365 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0366 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0367 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0368 | 3 Phase fault on BELL 2 69.000 (533783) 69 kV Bus a. Apply fault at the BELL 2 69.000 (533783) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0369 | 3 Phase fault on CANALN 2 69.000 (533790) 69 kV Bus a. Apply fault at the CANALN 2 69.000 (533790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALN 2 (533790) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0370 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0371 | 3 Phase fault on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0372 | 3 Phase fault on MACARTH2 69.000 (533813) 69 kV Bus a. Apply fault at the MACARTH2 69.000 (533813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACARTH2 (533813) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0373 | 3 Phase fault on MONTGOM2 69.000 (533698) 69 kV Bus a. Apply fault at the MONTGOM2 69.000 (533698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0374 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0375 | 3 Phase fault on PARSONS2 69.000 (533704) 69 kV Bus a. Apply fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0376 | 3 Phase fault on TIOGA 2 69.000 (533646) 69 kV Bus a. Apply fault at the TIOGA 2 69.000 (533646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0377 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0378 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0379 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0380 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0381 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0382 | 3 Phase fault on CHELSA4 138.00 (510410) 138 kV Bus a. Apply fault at the CHELSA4 138.00 (510410) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHELSA4 (510410) 138.0 kV to G22-234-TAP (771660) 138.0 kV Transmission Circuit #1 b.2. ALWUETP4 (510429) 138.0 kV to G22-234-TAP (771660) 138.0 kV Transmission Circuit #1 b.3. N.E.S.-4 (510396) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.4. CHELSA4 (510410) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.5. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0383 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0384 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 (510418) 69.0 kV to VINTAJC4 (510417) 138.0 kV to VINJT1-1 (510367) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0385 | 3 Phase fault on TERRACE5 161.00 (542991) 161 kV Bus a. Apply fault at the TERRACE5 161.00 (542991) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0386 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0387 | 3 Phase fault on BARBER 5 161.00 (546651) 161 kV Bus a. Apply fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0388 | 3 Phase fault on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0389 | 3 Phase fault on GIBBS 5 161.00 (546658) 161 kV Bus a. Apply fault at the GIBBS 5 161.00 (546658) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0390 | 3 Phase fault on PIPER 5 161.00 (546668) 161 kV Bus a. Apply fault at the PIPER 5 161.00 (546668) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0391 | 3 Phase fault on KAW 2 69.000 (546678) 69 kV Bus a. Apply fault at the KAW 2 69.000 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to BARBER 2 (546691) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0392 | 3 Phase fault on BARBER 5 161.00 (546651) 161 kV Bus a. Apply fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0393 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0394 | 3 Phase fault on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0395 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0396 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0397 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0398 | 3 Phase fault on 5ELMCRK 161.00 (300993) 161 kV Bus a. Apply fault at the 5ELMCRK 161.00 (300993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit #1 b.2. 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0399 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0400 | 3 Phase fault on NWMAID5 161.00 (512757) 161 kV Bus a. Apply fault at the NWMAID5 161.00 (512757) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0401 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0402 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0403 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0404 | 3 Phase fault on KANSATP5 161.00 (512714) 161 kV Bus a. Apply fault at the KANSATP5 161.00 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 412SUB 5 (512637) 161.0 kV to KANSATP5 (512714) 161.0 kV Transmission Circuit #1 b.2. KANSATP5 (512714) 161.0 kV to KANSAS 5 (512716) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0405 | 3 Phase fault on PENSA 5 161.00 (512654) 161 kV Bus a. Apply fault at the PENSA 5 161.00 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0406 | 3 Phase fault on LOCSTGVKM 5 161.00 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 161.00 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0407 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0408 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0409 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0410 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0411 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0412 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0413 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0414 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0415 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0416 | 3 Phase fault on 2NEWPORT 69.000 (301467) 69 kV Bus a. Apply fault at the 2NEWPORT 69.000 (301467) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MONKEY (301465) 69.0 kV to 2NEWPORT (301467) 69.0 kV Transmission Circuit #1 b.2. 2NEWPORT (301467) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0417 | 3 Phase fault on SAILBOA2 69.000 (510409) 69 kV Bus a. Apply fault at the SAILBOA2 69.000 (510409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAILBOA2 (510409) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0418 | 3 Phase fault on AMERCAST S2 69.000 (512681) 69 kV Bus a. Apply fault at the AMERCAST S2 69.000 (512681) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to AMERCAST S2 (512681) 69.0 kV Transmission Circuit #1 b.2. CPPTAP 2 (512661) 69.0 kV to AMERCAST S2 (512681) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0419 | 3 Phase fault on REDDEN 2 69.000 (512698) 69 kV Bus a. Apply fault at the REDDEN 2 69.000 (512698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to REDDEN 2 (512698) 69.0 kV Transmission Circuit #1 b.2. AMERCAST N2 (512683) 69.0 kV to CASTING TAP2 (512685) 69.0 kV Transmission Circuit #1 b.3. CASTING TAP2 (512685) 69.0 kV to REDDEN 2 (512698) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0420 | 3 Phase fault on CLEORTP2 69.000 (512692) 69 kV Bus a. Apply fault at the CLEORTP2 69.000 (512692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEORA (301460) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 b.2. PENSA 2 (512628) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 b.3. AFTON 2 (512633) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0421 | 3 Phase fault on ESH TP 2 69.000 (512680) 69 kV Bus a. Apply fault at the ESH TP 2 69.000 (512680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2J6 (300829) 69.0 kV to AFTP TP2 (512620) 69.0 kV Transmission Circuit #1 b.2. 2J6 (300829) 69.0 kV to VINEOTP2 (512673) 69.0 kV Transmission Circuit #1 b.3. 2VINITAHQ (300983) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.4. 2ESHOSP (301468) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.5. 2VIN NEO (301478) 69.0 kV to VINEOTP2 (512673) 69.0 kV Transmission Circuit #1 b.6. VINITA-2 (510404) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.7. AFTONTP2 (510415) 69.0 kV to A-CONT 2 (510427) 69.0 kV Transmission Circuit #1 b.8. AFTONTP2 (510415) 69.0 kV to AFTN-EX2 (510428) 69.0 kV Transmission Circuit #1 b.9. AFTONTP2 (510415) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.10. AFTP TP2 (512620) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.11. AFTON 2 (512633) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.12. VINEOTP2 (512673) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0422 | 3 Phase fault on FAIRTAP2 69.000 (512708) 69 kV Bus a. Apply fault at the FAIRTAP2 69.000 (512708) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to FAIRNEO2 (512691) 69.0 kV Transmission Circuit #1 b.2. AFTON 2 (512633) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 b.3. FAIRNEO2 (512691) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 b.4. FAIRTAP2 (512708) 69.0 kV to FRL363 2 (547583) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0423 | 3 Phase fault on MIAMI 2 69.000 (512630) 69 kV Bus a. Apply fault at the MIAMI 2 69.000 (512630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI1 2 (513020) 69.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI3 2 (513024) 69.0 kV Transmission Circuit #1 b.3. MIAMI1 2 (513020) 69.0 kV to MIAMI4 2 (513022) 69.0 kV Transmission Circuit #1 b.4. MIAMI4 2 (513022) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 b.5. MIAMI3 2 (513024) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0424 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0425 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0426 | 3 Phase fault on 2WLKRTP 69.000 (300760) 69 kV Bus a. Apply fault at the 2WLKRTP 69.000 (300760) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSHO (300750) 69.0 kV to 2WLKRTP (300760) 69.0 kV Transmission Circuit #1 b.2. 2WLKRTP (300760) 69.0 kV to 2WLKRVL (300761) 69.0 kV Transmission Circuit #1 b.3. 2WLKRTP (300760) 69.0 kV to 2SENECA (300830) 69.0 kV Transmission Circuit #1 b.4. 2SENECA (300830) 69.0 kV to 2MIAETP (300852) 69.0 kV Transmission Circuit #1 b.5. 2MIAETP (300852) 69.0 kV to MIAMI 2 (512630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0427 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0428 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0429 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0430 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0431 | 3 Phase fault on TONECE7 345.00 (512750) 345 kV Bus a. Apply fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0432 | 3 Phase fault on KERR BRK1 5 161.00 (512770) 161 kV Bus a. Apply fault at the KERR BRK1 5 161.00 (512770) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK1 5 (512770) 161.0 kV to KERR GR3 (512634) 115.0 kV to KERR1 1 (512846) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0433 | 3 Phase fault on KERR BRK4 5 161.00 (512771) 161 kV Bus a. Apply fault at the KERR BRK4 5 161.00 (512771) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK4 5 (512771) 161.0 kV to KERR GR3 (512634) 115.0 kV to KERR2 1 (512847) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0434 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0435 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0436 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0437 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0438 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0439 | 3 Phase fault on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0440 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0441 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0442 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0443 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0444 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. HOC404A1 (547715) 12.5 kV to HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0445 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0446 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0447 | 3 Phase fault on 5MCBAIN T 161.00 (345071) 161 kV Bus a. Apply fault at the 5MCBAIN T 161.00 (345071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0448 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0449 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0450 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0451 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0452 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0453 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0454 | 3 Phase fault on 5APCH TP 161.00 (344026) 161 kV Bus a. Apply fault at the 5APCH TP 161.00 (344026) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0455 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MPLTAP (300036) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 b.3. 5MPLTAP (300036) 161.0 kV to 5LATHROP (344923) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0456 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0457 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0458 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0459 | 3 Phase fault on 5LOYMART 1 161.00 (344040) 161 kV Bus a. Apply fault at the 5LOYMART 1 161.00 (344040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOYMART 1 (344040) 161.0 kV to 5LOYMART 2 (344041) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0460 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0461 | 3 Phase fault on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GUTHRIE 1 (344677) 161.0 kV to 5GUTHRIE 2 (344678) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0462 | 3 Phase fault on 5JC ZION 161.00 (344814) 161 kV Bus a. Apply fault at the 5JC ZION 161.00 (344814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JC ZION (344814) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #z b.2. 2JC ZION (346089) 69.0 kV to 5JC ZION (344814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0463 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0464 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0465 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0466 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0467 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to VSC2_3 (992003) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0468 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0469 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0470 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BOONE (300061) 161.0 kV to 5MCBAINB1 (300501) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0471 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BOONE (300061) 161.0 kV to 5MLRSBGB1 (300519) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0472 | 3 Phase fault on 5CALIF 161.00 (300063) 161 kV Bus a. Apply fault at the 5CALIF 161.00 (300063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF (300063) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0473 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0474 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0475 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0476 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0477 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0478 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0479 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0480 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0481 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0482 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0483 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0484 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0485 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0486 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0487 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0488 | 3 Phase fault on 5OSBORN 161.00 (300107) 161 kV Bus a. Apply fault at the 5OSBORN 161.00 (300107) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSBORN (300107) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0489 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0490 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0491 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0492 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0493 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2MOCITY (300304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0494 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0495 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0496 | 3 Phase fault on 2ASHLND 69.000 (300492) 69 kV Bus a. Apply fault at the 2ASHLND 69.000 (300492) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHLND (300492) 69.0 kV to 2BOONE (300493) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0497 | 3 Phase fault on 2BOONE 69.000 (300493) 69 kV Bus a. Apply fault at the 2BOONE 69.000 (300493) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOONE (300493) 69.0 kV to 2DEERPK (300497) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0498 | 3 Phase fault on 2BOONE 69.000 (300493) 69 kV Bus a. Apply fault at the 2BOONE 69.000 (300493) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOONE (300493) 69.0 kV to 2GRINDSTN (343006) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0499 | 3 Phase fault on 5MCBAINB1 161.00 (300501) 161 kV Bus a. Apply fault at the 5MCBAINB1 161.00 (300501) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB1 (300501) 161.0 kV to 5MCBAINB2 (301489) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0500 | 3 Phase fault on 5MLRSBGB1 161.00 (300519) 161 kV Bus a. Apply fault at the 5MLRSBGB1 161.00 (300519) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MLRSBGB1 (300519) 161.0 kV to 5MLRSBGB2 (301498) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0501 | 3 Phase fault on 2DRESDN 69.000 (300528) 69 kV Bus a. Apply fault at the 2DRESDN 69.000 (300528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DRESDN (300528) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0502 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0503 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0504 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0505 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0506 | 3 Phase fault on 2HUGHSV 69.000 (300533) 69 kV Bus a. Apply fault at the 2HUGHSV 69.000 (300533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HUGHSV (300533) 69.0 kV to 2SWSPJC (300543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0507 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0508 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0509 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0510 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0511 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0512 | 3 Phase fault on 2CALIF 69.000 (300550) 69 kV Bus a. Apply fault at the 2CALIF 69.000 (300550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 2FORTNA (300554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0513 | 3 Phase fault on 2CALIF 69.000 (300550) 69 kV Bus a. Apply fault at the 2CALIF 69.000 (300550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 2PRARIE (300561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0514 | 3 Phase fault on 2CALIF 69.000 (300550) 69 kV Bus a. Apply fault at the 2CALIF 69.000 (300550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 2ST_MARTINS (301442) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0515 | 3 Phase fault on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FORTNA (300554) 69.0 kV to 2NEEDY (300559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0516 | 3 Phase fault on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FORTNA (300554) 69.0 kV to 2SYRACS (300564) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0517 | 3 Phase fault on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FORTNA (300554) 69.0 kV to 2VERSAL (300565) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0518 | 3 Phase fault on 5GRAVOIB1 161.00 (300555) 161 kV Bus a. Apply fault at the 5GRAVOIB1 161.00 (300555) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRAVOIB1 (300555) 161.0 kV to 5GRAVOIB2 (300574) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0519 | 3 Phase fault on 2HIGHPT 69.000 (300556) 69 kV Bus a. Apply fault at the 2HIGHPT 69.000 (300556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HIGHPT (300556) 69.0 kV to 2BARNET (300618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0520 | 3 Phase fault on 2PILOTG 69.000 (300560) 69 kV Bus a. Apply fault at the 2PILOTG 69.000 (300560) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PILOTG (300560) 69.0 kV to 2PRARIE (300561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0521 | 3 Phase fault on 2VERSAL 69.000 (300565) 69 kV Bus a. Apply fault at the 2VERSAL 69.000 (300565) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERSAL (300565) 69.0 kV to 2BARNET (300618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0522 | 3 Phase fault on 2BARNET 69.000 (300618) 69 kV Bus a. Apply fault at the 2BARNET 69.000 (300618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BARNET (300618) 69.0 kV to 2MTPLSTC (300633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0523 | 3 Phase fault on 2SCRUGG 69.000 (300637) 69 kV Bus a. Apply fault at the 2SCRUGG 69.000 (300637) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SCRUGG (300637) 69.0 kV to 2ST_MARTINS (301442) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0524 | 3 Phase fault on 2BLLMYTP 69.000 (300647) 69 kV Bus a. Apply fault at the 2BLLMYTP 69.000 (300647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLLMYTP (300647) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0525 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0526 | 3 Phase fault on 2LAMR 69.000 (300651) 69 kV Bus a. Apply fault at the 2LAMR 69.000 (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0527 | 3 Phase fault on 2LAMR 69.000 (300651) 69 kV Bus a. Apply fault at the 2LAMR 69.000 (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2LAMARPT (300685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0528 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0529 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0530 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0531 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0532 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0533 | 3 Phase fault on 2MIAETP 69.000 (300852) 69 kV Bus a. Apply fault at the 2MIAETP 69.000 (300852) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MIAETP (300852) 69.0 kV to 2MIAENEO (301461) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0534 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0535 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0536 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0537 | 3 Phase fault on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PLATCTY (301552) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0538 | 3 Phase fault on 5REBEL 161.00 (343007) 161 kV Bus a. Apply fault at the 5REBEL 161.00 (343007) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REBEL (343007) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0539 | 3 Phase fault on 2APCH FLT 69.000 (344027) 69 kV Bus a. Apply fault at the 2APCH FLT 69.000 (344027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2APCH FLT (344027) 69.0 kV to 2JC RAINB (346082) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0540 | 3 Phase fault on 2APCH FLT 69.000 (344027) 69 kV Bus a. Apply fault at the 2APCH FLT 69.000 (344027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2APCH FLT (344027) 69.0 kV to 2JC SCRGG (346084) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0541 | 3 Phase fault on 5APCH FLT 161.00 (344028) 161 kV Bus a. Apply fault at the 5APCH FLT 161.00 (344028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0542 | 3 Phase fault on 5JC ZION TP 161.00 (344815) 161 kV Bus a. Apply fault at the 5JC ZION TP 161.00 (344815) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JC ZION TP (344815) 161.0 kV to 5MARIOSA (345027) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0543 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0544 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0545 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2MACON_AM (346096) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0546 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2DUPONT (346169) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0547 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2ROTH TAP (346170) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0548 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2SPRK TAP (346171) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0549 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0550 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0551 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to KERR BRK1 5 (512770) 161.0 kV Transmission Circuit #z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0552 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to KERR BRK4 5 (512771) 161.0 kV Transmission Circuit #z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0553 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0554 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to G21-047-TAP (765721) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0555 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0556 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0557 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0558 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0559 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0560 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0561 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0562 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0563 | 3 Phase fault on N HAYS3 115.00 (530581) 115 kV Bus a. Apply fault at the N HAYS3 115.00 (530581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0564 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0565 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0566 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0567 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0568 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0569 | 3 Phase fault on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0570 | 3 Phase fault on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0571 | 3 Phase fault on VINETAP3 115.00 (530693) 115 kV Bus a. Apply fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0572 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0573 | 3 Phase fault on GEM_SW 3 115.00 (530713) 115 kV Bus a. Apply fault at the GEM_SW 3 115.00 (530713) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEM_SW 3 (530713) 115.0 kV to COLBY_PUMP3 (530716) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0574 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0575 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0576 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0577 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0578 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0579 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0580 | 3 Phase fault on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0581 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0582 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0583 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0584 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0585 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0586 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0587 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0588 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0589 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0590 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0591 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0592 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0593 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0594 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0595 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0596 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0597 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to TCBURNS4 (532994) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0598 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0599 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0600 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0601 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0602 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0603 | 3 Phase fault on CENTENN4 138.00 (533034) 138 kV Bus a. Apply fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0604 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0605 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G17-068 (589063). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0606 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G17-068 (589063). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0607 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0608 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0609 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0610 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0611 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0612 | 3 Phase fault on WACO S 4 138.00 (533071) 138 kV Bus a. Apply fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0613 | 3 Phase fault on WACO 4 138.00 (533072) 138 kV Bus a. Apply fault at the WACO 4 138.00 (533072) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0614 | 3 Phase fault on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0615 | 3 Phase fault on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0616 | 3 Phase fault on LANG 3 115.00 (533304) 115 kV Bus a. Apply fault at the LANG 3 115.00 (533304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0617 | 3 Phase fault on READING3 115.00 (533306) 115 kV Bus a. Apply fault at the READING3 115.00 (533306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. READING3 (533306) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0618 | 3 Phase fault on FLORENC3 115.00 (533366) 115 kV Bus a. Apply fault at the FLORENC3 115.00 (533366) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0619 | 3 Phase fault on SPRGCRK3 115.00 (533380) 115 kV Bus a. Apply fault at the SPRGCRK3 115.00 (533380) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0620 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0621 | 3 Phase fault on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0622 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0623 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0624 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0625 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to BURLIND2 (533625) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0626 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to CC1BURL2 (533628) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0627 | 3 Phase fault on ALTAMNT2 69.000 (533671) 69 kV Bus a. Apply fault at the ALTAMNT2 69.000 (533671) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0628 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODESH2 (533699) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0629 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0630 | 3 Phase fault on YELLOWJ2 69.000 (533692) 69 kV Bus a. Apply fault at the YELLOWJ2 69.000 (533692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YELLOWJ2 (533692) 69.0 kV to NEW ALB2 (533701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0631 | 3 Phase fault on LABETTE2 69.000 (533695) 69 kV Bus a. Apply fault at the LABETTE2 69.000 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0632 | 3 Phase fault on NEODJCT2 69.000 (533700) 69 kV Bus a. Apply fault at the NEODJCT2 69.000 (533700) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEODJCT2 (533700) 69.0 kV to RA6BROO2 (533707) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0633 | 3 Phase fault on NEW ALB2 69.000 (533701) 69 kV Bus a. Apply fault at the NEW ALB2 69.000 (533701) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEW ALB2 (533701) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0634 | 3 Phase fault on ORDNCE 2 69.000 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 69.000 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0635 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0636 | 3 Phase fault on CANALS 2 69.000 (533784) 69 kV Bus a. Apply fault at the CANALS 2 69.000 (533784) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0637 | 3 Phase fault on CANALS 2 69.000 (533784) 69 kV Bus a. Apply fault at the CANALS 2 69.000 (533784) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0638 | 3 Phase fault on CHENEY 2 69.000 (533785) 69 kV Bus a. Apply fault at the CHENEY 2 69.000 (533785) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHENEY 2 (533785) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0639 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0640 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCAN 2 (533850) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0641 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0642 | 3 Phase fault on GLENDAL2 69.000 (533797) 69 kV Bus a. Apply fault at the GLENDAL2 69.000 (533797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL2 (533797) 69.0 kV to OLIVER 2 (533826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0643 | 3 Phase fault on GLENDAL2 69.000 (533797) 69 kV Bus a. Apply fault at the GLENDAL2 69.000 (533797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL2 (533797) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0644 | 3 Phase fault on HAYSV 2 69.000 (533803) 69 kV Bus a. Apply fault at the HAYSV 2 69.000 (533803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYSV 2 (533803) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0645 | 3 Phase fault on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0646 | 3 Phase fault on HOOVERS2 69.000 (533806) 69 kV Bus a. Apply fault at the HOOVERS2 69.000 (533806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0647 | 3 Phase fault on LIN 2 69.000 (533812) 69 kV Bus a. Apply fault at the LIN 2 69.000 (533812) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0648 | 3 Phase fault on OAKLAWN2 69.000 (533824) 69 kV Bus a. Apply fault at the OAKLAWN2 69.000 (533824) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAWN2 (533824) 69.0 kV to OLIVER 2 (533826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0649 | 3 Phase fault on PLAZA E2 69.000 (533829) 69 kV Bus a. Apply fault at the PLAZA E2 69.000 (533829) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0650 | 3 Phase fault on RIPLEYW2 69.000 (533832) 69 kV Bus a. Apply fault at the RIPLEYW2 69.000 (533832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIPLEYW2 (533832) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0651 | 3 Phase fault on GALE TP2 69.000 (533845) 69 kV Bus a. Apply fault at the GALE TP2 69.000 (533845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALE TP2 (533845) 69.0 kV to SG4ANDL2 (533872) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0652 | 3 Phase fault on GALE TP2 69.000 (533845) 69 kV Bus a. Apply fault at the GALE TP2 69.000 (533845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALE TP2 (533845) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0653 | 3 Phase fault on PLAZA M2 69.000 (533857) 69 kV Bus a. Apply fault at the PLAZA M2 69.000 (533857) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0654 | 3 Phase fault on GODDTAP2 69.000 (533879) 69 kV Bus a. Apply fault at the GODDTAP2 69.000 (533879) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GODDTAP2 (533879) 69.0 kV to GODDARD2 (533880) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0655 | 3 Phase fault on RAGO 4 138.00 (539000) 138 kV Bus a. Apply fault at the RAGO 4 138.00 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0656 | 3 Phase fault on NW-DGTP3 115.00 (539628) 115 kV Bus a. Apply fault at the NW-DGTP3 115.00 (539628) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DGTP3 (539628) 115.0 kV to W-DODGE3 (539699) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0657 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0658 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0659 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0660 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0661 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0662 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0663 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0664 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-058 (763895) andG19-063 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0665 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-058 (763895) andG19-063 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0666 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-058 (763895) andG19-063 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0667 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-058 (763895) andG19-063 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0668 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0669 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0670 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0671 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0672 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0673 | 3 Phase fault on WBURGE_CAP5 161.00 (541148) 161 kV Bus a. Apply fault at the WBURGE_CAP5 161.00 (541148) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE_CAP5 (541148) 161.0 kV to WBURGE 5 (541228) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0674 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0675 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0676 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0677 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0678 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0679 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0680 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0681 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0682 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0683 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0684 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0685 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0686 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0687 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0688 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0689 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0690 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to POPE (541349) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0691 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0692 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0693 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0694 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0695 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0696 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0697 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0698 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0699 | 3 Phase fault on KCI 5 161.00 (541212) 161 kV Bus a. Apply fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCI 5 (541212) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0700 | 3 Phase fault on KCI 5 161.00 (541212) 161 kV Bus a. Apply fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCI 5 (541212) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0701 | 3 Phase fault on FRLVW 5 161.00 (541213) 161 kV Bus a. Apply fault at the FRLVW 5 161.00 (541213) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRLVW 5 (541213) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0702 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0703 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0704 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0705 | 3 Phase fault on RAYTOWN5 161.00 (541219) 161 kV Bus a. Apply fault at the RAYTOWN5 161.00 (541219) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0706 | 3 Phase fault on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0707 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0708 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0709 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0710 | 3 Phase fault on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 5 (541229) 161.0 kV to LEX161 5 (541232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0711 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0712 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0713 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0714 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0715 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0716 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0717 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0718 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0719 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0720 | 3 Phase fault on EAST 5 161.00 (541254) 161 kV Bus a. Apply fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0721 | 3 Phase fault on IND PRK5 161.00 (541256) 161 kV Bus a. Apply fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0722 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0723 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0724 | 3 Phase fault on KNOSTER2 69.000 (541270) 69 kV Bus a. Apply fault at the KNOSTER2 69.000 (541270) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOSTER2 (541270) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0725 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to KELHYS 2 (541273) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0726 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0727 | 3 Phase fault on SEDS 2 69.000 (541272) 69 kV Bus a. Apply fault at the SEDS 2 69.000 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0728 | 3 Phase fault on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0729 | 3 Phase fault on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0730 | 3 Phase fault on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0731 | 3 Phase fault on COLECMP2 69.000 (541276) 69 kV Bus a. Apply fault at the COLECMP2 69.000 (541276) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLECMP2 (541276) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0732 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0733 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0734 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0735 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBW5 (541336) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0736 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0737 | 3 Phase fault on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161.0 kV to WAFBE5 (541338) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0738 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0739 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0740 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0741 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0742 | 3 Phase fault on IATAN5 161.00 (541350) 161 kV Bus a. Apply fault at the IATAN5 161.00 (541350) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0743 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0744 | 3 Phase fault on MONSERTP 69.000 (541524) 69 kV Bus a. Apply fault at the MONSERTP 69.000 (541524) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONSERTP (541524) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0745 | 3 Phase fault on KNOSTERTP 69.000 (541534) 69 kV Bus a. Apply fault at the KNOSTERTP 69.000 (541534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOSTERTP (541534) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0746 | 3 Phase fault on LAMONTETP 69.000 (541535) 69 kV Bus a. Apply fault at the LAMONTETP 69.000 (541535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMONTETP (541535) 69.0 kV to LAMONTE (541536) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0747 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0748 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G20-058 (764379 and 764376). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0749 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G20-058 (764379 and 764376). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0750 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY_CAP 5 (542944) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0751 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0752 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0753 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0754 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0755 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0756 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0757 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0758 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0759 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0760 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0761 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0762 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0763 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0764 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0765 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0766 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0767 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0768 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0769 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0770 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0771 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0772 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0773 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0774 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0775 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0776 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0777 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0778 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0779 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 4.75 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 4.75 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0780 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0781 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0782 | 3 Phase fault on TROOST 5 161.00 (542986) 161 kV Bus a. Apply fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0783 | 3 Phase fault on TROOST 5 161.00 (542986) 161 kV Bus a. Apply fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0784 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0785 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0786 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0787 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0788 | 3 Phase fault on CROSTWN5 161.00 (542990) 161 kV Bus a. Apply fault at the CROSTWN5 161.00 (542990) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSTWN5 (542990) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0789 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0790 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0791 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0792 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0793 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to ROEPARK5 (543040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0794 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0795 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0796 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0797 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0798 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0799 | 3 Phase fault on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0800 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0801 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0802 | 3 Phase fault on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0803 | 3 Phase fault on CLAYCM15 161.00 (543022) 161 kV Bus a. Apply fault at the CLAYCM15 161.00 (543022) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLAYCM15 (543022) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0804 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0805 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0806 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0807 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0808 | 3 Phase fault on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to ROEPARK5 (543040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0809 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0810 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0811 | 3 Phase fault on OXFORD 5 161.00 (543046) 161 kV Bus a. Apply fault at the OXFORD 5 161.00 (543046) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 5 (543046) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0812 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0813 | 3 Phase fault on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0814 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0815 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0816 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0817 | 3 Phase fault on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSTVAL5 (543077) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0818 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0819 | 3 Phase fault on SUGRCRK_N2 69.000 (543089) 69 kV Bus a. Apply fault at the SUGRCRK_N2 69.000 (543089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_N2 (543089) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0820 | 3 Phase fault on DUNCNRD2 69.000 (543091) 69 kV Bus a. Apply fault at the DUNCNRD2 69.000 (543091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0821 | 3 Phase fault on LIBRTYS2 69.000 (543095) 69 kV Bus a. Apply fault at the LIBRTYS2 69.000 (543095) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0822 | 3 Phase fault on SUGRCK_TP_W269.000 (543164) 69 kV Bus a. Apply fault at the SUGRCK_TP_W269.000 (543164) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0823 | 3 Phase fault on KAW 5 161.00 (546214) 161 kV Bus a. Apply fault at the KAW 5 161.00 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0824 | 3 Phase fault on KAW 5 161.00 (546214) 161 kV Bus a. Apply fault at the KAW 5 161.00 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0825 | 3 Phase fault on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to MILLST 5 (546224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0826 | 3 Phase fault on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0827 | 3 Phase fault on SCAM66 2 69.000 (547409) 69 kV Bus a. Apply fault at the SCAM66 2 69.000 (547409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCAM66 2 (547409) 69.0 kV to SCM66T 2 (547455) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0828 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0829 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to SEK225 2 (547413) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0830 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to SMN425 2 (547414) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0831 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to SHR444 2 (547415) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0832 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0833 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to CHE299 2 (547417) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0834 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to CHE300 2 (547418) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0835 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0836 | 3 Phase fault on CHE300 2 69.000 (547418) 69 kV Bus a. Apply fault at the CHE300 2 69.000 (547418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE300 2 (547418) 69.0 kV to TWN388 2 (547419) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0837 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0838 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0839 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0840 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0841 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0842 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0843 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0844 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0845 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0846 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0847 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0848 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0849 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0850 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0851 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0852 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0853 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0854 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0855 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0856 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0857 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0858 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0859 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0860 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0861 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0862 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0863 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0864 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0865 | 3 Phase fault on GAT258 2 69.000 (547551) 69 kV Bus a. Apply fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0866 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0867 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0868 | 3 Phase fault on GAL278 2 69.000 (547555) 69 kV Bus a. Apply fault at the GAL278 2 69.000 (547555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAL278 2 (547555) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0869 | 3 Phase fault on COM381T2 69.000 (547579) 69 kV Bus a. Apply fault at the COM381T2 69.000 (547579) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COM381T2 (547579) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0870 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0871 | 3 Phase fault on JOP389 2 69.000 (547592) 69 kV Bus a. Apply fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0872 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0873 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0874 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0875 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0876 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0877 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0878 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0879 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0880 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0881 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0882 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0883 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0884 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0885 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0886 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0887 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0888 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0889 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0890 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0891 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0892 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0893 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0894 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0895 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0896 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0897 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0898 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0899 | 3 Phase fault on MALONEY7 115.00 (640265) 115 kV Bus a. Apply fault at the MALONEY7 115.00 (640265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0900 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0901 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0902 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0903 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0904 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0905 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0906 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0907 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0908 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0909 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0910 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0911 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | The Grand Prairie Wind Units (645065, 645066, 645067 and 645068) become unstable following the fault clearance and protection trips the units. Reducing the critical clearing time to 2.7 cycles mitigates the issue. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0912 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0913 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0914 | 3 Phase fault on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0915 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT11_2 (543663) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0916 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT12_2 (543664) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0917 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5KINGDMB1 (300090) 161.0 kV to 7KINGDM (300043) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0918 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0919 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF3 (301506) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0920 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0921 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BARNET (300618) 69.0 kV to 5BARNET (300057) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0922 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOONE (300493) 69.0 kV to 5BOONE (300061) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0923 | 3 Phase fault on 5CALIF 161.00 (300063) 161 kV Bus a. Apply fault at the 5CALIF 161.00 (300063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 5CALIF (300063) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0924 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLARK (300802) 69.0 kV to 5CLARK (300070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0925 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0926 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0927 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0928 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHRP (300302) 69.0 kV to 5LATHRP (300091) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0929 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0930 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0931 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0932 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0933 | 3 Phase fault on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PLATCTY (300307) 69.0 kV to 5PLATCTY (301552) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0934 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0935 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0936 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes