03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0937 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0938 | 3 Phase fault on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PERCHE (343004) 161.0 kV to 2PERCHE (343005) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0939 | 3 Phase fault on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PERCHE (343004) 161.0 kV to 2PERCHE2 (343052) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0940 | 3 Phase fault on 5GRINDSTN 161.00 (343014) 161 kV Bus a. Apply fault at the 5GRINDSTN 161.00 (343014) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GRINDSTN (343006) 69.0 kV to 5GRINDSTN (343014) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0941 | 3 Phase fault on 5APCH FLT 161.00 (344028) 161 kV Bus a. Apply fault at the 5APCH FLT 161.00 (344028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0942 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0943 | 3 Phase fault on 5LATHROP 161.00 (344923) 161 kV Bus a. Apply fault at the 5LATHROP 161.00 (344923) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHROP (346093) 69.0 kV to 5LATHROP (344923) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0944 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0945 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0946 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0947 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0948 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0949 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0950 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0951 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to CATOOSA4 (509790) 138.0 kV to CATTER1 1 (512833) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0952 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to CATOOSA4 (509790) 138.0 kV to CATTER2 1 (512834) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0953 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0954 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0955 | 3 Phase fault on PENSA 5 161.00 (512654) 161 kV Bus a. Apply fault at the PENSA 5 161.00 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to PENSA 2 (512628) 69.0 kV to PENSA 1 (512841) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0956 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0957 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0958 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0959 | 3 Phase fault on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138.0 kV to WAKITA 2 (521085) 69.0 kV to WAKITA_13.8 (520435) 13.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0960 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0961 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0962 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0963 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0964 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0965 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0966 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0967 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0968 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0969 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0970 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0971 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0972 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0973 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0974 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0975 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0976 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0977 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 2X1 (532840) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0978 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0979 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0980 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0981 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0982 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0983 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0984 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0985 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0986 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0987 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0988 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0989 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0990 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0991 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0992 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0993 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MCDOWEL3 (533335) 115.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0994 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0995 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0996 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0997 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0998 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_0999 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1000 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1001 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1002 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1003 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1004 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1005 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1006 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1007 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1008 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1009 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1010 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1011 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1012 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1013 | 3 Phase fault on 17TH 4 138.00 (533064) 138 kV Bus a. Apply fault at the 17TH 4 138.00 (533064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1014 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1015 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1016 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1017 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1018 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1019 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1020 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1021 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1022 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1023 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1024 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1025 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN2 (533876) 69.0 kV to FRANKLIN5 (532938) 161.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1026 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1027 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1028 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1029 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1030 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1031 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1032 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1033 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1034 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1035 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1036 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1037 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 2 (541269) 69.0 kV to WBURGE 5 (541228) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1038 | 3 Phase fault on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 2 (541267) 69.0 kV to ODESSA 5 (541229) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1039 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1040 | 3 Phase fault on LEX161 5 161.00 (541232) 161 kV Bus a. Apply fault at the LEX161 5 161.00 (541232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX69 2 (541264) 69.0 kV to LEX161 5 (541232) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1041 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1042 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1043 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1044 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to LBRTYST5 (541248) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1045 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1046 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1047 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1048 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1049 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to ATLNTIC3 (533279) 115.0 kV to ATLNT2X1 (533916) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1050 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to ATLNTIC3 (533279) 115.0 kV to ATLNT1X1 (533915) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1051 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1052 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1053 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1054 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1055 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1056 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1057 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1058 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1059 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1060 | 3 Phase fault on IATAN 7 345.00 (542982) 345 kV Bus a. Apply fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1061 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1062 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1063 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1064 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1065 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1066 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1067 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1068 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1069 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1070 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1071 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1072 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1073 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1074 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1075 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG8 (640101) 69.0 kV to CAMBRIG7 (640100) 115.0 kV to CAMBRIDGET19 (643028) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1076 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 8 (640168) 69.0 kV to ENDERS 7 (640167) 115.0 kV to ENDERS T1 9 (643055) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1077 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1078 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1079 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT8 (640288) 69.0 kV to N.PLATT7 (640287) 115.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1080 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1081 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1082 | 3 Phase fault on VSC2_3 345.00 (992003) 345 kV Bus a. Apply fault at the VSC2_3 345.00 (992003) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VSC2_3 (992003) 345.0 kV to VSC2_2 (992002) 276.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1083 | 3 Phase fault on VSC2_3 345.00 (992003) 345 kV Bus a. Apply fault at the VSC2_3 345.00 (992003) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VSC2_3 (992003) 345.0 kV to VSC2_6 (992006) 276.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1084 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1085 | 3 Phase fault on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1086 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1087 | 3 Phase fault on JOP430 2 69.000 (547608) 69 kV Bus a. Apply fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP430 2 (547608) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1088 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1089 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1090 | 3 Phase fault on SUB M 69.000 (548815) 69 kV Bus a. Apply fault at the SUB M 69.000 (548815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1091 | 3 Phase fault on SUB N 69.000 (548821) 69 kV Bus a. Apply fault at the SUB N 69.000 (548821) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1092 | 3 Phase fault on SUB C 69.000 (548825) 69 kV Bus a. Apply fault at the SUB C 69.000 (548825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB C (548825) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT_1093 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0001 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0002 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0003 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0004 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0005 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0006 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0007 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0008 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0009 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0010 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0011 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0013 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0014 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0015 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0016 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0017 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0018 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0019 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0020 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0021 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0022 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0023 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0024 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0025 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0026 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0027 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0028 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0029 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0030 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-058 (763895) andG19-063 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0031 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-058 (763895) andG19-063 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0032 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0033 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0035 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0036 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0037 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0038 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0039 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0040 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0041 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0042 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0043 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0044 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0045 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0046 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0048 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0049 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT_0051 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0001 | Single Phase Fault with Stuck Breaker on 5GRINDSTN 161.00 (343014) 161 kV Bus a. Apply Fault at the 5GRINDSTN 161.00 (343014) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BOONE (300061) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 b.2. 2GRINDSTN (343006) 69.0 kV to 5GRINDSTN (343014) 161.0 kV Two Winding #1 b.3. 5REBEL (343007) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0002 | Single Phase Fault with Stuck Breaker on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply Fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 b.2. 5PERCHE (343004) 161.0 kV to 2PERCHE (343005) 69.0 kV Two Winding #1 b.3. 5PERCHE (343004) 161.0 kV to 2PERCHE2 (343052) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0003 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0007 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0008 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0010 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 b.3. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0011 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0012 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0013 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0014 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0015 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0016 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-100-TAP (768980) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0017 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0018 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0019 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0020 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0021 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0022 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0023 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0024 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0025 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0026 | Single Phase Fault with Stuck Breaker on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply Fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 b.3. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 b.4. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 b.5. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0027 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-100-TAP (768980) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0028 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0029 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 b.4. SALSBRY5 (543062) 161.0 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0030 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0031 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0032 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0033 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0034 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0035 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NEAST_DG1 (543160) 4.2 kV to NE CT11 (542958) 13.8 kV Two Winding #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 b.6. NEASTN5 (543666) 161.0 kV to Load #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0036 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEAST_DG1 (543160) 4.2 kV to NE CT11 (542958) 13.8 kV Two Winding #1 b.3. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0037 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # b.6. NEASTN5 (543666) 161.0 kV to Load #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0038 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NE CT17 (542983) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT18 (542984) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0039 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NE CT17 (542983) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT18 (542984) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0040 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0041 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0042 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0043 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 b.2. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0044 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0045 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0046 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0047 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0048 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0049 | Single Phase Fault with Stuck Breaker on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply Fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT7 1 (542963) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.2. HAWCT8 1 (542964) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.3. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0050 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to Load #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0051 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NRTHST_B90_1 (543082) 13.8 kV to Load #90 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0052 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NRTHST_B34_1 (543081) 13.8 kV to Load #34 b.3. NEASTN5 (543666) 161.0 kV to Load #78 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0053 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NRTHST_B34_1 (543081) 13.8 kV to Load #34 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0054 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # b.2. NEASTN5 (543666) 161.0 kV to Load #78 b.3. NRTHST_B90_1 (543082) 13.8 kV to Load #90 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0055 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0056 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0057 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0058 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0059 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.4. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0060 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0061 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0062 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0063 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0064 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0065 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0066 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0067 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0068 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 b.2. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0069 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0070 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0071 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0072 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0073 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0074 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0075 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0076 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0077 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0078 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0079 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0080 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0081 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0082 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0083 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0084 | Single Phase Fault with Stuck Breaker on COLBY 3 115.00 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0085 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.3. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0086 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 b.2. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 b.4. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0087 | Single Phase Fault with Stuck Breaker on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply Fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 b.2. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 b.3. ENDERS 7 (640167) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #1 b.4. ENDERS 7 (640167) 115.0 kV to ENDERS 8 (640168) 69.0 kV to ENDERS T1 9 (643055) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0088 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to MCCOOK G (640017) 13.8 kV Two Winding #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.4. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.5. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 b.6. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0089 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.4. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.5. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0090 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.3. N.PLATTG (640018) 13.8 kV to N.PLATT9 (640289) 34.5 kV to N.PLATT7 (640287) 115.0 kV Three Winding #1 b.4. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 b.6. N.PLATT7 (640287) 115.0 kV to N.PLATT8 (640288) 69.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 b.7. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to N.PLATTG (640018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0091 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.3. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.4. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.5. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 b.6. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 b.7. N.PLATT7 (640287) 115.0 kV to N.PLATT8 (640288) 69.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 b.8. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to N.PLATTG (640018) 13.8 kV Three Winding #1 b.9. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to NORTHPLT T79 (643107) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0092 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 b.3. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0093 | Single Phase Fault with Stuck Breaker on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply Fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.6. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.7. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.8. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.9. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 b.10. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.11. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.12. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.13. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.14. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0094 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.4. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.7. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.8. HARPER 4 (539668) 138.0 kV to HARPER 1 (539713) 34.5 kV to HARPER-T (539913) 8.7 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0095 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0096 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0097 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0098 | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply Fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.3. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.4. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.8. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0099 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0100 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.2. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.3. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.4. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.6. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.9. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0101 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.2. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.3. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0102 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 b.4. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0103 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0104 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0105 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0106 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0107 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0108 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0109 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0110 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0111 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0112 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0113 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-065-TAP (768280) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0114 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0115 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0116 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0117 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 b.5. HOLCOMB3 (531448) 115.0 kV to Load #S1 b.6. HOLCOMB3 (531448) 115.0 kV to Load #S2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0118 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0119 | Single Phase Fault with Stuck Breaker on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply Fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. FTDODGP1 (539670) 15.0 kV to FTDODGE3 (539671) 115.0 kV Two Winding #1 b.4. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.5. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 b.6. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. FTDODGE3 (539671) 115.0 kV to FTDDGDV1 (539715) 34.5 kV to FTDODG-T (539915) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0120 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0121 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0122 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0123 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0124 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0125 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0126 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0127 | Single Phase Fault with Stuck Breaker on SPRINGH3 115.00 (533267) 115 kV Bus a. Apply Fault at the SPRINGH3 115.00 (533267) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.4. SPRINGH3 (533267) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0128 | Single Phase Fault with Stuck Breaker on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply Fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.4. SPRINGH3 (533267) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0129 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 b.4. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 2X1 (532840) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0130 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0131 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0132 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0133 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0134 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0135 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC6 1 (532743) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0136 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0137 | Single Phase Fault with Stuck Breaker on GEARY 7 345.00 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.3. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0138 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.3. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0139 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0140 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0141 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0142 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0143 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0144 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0145 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0146 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0147 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0148 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0149 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0150 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0151 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0152 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0153 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0154 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0155 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0156 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0157 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to GEN-2016-174 (588250) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0158 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0159 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0160 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0161 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0162 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0163 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0164 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0165 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0166 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0167 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0168 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0169 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. BLUMILS5 (543004) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0170 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0171 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0172 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY (548806) 69.0 kV to Load #T2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0173 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0174 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0175 | Single Phase Fault with Stuck Breaker on BLUVLY 69.000 (548806) 69 kV Bus a. Apply Fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.3. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.4. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.5. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 b.6. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 b.7. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 b.8. BLUVLY (548806) 69.0 kV to Load #T1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0176 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.3. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0177 | Single Phase Fault with Stuck Breaker on SUB N-161 161.00 (548820) 161 kV Bus a. Apply Fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0178 | Single Phase Fault with Stuck Breaker on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply Fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 b.2. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0179 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0181 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0182 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0183 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0184 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0185 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0186 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0187 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0188 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0189 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0190 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0191 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0192 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0193 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0194 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0195 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0196 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP5 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0197 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0198 | Single Phase Fault with Stuck Breaker on AFTON 5 161.00 (512632) 161 kV Bus a. Apply Fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.4. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0199 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.2. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.3. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0200 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.2. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.3. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.6. 1CHOTCT2 (300033) 16.0 kV to Load #P2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0201 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.2. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.3. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0202 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.5. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.6. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.7. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.8. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.9. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0203 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0204 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.6. 1CHOTCT4 (300020) 16.0 kV to Load #P1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0205 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.6. 1CHOTCT5 (300021) 16.0 kV to Load #P2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0206 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0207 | Single Phase Fault with Stuck Breaker on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply Fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.5. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0208 | Single Phase Fault with Stuck Breaker on 5APCH FLT 161.00 (344028) 161 kV Bus a. Apply Fault at the 5APCH FLT 161.00 (344028) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.2. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.4. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.5. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0209 | Single Phase Fault with Stuck Breaker on 5BARNET 161.00 (300057) 161 kV Bus a. Apply Fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.3. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.4. 2BARNET (300618) 69.0 kV to 5BARNET (300057) 161.0 kV Two Winding #1 b.5. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.6. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0210 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 161.00 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 161.00 (344234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5CALIF (300063) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.4. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.5. 1CALIF (346027) 34.5 kV to 5CALIF UE 2 (344234) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0211 | Single Phase Fault with Stuck Breaker on 5JC ZION 161.00 (344814) 161 kV Bus a. Apply Fault at the 5JC ZION 161.00 (344814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.2. 5MARIOSA (345027) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.3. 5JC ZION (344814) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #z b.4. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.5. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.6. 2JC ZION (346089) 69.0 kV to 5JC ZION (344814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0212 | Single Phase Fault with Stuck Breaker on 5ELDON 2 161.00 (344533) 161 kV Bus a. Apply Fault at the 5ELDON 2 161.00 (344533) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.3. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.4. 2BARNET (300618) 69.0 kV to 5BARNET (300057) 161.0 kV Two Winding #1 b.5. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.6. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.7. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.8. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 b.9. 1ELDON 2 (346045) 34.5 kV to 5ELDON 2 (344533) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0213 | Single Phase Fault with Stuck Breaker on 5ELDON 2 161.00 (344533) 161 kV Bus a. Apply Fault at the 5ELDON 2 161.00 (344533) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.2. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.3. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.4. 4OSAGE (345400) 138.0 kV to 4OSG_1&2TAP (345401) 138.0 kV Transmission Circuit #z b.5. 4OSAGE (345400) 138.0 kV to 4OSG_5&6TAP (345406) 138.0 kV Transmission Circuit #1 b.6. 4OSAGE (345400) 138.0 kV to 4OSG_7&8TAP (345407) 138.0 kV Transmission Circuit #1 b.7. 4OSAGE (345400) 138.0 kV to 1OSAGE (346116) 34.5 kV Two Winding #1 b.8. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.9. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 b.10. 1ELDON 2 (346045) 34.5 kV to 5ELDON 2 (344533) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0214 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 161.00 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 161.00 (344234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CALIF (300063) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.2. 2CALIF (300550) 69.0 kV to 5CALIF (300063) 161.0 kV Two Winding #2 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.4. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z b.5. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.6. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 b.7. 1CALIF (346027) 34.5 kV to 5CALIF UE 2 (344234) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0215 | Single Phase Fault with Stuck Breaker on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply Fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0216 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.4. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.5. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0217 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0218 | Single Phase Fault with Stuck Breaker on RIV167 5 161.00 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0219 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0220 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.4. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0221 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0222 | Single Phase Fault with Stuck Breaker on FIR417 5 161.00 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 161.00 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0223 | Single Phase Fault with Stuck Breaker on OAK432 5 161.00 (547494) 161 kV Bus a. Apply Fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0224 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. OAK432 5 (547494) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0225 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0226 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0227 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0228 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0229 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0230 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0231 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0232 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0233 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0234 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0235 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0236 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0237 | Single Phase Fault with Stuck Breaker on 5APCH TP 161.00 (344026) 161 kV Bus a. Apply Fault at the 5APCH TP 161.00 (344026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.4. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.5. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0238 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0239 | Single Phase Fault with Stuck Breaker on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply Fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5LOYMART 1 (344040) 161.0 kV to 5LOYMART 2 (344041) 161.0 kV Transmission Circuit #z b.3. 5LOYMART 1 (344040) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.4. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.5. 5J994 SUB (344656) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.6. 5GUTHRIE 1 (344677) 161.0 kV to 5GUTHRIE 2 (344678) 161.0 kV Transmission Circuit #z b.7. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.8. 1LOYMART 1 (346010) 12.5 kV to 5LOYMART 1 (344040) 161.0 kV Two Winding #1 b.9. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0240 | Single Phase Fault with Stuck Breaker on 5ELDON 2 161.00 (344533) 161 kV Bus a. Apply Fault at the 5ELDON 2 161.00 (344533) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.2. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.3. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.4. 4OSAGE (345400) 138.0 kV to 4OSG_1&2TAP (345401) 138.0 kV Transmission Circuit #z b.5. 4OSAGE (345400) 138.0 kV to 4OSG_3&4TAP (345404) 138.0 kV Transmission Circuit #z b.6. 4OSAGE (345400) 138.0 kV to 4OSG_5&6TAP (345406) 138.0 kV Transmission Circuit #1 b.7. 4OSAGE (345400) 138.0 kV to 4OSG_7&8TAP (345407) 138.0 kV Transmission Circuit #1 b.8. 4OSAGE (345400) 138.0 kV to 1OSAGE (346116) 34.5 kV Two Winding #1 b.9. 4OSAGE (345400) 138.0 kV to 1OSAGE (346116) 34.5 kV Two Winding #2 b.10. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.11. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 b.12. 1ELDON 2 (346045) 34.5 kV to 5ELDON 2 (344533) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0241 | Single Phase Fault with Stuck Breaker on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply Fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LOYMART 1 (344040) 161.0 kV to 5LOYMART 2 (344041) 161.0 kV Transmission Circuit #z b.2. 5LOYMART 1 (344040) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.3. 5J994 SUB (344656) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.4. 5GUTHRIE 1 (344677) 161.0 kV to 5GUTHRIE 2 (344678) 161.0 kV Transmission Circuit #z b.5. 5GUTHRIE 2 (344678) 161.0 kV to 5MONTGMRY 1 (345231) 161.0 kV Transmission Circuit #1 b.6. 5GUTHRIE 2 (344678) 161.0 kV to 5MOREAU 1 (345239) 161.0 kV Transmission Circuit #1 b.7. 1LOYMART 1 (346010) 12.5 kV to 5LOYMART 1 (344040) 161.0 kV Two Winding #1 b.8. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0242 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.6. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.7. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0243 | Single Phase Fault with Stuck Breaker on 5JC ZION 161.00 (344814) 161 kV Bus a. Apply Fault at the 5JC ZION 161.00 (344814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.2. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.3. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.4. 5JC ZION (344814) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #z b.5. 2JC ZION (346089) 69.0 kV to 5JC ZION (344814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0244 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0245 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.4. NE CT17 (542983) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT18 (542984) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0246 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0247 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0248 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0249 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0250 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0251 | Single Phase Fault with Stuck Breaker on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply Fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.6. NKMA2 1 (530630) 12.5 kV to NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0252 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0253 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.4. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.5. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0254 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0255 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.4. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.5. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0256 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0257 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0258 | Single Phase Fault with Stuck Breaker on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply Fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0259 | Single Phase Fault with Stuck Breaker on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. RULETON3 (531357) 115.0 kV to LAWNRID3 (531368) 115.0 kV Transmission Circuit #1 b.5. BIRDCTY3 (531365) 115.0 kV to STFRAN 3 (531370) 115.0 kV Transmission Circuit #1 b.6. BIRDCTY3 (531365) 115.0 kV to MCDONLD3 (531487) 115.0 kV Transmission Circuit #1 b.7. LAWNRID3 (531368) 115.0 kV to STFRANT3 (531471) 115.0 kV Transmission Circuit #1 b.8. STFRAN 3 (531370) 115.0 kV to STFRANT3 (531471) 115.0 kV Transmission Circuit #1 b.9. CSTFRAN3 (531441) 115.0 kV to STFRANT3 (531471) 115.0 kV Transmission Circuit #1 b.10. MCDONLD3 (531487) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.11. BVERVLLY (531488) 115.0 kV to ONEOK 3 (531489) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0260 | Single Phase Fault with Stuck Breaker on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. LUDELLT3 (531220) 115.0 kV to LUDELL 3 (531221) 115.0 kV Transmission Circuit #1 b.5. LUDELLT3 (531220) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.6. LUDELLT3 (531220) 115.0 kV to HERNDON3 (531367) 115.0 kV Transmission Circuit #1 b.7. ATWODSW3 (531364) 115.0 kV to NATWOOD3 (531369) 115.0 kV Transmission Circuit #1 b.8. HERNDON3 (531367) 115.0 kV to JOHNSON3 (531371) 115.0 kV Transmission Circuit #1 b.9. JOHNSON3 (531371) 115.0 kV to OBER T 3 (531457) 115.0 kV Transmission Circuit #1 b.10. NORCATR3 (531372) 115.0 kV to RHOADES3 (531373) 115.0 kV Transmission Circuit #1 b.11. NORCATR3 (531372) 115.0 kV to OBER T 3 (531457) 115.0 kV Transmission Circuit #1 b.12. OBER T 3 (531457) 115.0 kV to OBERLIN3 (531458) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0261 | Single Phase Fault with Stuck Breaker on GEM_SW 3 115.00 (530713) 115 kV Bus a. Apply Fault at the GEM_SW 3 115.00 (530713) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. SEGNTP 3 (530682) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.3. GEM_SW 3 (530713) 115.0 kV to COLBY_PUMP3 (530716) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0262 | Single Phase Fault with Stuck Breaker on SEGNTP 3 115.00 (530682) 115 kV Bus a. Apply Fault at the SEGNTP 3 115.00 (530682) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.3. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.4. SEGNTP 3 (530682) 115.0 kV to SEGUIN 3 (530683) 115.0 kV Transmission Circuit #1 b.5. SEGNTP 3 (530682) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.6. SEGUIN 3 (530683) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0263 | Single Phase Fault with Stuck Breaker on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply Fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.2. PH RUN 3 (530559) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 b.3. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. SEGNTP 3 (530682) 115.0 kV to SEGUIN 3 (530683) 115.0 kV Transmission Circuit #1 b.5. SEGUIN 3 (530683) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0264 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.5. BEACH 3 (530557) 115.0 kV to HILLCTY3 (531387) 34.5 kV Two Winding #1 b.6. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.7. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0265 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0266 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0267 | Single Phase Fault with Stuck Breaker on GMEC 3 115.00 (530676) 115 kV Bus a. Apply Fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0268 | Single Phase Fault with Stuck Breaker on SALINE 3 115.00 (530551) 115 kV Bus a. Apply Fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0269 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.5. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.6. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.7. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0270 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0271 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0272 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0273 | Single Phase Fault with Stuck Breaker on NESCTY 3 115.00 (530607) 115 kV Bus a. Apply Fault at the NESCTY 3 115.00 (530607) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NESCTY 3 (530607) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NESCTY 3 (530607) 115.0 kV to NESS-CT1 (539722) 34.5 kV to NES-CT-T (539924) 13.8 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0274 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.9. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0275 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.10. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0276 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0277 | Single Phase Fault with Stuck Breaker on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply Fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.2. PH RUN 3 (530559) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 b.3. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. ARNOLD3 (531409) 115.0 kV to GOVE 3 (531411) 115.0 kV Transmission Circuit #1 b.5. ARNOLD3 (531409) 115.0 kV to RANSOM 3 (531414) 115.0 kV Transmission Circuit #1 b.6. GOVE 3 (531411) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0278 | Single Phase Fault with Stuck Breaker on GODLNDT3 115.00 (531443) 115 kV Bus a. Apply Fault at the GODLNDT3 115.00 (531443) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. BREWSTR3 (531351) 115.0 kV to GOODLND3 (531353) 115.0 kV Transmission Circuit #1 b.3. BREWSTR3 (531351) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. GOODLND3 (531353) 115.0 kV to GODLNDT3 (531443) 115.0 kV Transmission Circuit #1 b.5. RULETON3 (531357) 115.0 kV to GODLNDT3 (531443) 115.0 kV Transmission Circuit #1 b.6. GODLNDT3 (531443) 115.0 kV to GOODCTY3 (531444) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0279 | Single Phase Fault with Stuck Breaker on MINGO 3 115.00 (531429) 115 kV Bus a. Apply Fault at the MINGO 3 115.00 (531429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0280 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.5. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0281 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.5. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.7. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0282 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0283 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0284 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0285 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0286 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0287 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0288 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0289 | Single Phase Fault with Stuck Breaker on SHAYS_230 230.00 (530610) 230 kV Bus a. Apply Fault at the SHAYS_230 230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0290 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 b.8. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0291 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-065-TAP (768280) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0292 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0293 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0294 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0295 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0296 | Single Phase Fault with Stuck Breaker on BUFLOCRK6 230.00 (530688) 230 kV Bus a. Apply Fault at the BUFLOCRK6 230.00 (530688) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.3. BUFLOCRK1 (530689) 34.5 kV to PRWNDCL1 (530701) 34.5 kV Transmission Circuit #1 b.4. PRWINDG1 (530690) 0.7 kV to PRWNDCL1 (530701) 34.5 kV Two Winding #1 b.5. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.8. BUFLOCRK6 (530688) 230.0 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0297 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0298 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0299 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0300 | Single Phase Fault with Stuck Breaker on COLBY 3 115.00 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to Load #1 b.2. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0301 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0302 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0303 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0304 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0305 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0306 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLM1G (640010) 23.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0307 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0308 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.3. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0309 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0310 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0311 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0312 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0313 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0314 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.3. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0315 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0316 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0317 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0318 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0319 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0320 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0321 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0322 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0323 | Single Phase Fault with Stuck Breaker on BARBER 5 161.00 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.3. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.4. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.5. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.6. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0324 | Single Phase Fault with Stuck Breaker on WOLCOTT5 161.00 (546669) 161 kV Bus a. Apply Fault at the WOLCOTT5 161.00 (546669) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.2. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.3. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0325 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0326 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.4. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 b.7. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0327 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0328 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0329 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0330 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0331 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0332 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0333 | Single Phase Fault with Stuck Breaker on J1490_POI 345.00 (44888) 345 kV Bus a. Apply Fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1490_POI (44888) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 b.2. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0334 | Single Phase Fault with Stuck Breaker on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply Fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 b.2. 7KINGDM (300043) 345.0 kV to 5KINGDMB1 (300090) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0335 | Single Phase Fault with Stuck Breaker on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply Fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to VSC2_3 (992003) 345.0 kV Transmission Circuit #1 b.2. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0336 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to 5MORGANXF2 (301622) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0337 | Single Phase Fault with Stuck Breaker on 5BOONE 161.00 (300061) 161 kV Bus a. Apply Fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BOONE (300061) 161.0 kV to 5MLRSBGB1 (300519) 161.0 kV Transmission Circuit #1 b.2. 5BOONE (300061) 161.0 kV to 2BOONE (300493) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0338 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 b.2. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0339 | Single Phase Fault with Stuck Breaker on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply Fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LATHRP (300091) 161.0 kV to 5MPLTAP (300036) 161.0 kV Transmission Circuit #1 b.2. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0340 | Single Phase Fault with Stuck Breaker on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply Fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 b.2. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0341 | Single Phase Fault with Stuck Breaker on 5NORTON 161.00 (300105) 161 kV Bus a. Apply Fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 b.2. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0342 | Single Phase Fault with Stuck Breaker on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply Fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 b.2. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0343 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to 2SEDALI (300541) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0344 | Single Phase Fault with Stuck Breaker on 5MCBAINB1 161.00 (300501) 161 kV Bus a. Apply Fault at the 5MCBAINB1 161.00 (300501) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB1 (300501) 161.0 kV to 5MCBAINB2 (301489) 161.0 kV Transmission Circuit #z1 b.2. 5MCBAINB1 (300501) 161.0 kV to 5BOONE (300061) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0345 | Single Phase Fault with Stuck Breaker on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply Fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0346 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0347 | Single Phase Fault with Stuck Breaker on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply Fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0348 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 b.2. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0349 | Single Phase Fault with Stuck Breaker on 5CALIF 161.00 (300063) 161 kV Bus a. Apply Fault at the 5CALIF 161.00 (300063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CALIF (300550) 69.0 kV to 5CALIF (300063) 161.0 kV Two Winding #2 b.2. 2CALIF (300550) 69.0 kV to 2FORTNA (300554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0350 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0351 | Single Phase Fault with Stuck Breaker on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply Fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 b.2. 5LAMAR (300794) 161.0 kV to 2LAMR (300651) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0352 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to 5JASPER (300950) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0353 | Single Phase Fault with Stuck Breaker on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply Fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PLATCTY (301552) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #z1 b.2. 5PLATCTY (301552) 161.0 kV to 2PLATCTY (300307) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0354 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0355 | Single Phase Fault with Stuck Breaker on MIDLTNT4 138.00 (514804) 138 kV Bus a. Apply Fault at the MIDLTNT4 138.00 (514804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.2. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0356 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0357 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0358 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0359 | Single Phase Fault with Stuck Breaker on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0360 | Single Phase Fault with Stuck Breaker on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply Fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to JAGGER 3 (531360) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0361 | Single Phase Fault with Stuck Breaker on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply Fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEOTI 3 (531428) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 b.2. LEOTI 3 (531428) 115.0 kV to SELKIRK3 (531434) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0362 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 b.2. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0363 | Single Phase Fault with Stuck Breaker on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply Fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 b.2. SCOTCTY3 (531433) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0364 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0365 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 b.2. SETAB 3 (531464) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0366 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #2 b.2. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0367 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0368 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0369 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0370 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0371 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0372 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0373 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0374 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0375 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0376 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0377 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0378 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0379 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0380 | Single Phase Fault with Stuck Breaker on BURNS 7 345.00 (532803) 345 kV Bus a. Apply Fault at the BURNS 7 345.00 (532803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURNS 7 (532803) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. BURNS 7 (532803) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0381 | Single Phase Fault with Stuck Breaker on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0382 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 7 (532770) 345.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 b.2. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0383 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 b.2. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0384 | Single Phase Fault with Stuck Breaker on BAKER 2 69.000 (532926) 69 kV Bus a. Apply Fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0385 | Single Phase Fault with Stuck Breaker on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 b.2. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0386 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. MARMTNW5 (532935) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0387 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.2. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0388 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to LITCH 5 (532932) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0389 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to MIDLTNT4 (514804) 138.0 kV Transmission Circuit #1 b.2. CRESWLN4 (532981) 138.0 kV to CRESWLS2 (533573) 69.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0390 | Single Phase Fault with Stuck Breaker on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply Fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 4 (532982) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0391 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0392 | Single Phase Fault with Stuck Breaker on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply Fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.2. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0393 | Single Phase Fault with Stuck Breaker on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0394 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 4 (532996) 138.0 kV to TIOGA 2 (533646) 69.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0395 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK4 (532997) 138.0 kV to BUTLER 4 (532987) 138.0 kV Transmission Circuit #1 b.2. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0396 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. ALTOONA4 (533001) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0397 | Single Phase Fault with Stuck Breaker on DEARING4 138.00 (533002) 138 kV Bus a. Apply Fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0398 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0399 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONTGOM4 (533004) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0400 | Single Phase Fault with Stuck Breaker on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply Fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0401 | Single Phase Fault with Stuck Breaker on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply Fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0402 | Single Phase Fault with Stuck Breaker on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply Fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to HALSTD 4 (533011) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0403 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.2. NEOSHOS4 (533020) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0404 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.2. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0405 | Single Phase Fault with Stuck Breaker on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply Fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0406 | Single Phase Fault with Stuck Breaker on BU11PON4 138.00 (533032) 138 kV Bus a. Apply Fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BU11PON4 (533032) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0407 | Single Phase Fault with Stuck Breaker on CENTENN4 138.00 (533034) 138 kV Bus a. Apply Fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0408 | Single Phase Fault with Stuck Breaker on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0409 | Single Phase Fault with Stuck Breaker on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply Fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0410 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0411 | Single Phase Fault with Stuck Breaker on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply Fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0412 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0413 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to EVANS N4 (533040) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0414 | Single Phase Fault with Stuck Breaker on FARBER 4 138.00 (533042) 138 kV Bus a. Apply Fault at the FARBER 4 138.00 (533042) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0415 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0416 | Single Phase Fault with Stuck Breaker on GILL W 4 138.00 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.2. GILL W 4 (533045) 138.0 kV to GILL E 4 (533044) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0417 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.2. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0418 | Single Phase Fault with Stuck Breaker on GILL 4 138.00 (533047) 138 kV Bus a. Apply Fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL 4 (533047) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0419 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0420 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERS4 (533050) 138.0 kV to HOOVERN4 (533049) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0421 | Single Phase Fault with Stuck Breaker on 47TH ST4 138.00 (533058) 138 kV Bus a. Apply Fault at the 47TH ST4 138.00 (533058) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0422 | Single Phase Fault with Stuck Breaker on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. ROSEHIL4 (533062) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0423 | Single Phase Fault with Stuck Breaker on WACO S 4 138.00 (533071) 138 kV Bus a. Apply Fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WACO S 4 (533071) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #1 b.2. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0424 | Single Phase Fault with Stuck Breaker on WACO 4 138.00 (533072) 138 kV Bus a. Apply Fault at the WACO 4 138.00 (533072) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 b.2. WACO 4 (533072) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0425 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0426 | Single Phase Fault with Stuck Breaker on 4CORNER3 115.00 (533158) 115 kV Bus a. Apply Fault at the 4CORNER3 115.00 (533158) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CORNER3 (533158) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.2. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0427 | Single Phase Fault with Stuck Breaker on OSAGE J3 115.00 (533171) 115 kV Bus a. Apply Fault at the OSAGE J3 115.00 (533171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE J3 (533171) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.2. OSAGE J3 (533171) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0428 | Single Phase Fault with Stuck Breaker on EAST ST3 115.00 (533301) 115 kV Bus a. Apply Fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.2. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0429 | Single Phase Fault with Stuck Breaker on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply Fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0430 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LANG 3 (533304) 115.0 kV to LANG 7 (532769) 345.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 b.2. LANG 3 (533304) 115.0 kV to EAST ST3 (533301) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0431 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 3 (533305) 115.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 b.2. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0432 | Single Phase Fault with Stuck Breaker on READING3 115.00 (533306) 115 kV Bus a. Apply Fault at the READING3 115.00 (533306) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. READING3 (533306) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 b.2. READING3 (533306) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0433 | Single Phase Fault with Stuck Breaker on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply Fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (533307) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0434 | Single Phase Fault with Stuck Breaker on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply Fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0435 | Single Phase Fault with Stuck Breaker on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.2. WEMPORI3 (533309) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0436 | Single Phase Fault with Stuck Breaker on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply Fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WMBROSJ3 (533311) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0437 | Single Phase Fault with Stuck Breaker on BURLJCT2 69.000 (533626) 69 kV Bus a. Apply Fault at the BURLJCT2 69.000 (533626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0438 | Single Phase Fault with Stuck Breaker on CC2SHAR2 69.000 (533629) 69 kV Bus a. Apply Fault at the CC2SHAR2 69.000 (533629) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC2SHAR2 (533629) 69.0 kV to CC5SHAR1 (533888) 12.5 kV Two Winding #1 b.2. CC2SHAR2 (533629) 69.0 kV to CC6SHAR1 (533889) 12.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0439 | Single Phase Fault with Stuck Breaker on CC3WEST2 69.000 (533630) 69 kV Bus a. Apply Fault at the CC3WEST2 69.000 (533630) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC3WEST2 (533630) 69.0 kV to BURLJCT2 (533626) 69.0 kV Transmission Circuit #1 b.2. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0440 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0441 | Single Phase Fault with Stuck Breaker on UN1ELSM2 69.000 (533647) 69 kV Bus a. Apply Fault at the UN1ELSM2 69.000 (533647) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UN1ELSM2 (533647) 69.0 kV to MARMATN2 (533639) 69.0 kV Transmission Circuit #1 b.2. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0442 | Single Phase Fault with Stuck Breaker on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply Fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0443 | Single Phase Fault with Stuck Breaker on LABETTS2 69.000 (533696) 69 kV Bus a. Apply Fault at the LABETTS2 69.000 (533696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0444 | Single Phase Fault with Stuck Breaker on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply Fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0445 | Single Phase Fault with Stuck Breaker on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply Fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0446 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 b.2. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0447 | Single Phase Fault with Stuck Breaker on BELL 2 69.000 (533783) 69 kV Bus a. Apply Fault at the BELL 2 69.000 (533783) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELL 2 (533783) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 b.2. BELL 2 (533783) 69.0 kV to SC3MILL2 (533552) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0448 | Single Phase Fault with Stuck Breaker on CANAL 4 138.00 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 138.00 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALS 2 (533784) 69.0 kV to CANAL 4 (533033) 138.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 b.2. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0449 | Single Phase Fault with Stuck Breaker on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply Fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0450 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.2. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0451 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL W 2 (533796) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 b.2. GILL W 2 (533796) 69.0 kV to GILL E 4 (533044) 138.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0452 | Single Phase Fault with Stuck Breaker on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply Fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILLJCT2 (533798) 69.0 kV to GILL E 2 (533795) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0453 | Single Phase Fault with Stuck Breaker on HAYSVJS2 69.000 (533802) 69 kV Bus a. Apply Fault at the HAYSVJS2 69.000 (533802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYSVJS2 (533802) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #1 b.2. HAYSVJS2 (533802) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0454 | Single Phase Fault with Stuck Breaker on HAYSVJN2 69.000 (533804) 69 kV Bus a. Apply Fault at the HAYSVJN2 69.000 (533804) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYSVJN2 (533804) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #1 b.2. HAYSVJN2 (533804) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0455 | Single Phase Fault with Stuck Breaker on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply Fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0456 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERS2 (533806) 69.0 kV to HOOVERS4 (533050) 138.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 b.2. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0457 | Single Phase Fault with Stuck Breaker on HYDRJN2 69.000 (533808) 69 kV Bus a. Apply Fault at the HYDRJN2 69.000 (533808) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDRJN2 (533808) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 b.2. HYDRJN2 (533808) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0458 | Single Phase Fault with Stuck Breaker on HYDRJS2 69.000 (533810) 69 kV Bus a. Apply Fault at the HYDRJS2 69.000 (533810) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDRJS2 (533810) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 b.2. HYDRJS2 (533810) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0459 | Single Phase Fault with Stuck Breaker on LIN 2 69.000 (533812) 69 kV Bus a. Apply Fault at the LIN 2 69.000 (533812) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.2. LIN 2 (533812) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0460 | Single Phase Fault with Stuck Breaker on MACARTH2 69.000 (533813) 69 kV Bus a. Apply Fault at the MACARTH2 69.000 (533813) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MACARTH2 (533813) 69.0 kV to GILL E 2 (533795) 69.0 kV Transmission Circuit #1 b.2. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0461 | Single Phase Fault with Stuck Breaker on BLF-CRK4 138.00 (539002) 138 kV Bus a. Apply Fault at the BLF-CRK4 138.00 (539002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLF-CRK4 (539002) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0462 | Single Phase Fault with Stuck Breaker on CLDWELL4 138.00 (539003) 138 kV Bus a. Apply Fault at the CLDWELL4 138.00 (539003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLDWELL4 (539003) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0463 | Single Phase Fault with Stuck Breaker on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. MILAN_GOAB (539008) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0464 | Single Phase Fault with Stuck Breaker on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply Fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0465 | Single Phase Fault with Stuck Breaker on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply Fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0466 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to GRTBEND3 (539678) 115.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0467 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.2. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0468 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0469 | Single Phase Fault with Stuck Breaker on FORD 3 115.00 (539758) 115 kV Bus a. Apply Fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0470 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.2. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0471 | Single Phase Fault with Stuck Breaker on NFTDODG3 115.00 (539771) 115 kV Bus a. Apply Fault at the NFTDODG3 115.00 (539771) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NFTDODG3 (539771) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #2 b.2. NFTDODG3 (539771) 115.0 kV to SPRVL 3 (539759) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0472 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0473 | Single Phase Fault with Stuck Breaker on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply Fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345.0 kV to GEN-2008-124 (579480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0474 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0475 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0476 | Single Phase Fault with Stuck Breaker on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 b.2. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0477 | Single Phase Fault with Stuck Breaker on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. SMTHVL 5 (541204) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0478 | Single Phase Fault with Stuck Breaker on KCI 5 161.00 (541212) 161 kV Bus a. Apply Fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KCI 5 (541212) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. KCI 5 (541212) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0479 | Single Phase Fault with Stuck Breaker on FRLVW 5 161.00 (541213) 161 kV Bus a. Apply Fault at the FRLVW 5 161.00 (541213) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRLVW 5 (541213) 161.0 kV to KCI 5 (541212) 161.0 kV Transmission Circuit #1 b.2. FRLVW 5 (541213) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0480 | Single Phase Fault with Stuck Breaker on TWA 5 161.00 (541214) 161 kV Bus a. Apply Fault at the TWA 5 161.00 (541214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 b.2. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0481 | Single Phase Fault with Stuck Breaker on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply Fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 b.2. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0482 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0483 | Single Phase Fault with Stuck Breaker on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply Fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. PLTCTY 5 (541221) 161.0 kV to KCI 5 (541212) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0484 | Single Phase Fault with Stuck Breaker on GRAINVL5 161.00 (541226) 161 kV Bus a. Apply Fault at the GRAINVL5 161.00 (541226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAINVL5 (541226) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 b.2. GRAINVL5 (541226) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0485 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRIDGE5 (541230) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0486 | Single Phase Fault with Stuck Breaker on LEX161 5 161.00 (541232) 161 kV Bus a. Apply Fault at the LEX161 5 161.00 (541232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. LEX161 5 (541232) 161.0 kV to LEX69 2 (541264) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0487 | Single Phase Fault with Stuck Breaker on RICHMND5 161.00 (541236) 161 kV Bus a. Apply Fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to LEX161 5 (541232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0488 | Single Phase Fault with Stuck Breaker on BLSPW 5 161.00 (541237) 161 kV Bus a. Apply Fault at the BLSPW 5 161.00 (541237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPW 5 (541237) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0489 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDEAST5 (541241) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 b.2. SEDEAST5 (541241) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0490 | Single Phase Fault with Stuck Breaker on LBRTYWT5 161.00 (541247) 161 kV Bus a. Apply Fault at the LBRTYWT5 161.00 (541247) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYWT5 (541247) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 b.2. LBRTYWT5 (541247) 161.0 kV to HLLMRK 5 (541215) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0491 | Single Phase Fault with Stuck Breaker on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply Fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. LBRTYST5 (541248) 161.0 kV to LIBRTYS2 (543095) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0492 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 b.2. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0493 | Single Phase Fault with Stuck Breaker on STALEY 2 69.000 (541261) 69 kV Bus a. Apply Fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STALEY 2 (541261) 69.0 kV to RNRDGE 2 (541260) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0494 | Single Phase Fault with Stuck Breaker on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply Fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY2 (541262) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 b.2. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0495 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 b.2. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0496 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0497 | Single Phase Fault with Stuck Breaker on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply Fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDN 2 (541271) 69.0 kV Transmission Circuit #1 b.2. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0498 | Single Phase Fault with Stuck Breaker on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply Fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDS 2 (541272) 69.0 kV Transmission Circuit #1 b.2. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0499 | Single Phase Fault with Stuck Breaker on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply Fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDPLT 2 (541275) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 b.2. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0500 | Single Phase Fault with Stuck Breaker on COLECMP2 69.000 (541276) 69 kV Bus a. Apply Fault at the COLECMP2 69.000 (541276) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLECMP2 (541276) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 b.2. COLECMP2 (541276) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0501 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAFBE_SW5 (541337) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. WAFBE_SW5 (541337) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0502 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 b.2. S.HARP 5 (541341) 161.0 kV to ARCHIE 5 (541207) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0503 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0504 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0505 | Single Phase Fault with Stuck Breaker on KNOSTERTP 69.000 (541534) 69 kV Bus a. Apply Fault at the KNOSTERTP 69.000 (541534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOSTERTP (541534) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 b.2. KNOSTERTP (541534) 69.0 kV to MONSERTP (541524) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0506 | Single Phase Fault with Stuck Breaker on LAMONTETP 69.000 (541535) 69 kV Bus a. Apply Fault at the LAMONTETP 69.000 (541535) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMONTETP (541535) 69.0 kV to SEDN 2 (541271) 69.0 kV Transmission Circuit #1 b.2. LAMONTETP (541535) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0507 | Single Phase Fault with Stuck Breaker on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply Fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0508 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to ATLNTIC7 (542940) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0509 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0510 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 b.2. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0511 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0512 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0513 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LAC G1 1 (542955) 22.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0514 | Single Phase Fault with Stuck Breaker on TROOST 5 161.00 (542986) 161 kV Bus a. Apply Fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 b.2. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0515 | Single Phase Fault with Stuck Breaker on GRAND 5 161.00 (542987) 161 kV Bus a. Apply Fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0516 | Single Phase Fault with Stuck Breaker on GRAND W5 161.00 (542988) 161 kV Bus a. Apply Fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0517 | Single Phase Fault with Stuck Breaker on NAVY 5 161.00 (542989) 161 kV Bus a. Apply Fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NAVY 5 (542989) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0518 | Single Phase Fault with Stuck Breaker on CROSTWN5 161.00 (542990) 161 kV Bus a. Apply Fault at the CROSTWN5 161.00 (542990) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSTWN5 (542990) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. CROSTWN5 (542990) 161.0 kV to TROOST 5 (542986) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0519 | Single Phase Fault with Stuck Breaker on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply Fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDTOWN5 (542996) 161.0 kV to TROOST 5 (542986) 161.0 kV Transmission Circuit #1 b.2. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0520 | Single Phase Fault with Stuck Breaker on LEEDS 5 161.00 (542997) 161 kV Bus a. Apply Fault at the LEEDS 5 161.00 (542997) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEEDS 5 (542997) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0521 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0522 | Single Phase Fault with Stuck Breaker on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0523 | Single Phase Fault with Stuck Breaker on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to AVONDAL5 (543015) 161.0 kV Transmission Circuit #1 b.2. GLADSTN5 (543016) 161.0 kV to GLADSTN_CAP5 (542946) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0524 | Single Phase Fault with Stuck Breaker on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply Fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 b.2. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0525 | Single Phase Fault with Stuck Breaker on BARRY 5 161.00 (543019) 161 kV Bus a. Apply Fault at the BARRY 5 161.00 (543019) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRY 5 (543019) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. BARRY 5 (543019) 161.0 kV to BARRY_CAP 5 (542944) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0526 | Single Phase Fault with Stuck Breaker on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply Fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMGHAM5 (543020) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.2. BRMGHAM5 (543020) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0527 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV to NASHUA 7 (542980) 345.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 b.2. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0528 | Single Phase Fault with Stuck Breaker on SHOLCRK5 161.00 (543029) 161 kV Bus a. Apply Fault at the SHOLCRK5 161.00 (543029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHOLCRK5 (543029) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. SHOLCRK5 (543029) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0529 | Single Phase Fault with Stuck Breaker on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply Fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 b.2. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0530 | Single Phase Fault with Stuck Breaker on COURTNY2 69.000 (543085) 69 kV Bus a. Apply Fault at the COURTNY2 69.000 (543085) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0531 | Single Phase Fault with Stuck Breaker on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply Fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0532 | Single Phase Fault with Stuck Breaker on BLUSPRG2 69.000 (543088) 69 kV Bus a. Apply Fault at the BLUSPRG2 69.000 (543088) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0533 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 b.2. DUNCNRD2 (543091) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0534 | Single Phase Fault with Stuck Breaker on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply Fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUGRCK_TP_E2 (543165) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 b.2. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0535 | Single Phase Fault with Stuck Breaker on DAKOTA_5 161.00 (543650) 161 kV Bus a. Apply Fault at the DAKOTA_5 161.00 (543650) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAKOTA_5 (543650) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #1 b.2. DAKOTA_5 (543650) 161.0 kV to CNTRVIL5 (543065) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0536 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0537 | Single Phase Fault with Stuck Breaker on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply Fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0538 | Single Phase Fault with Stuck Breaker on COL 94 2 69.000 (547530) 69 kV Bus a. Apply Fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0539 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 2 (547539) 69.0 kV to JOP145 5 (547470) 161.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 b.2. JOP145 2 (547539) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0540 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to RIV4525 (547469) 161.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 b.2. RIV167 2 (547541) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0541 | Single Phase Fault with Stuck Breaker on BAX271 2 69.000 (547554) 69 kV Bus a. Apply Fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.2. BAX271 2 (547554) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0542 | Single Phase Fault with Stuck Breaker on GLF339 2 69.000 (547690) 69 kV Bus a. Apply Fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLF339 2 (547690) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0543 | Single Phase Fault with Stuck Breaker on SUB I 69.000 (548800) 69 kV Bus a. Apply Fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 b.2. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0544 | Single Phase Fault with Stuck Breaker on SUB K 69.000 (548801) 69 kV Bus a. Apply Fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0545 | Single Phase Fault with Stuck Breaker on SUB H 69.000 (548802) 69 kV Bus a. Apply Fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB H (548802) 69.0 kV to COURTNY2 (543085) 69.0 kV Transmission Circuit #1 b.2. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0546 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0547 | Single Phase Fault with Stuck Breaker on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply Fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0548 | Single Phase Fault with Stuck Breaker on SUB B 69.000 (548810) 69 kV Bus a. Apply Fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 b.2. SUB B (548810) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0549 | Single Phase Fault with Stuck Breaker on SUB J 69.000 (548811) 69 kV Bus a. Apply Fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB J (548811) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0550 | Single Phase Fault with Stuck Breaker on G15052_T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15052_T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15052_T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15052_T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0551 | Single Phase Fault with Stuck Breaker on G16-046-TAP 345.00 (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP 345.00 (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0552 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0553 | Single Phase Fault with Stuck Breaker on GEN-2022-161345.00 (562477) 345 kV Bus a. Apply Fault at the GEN-2022-161345.00 (562477) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-161 (562477) 345.0 kV to GEN-2014-001 (583850) 345.0 kV Transmission Circuit #z1 b.2. GEN-2022-161 (562477) 345.0 kV to G22-161XFMR2 (770205) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0554 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583850) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583850) 345.0 kV to GEN-2014-001 (583859) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583850) 345.0 kV to GEN-2022-161 (562477) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0555 | Single Phase Fault with Stuck Breaker on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply Fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-074 (587680) 345.0 kV to G16-074XFMR1 (587681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0556 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR1 (588361) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0557 | Single Phase Fault with Stuck Breaker on G16-153-TAP 345.00 (588364) 345 kV Bus a. Apply Fault at the G16-153-TAP 345.00 (588364) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-153-TAP (588364) 345.0 kV to GEN-2016-153 (588360) 345.0 kV Transmission Circuit #1 b.2. G16-153-TAP (588364) 345.0 kV to GEN-2017-086 (589240) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0558 | Single Phase Fault with Stuck Breaker on GEN-2017-005161.00 (588500) 161 kV Bus a. Apply Fault at the GEN-2017-005161.00 (588500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-005 (588500) 161.0 kV to G17-005XFMR1 (588501) 34.5 kV Two Winding #1 b.2. GEN-2017-005 (588500) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0559 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0560 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0561 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0562 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0563 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0564 | Single Phase Fault with Stuck Breaker on GI-95_POI 345.00 (709500) 345 kV Bus a. Apply Fault at the GI-95_POI 345.00 (709500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI-95_POI (709500) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. GI-95_POI (709500) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0565 | Single Phase Fault with Stuck Breaker on GEN-2017-183345.00 (761376) 345 kV Bus a. Apply Fault at the GEN-2017-183345.00 (761376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-183 (761376) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-183 (761376) 345.0 kV to G17-184XFMR2 (761401) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0566 | Single Phase Fault with Stuck Breaker on GEN-2018-125345.00 (763406) 345 kV Bus a. Apply Fault at the GEN-2018-125345.00 (763406) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-125 (763406) 345.0 kV to G18-125-XFM1 (763407) 34.5 kV Two Winding #1 b.2. GEN-2018-125 (763406) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0567 | Single Phase Fault with Stuck Breaker on GEN-2018-128345.00 (763417) 345 kV Bus a. Apply Fault at the GEN-2018-128345.00 (763417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-128 (763417) 345.0 kV to G18-128-XFM1 (763418) 34.5 kV Two Winding #1 b.2. GEN-2018-128 (763417) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0568 | Single Phase Fault with Stuck Breaker on GEN-2019-030345.00 (763670) 345 kV Bus a. Apply Fault at the GEN-2019-030345.00 (763670) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-030 (763670) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 b.2. GEN-2019-030 (763670) 345.0 kV to G19-030-XFM1 (763671) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0569 | Single Phase Fault with Stuck Breaker on G19-053/055 230.00 (763846) 230 kV Bus a. Apply Fault at the G19-053/055 230.00 (763846) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-053/055 (763846) 230.0 kV to G19-055-XFM1 (763869) 34.5 kV Two Winding #1 b.2. G19-053/055 (763846) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0570 | Single Phase Fault with Stuck Breaker on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply Fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0571 | Single Phase Fault with Stuck Breaker on G19-054/068 230.00 (763857) 230 kV Bus a. Apply Fault at the G19-054/068 230.00 (763857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054/068 (763857) 230.0 kV to G19-054-XFM1 (763858) 34.5 kV Two Winding #1 b.2. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0572 | Single Phase Fault with Stuck Breaker on GEN-2020-072161.00 (764345) 161 kV Bus a. Apply Fault at the GEN-2020-072161.00 (764345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-072 (764345) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-072 (764345) 161.0 kV to G20-072-XFM1 (764348) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0573 | Single Phase Fault with Stuck Breaker on GEN-2020-090345.00 (765190) 345 kV Bus a. Apply Fault at the GEN-2020-090345.00 (765190) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-090 (765190) 345.0 kV to G20-090-XFM1 (765193) 34.5 kV Two Winding #1 b.2. GEN-2020-090 (765190) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0574 | Single Phase Fault with Stuck Breaker on G20-090-TAP 345.00 (765200) 345 kV Bus a. Apply Fault at the G20-090-TAP 345.00 (765200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-090-TAP (765200) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. G20-090-TAP (765200) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0575 | Single Phase Fault with Stuck Breaker on GEN-2021-029345.00 (765570) 345 kV Bus a. Apply Fault at the GEN-2021-029345.00 (765570) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-029 (765570) 345.0 kV to G21-029-XFM1 (765574) 34.5 kV Two Winding #1 b.2. GEN-2021-029 (765570) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0576 | Single Phase Fault with Stuck Breaker on G21-029-TAP 345.00 (765571) 345 kV Bus a. Apply Fault at the G21-029-TAP 345.00 (765571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. G21-029-TAP (765571) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0577 | Single Phase Fault with Stuck Breaker on GEN-2021-068345.00 (765910) 345 kV Bus a. Apply Fault at the GEN-2021-068345.00 (765910) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-068 (765910) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-068 (765910) 345.0 kV to G21-068-XFM1 (765914) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0578 | Single Phase Fault with Stuck Breaker on G21-068-TAP 345.00 (765911) 345 kV Bus a. Apply Fault at the G21-068-TAP 345.00 (765911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-068-TAP (765911) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. G21-068-TAP (765911) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0579 | Single Phase Fault with Stuck Breaker on GEN-2020-007345.00 (766260) 345 kV Bus a. Apply Fault at the GEN-2020-007345.00 (766260) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-007 (766260) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-007 (766260) 345.0 kV to G20-007-XFM1 (766264) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0580 | Single Phase Fault with Stuck Breaker on G22-007-TAP 115.00 (767120) 115 kV Bus a. Apply Fault at the G22-007-TAP 115.00 (767120) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-007-TAP (767120) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.2. G22-007-TAP (767120) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0581 | Single Phase Fault with Stuck Breaker on G22-013-TAP 345.00 (767240) 345 kV Bus a. Apply Fault at the G22-013-TAP 345.00 (767240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-013-TAP (767240) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G22-013-TAP (767240) 345.0 kV to GEN-2022-013 (767241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0582 | Single Phase Fault with Stuck Breaker on G22-015-TAP 345.00 (767280) 345 kV Bus a. Apply Fault at the G22-015-TAP 345.00 (767280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. G22-015-TAP (767280) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0583 | Single Phase Fault with Stuck Breaker on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply Fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-065-TAP (768280) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. G22-065-TAP (768280) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0584 | Single Phase Fault with Stuck Breaker on G22-075-TAP 345.00 (768480) 345 kV Bus a. Apply Fault at the G22-075-TAP 345.00 (768480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-075-TAP (768480) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G22-075-TAP (768480) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0585 | Single Phase Fault with Stuck Breaker on G22-100-TAP 161.00 (768980) 161 kV Bus a. Apply Fault at the G22-100-TAP 161.00 (768980) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-100-TAP (768980) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. G22-100-TAP (768980) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0586 | Single Phase Fault with Stuck Breaker on G22-214-TAP 138.00 (771260) 138 kV Bus a. Apply Fault at the G22-214-TAP 138.00 (771260) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-214-TAP (771260) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 b.2. G22-214-TAP (771260) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0587 | Single Phase Fault with Stuck Breaker on 5BOONE 161.00 (300061) 161 kV Bus a. Apply Fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BOONE (300493) 69.0 kV to 5BOONE (300061) 161.0 kV Two Winding #1 b.2. 2BOONE (300493) 69.0 kV to 2DEERPK (300497) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0588 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEORGE (300531) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 b.2. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0589 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 b.2. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0590 | Single Phase Fault with Stuck Breaker on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply Fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PLATCTY (300307) 69.0 kV to 5PLATCTY (301552) 161.0 kV Two Winding #1 b.2. 2PLATCTY (300307) 69.0 kV to 2HOOVER (300298) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0591 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.2. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0592 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 b.2. 5JASPER (300950) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0593 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0594 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0595 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0596 | Single Phase Fault with Stuck Breaker on COLBY 3 115.00 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0597 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0598 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0599 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0600 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0601 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LANG 7 (532769) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0602 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 7 (532770) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0603 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0604 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.2. NEOSHON4 (533022) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0605 | Single Phase Fault with Stuck Breaker on CANAL 4 138.00 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 138.00 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANAL 4 (533033) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #1 b.2. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0606 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASOE4 (533059) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #z1 b.2. ELPASOE4 (533059) 138.0 kV to 47TH ST4 (533058) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0607 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 b.2. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0608 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 b.2. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0609 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 b.2. CRESWLS2 (533573) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0610 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 2 (533646) 69.0 kV to COALCRK2 (533633) 69.0 kV Transmission Circuit #1 b.2. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0611 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.2. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0612 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0613 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0614 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0615 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0616 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0617 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0618 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0619 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0620 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0621 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0622 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0623 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 b.2. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0624 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0625 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0626 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 b.2. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0627 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO7 (640326) 115.0 kV to BEVERLY7 (640082) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0628 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD7 (640381) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0629 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0630 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT4 (532992) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0631 | Single Phase Fault with Stuck Breaker on SHERIDN2 69.000 (533841) 69 kV Bus a. Apply Fault at the SHERIDN2 69.000 (533841) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHERIDN2 (533841) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0632 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0633 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 b.2. SUB M (548815) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0634 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOK 7 (640269) 115.0 kV to CAMBRIG7 (640100) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0635 | Single Phase Fault with Stuck Breaker on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply Fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7THOMHL (300049) 345.0 kV to 5THOMHLXF4 (301510) 161.0 kV Two Winding #4 b.2. 7THOMHL (300049) 345.0 kV to 5THOMHLXF3 (301506) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0636 | Single Phase Fault with Stuck Breaker on VSC2_3 345.00 (992003) 345 kV Bus a. Apply Fault at the VSC2_3 345.00 (992003) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VSC2_3 (992003) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 b.2. VSC2_3 (992003) 345.0 kV to VSC2_6 (992006) 276.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0637 | Single Phase Fault with Stuck Breaker on 5MLRSBGB1 161.00 (300519) 161 kV Bus a. Apply Fault at the 5MLRSBGB1 161.00 (300519) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MLRSBGB1 (300519) 161.0 kV to 5MLRSBGB2 (301498) 161.0 kV Transmission Circuit #z1 b.2. 5MLRSBGB1 (300519) 161.0 kV to 5BOONE (300061) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0638 | Single Phase Fault with Stuck Breaker on 5NORTONTP 161.00 (301567) 161 kV Bus a. Apply Fault at the 5NORTONTP 161.00 (301567) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTONTP (301567) 161.0 kV to 5GEORGE (300082) 161.0 kV Transmission Circuit #1 b.2. 5NORTONTP (301567) 161.0 kV to 5NORTON (300105) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0639 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0640 | Single Phase Fault with Stuck Breaker on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply Fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to 5PITTSV (300110) 161.0 kV Transmission Circuit #1 b.2. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0641 | Single Phase Fault with Stuck Breaker on G20-072-TAP 161.00 (764355) 161 kV Bus a. Apply Fault at the G20-072-TAP 161.00 (764355) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-072-TAP (764355) 161.0 kV to 5SEDALA (300117) 161.0 kV Transmission Circuit #1 b.2. G20-072-TAP (764355) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0642 | Single Phase Fault with Stuck Breaker on 5MCBAINB2 161.00 (301489) 161 kV Bus a. Apply Fault at the 5MCBAINB2 161.00 (301489) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5MCBAINB2 (301489) 161.0 kV to 5MCBAINB1 (300501) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0643 | Single Phase Fault with Stuck Breaker on 2SYLVAN 69.000 (300545) 69 kV Bus a. Apply Fault at the 2SYLVAN 69.000 (300545) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SYLVAN (300545) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2SYLVAN (300545) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0644 | Single Phase Fault with Stuck Breaker on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply Fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2FORTNA (300554) 69.0 kV to 2CALIF (300550) 69.0 kV Transmission Circuit #1 b.2. 2FORTNA (300554) 69.0 kV to 2SYRACS (300564) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0645 | Single Phase Fault with Stuck Breaker on 2PRARIE 69.000 (300561) 69 kV Bus a. Apply Fault at the 2PRARIE 69.000 (300561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PRARIE (300561) 69.0 kV to 2CALIF (300550) 69.0 kV Transmission Circuit #1 b.2. 2PRARIE (300561) 69.0 kV to 2PILOTG (300560) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0646 | Single Phase Fault with Stuck Breaker on 2ST_MARTINS 69.000 (301442) 69 kV Bus a. Apply Fault at the 2ST_MARTINS 69.000 (301442) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ST_MARTINS (301442) 69.0 kV to 2CALIF (300550) 69.0 kV Transmission Circuit #1 b.2. 2ST_MARTINS (301442) 69.0 kV to 2SCRUGG (300637) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0647 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0648 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0649 | Single Phase Fault with Stuck Breaker on G18-128-TAP 345.00 (763421) 345 kV Bus a. Apply Fault at the G18-128-TAP 345.00 (763421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-128-TAP (763421) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. G18-128-TAP (763421) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0650 | Single Phase Fault with Stuck Breaker on GEN-2021-076345.00 (765990) 345 kV Bus a. Apply Fault at the GEN-2021-076345.00 (765990) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-076 (765990) 345.0 kV to G21-076-XFM1 (765994) 34.5 kV Two Winding #1 b.2. GEN-2021-076 (765990) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0651 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 7 (532773) 345.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0652 | Single Phase Fault with Stuck Breaker on CNTRLPL3 115.00 (531485) 115 kV Bus a. Apply Fault at the CNTRLPL3 115.00 (531485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRLPL3 (531485) 115.0 kV to LEOTI 3 (531428) 115.0 kV Transmission Circuit #1 b.2. CNTRLPL3 (531485) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0653 | Single Phase Fault with Stuck Breaker on G19-030-TAP 345.00 (763677) 345 kV Bus a. Apply Fault at the G19-030-TAP 345.00 (763677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-030-TAP (763677) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G19-030-TAP (763677) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0654 | Single Phase Fault with Stuck Breaker on GEN-2021-107345.00 (766240) 345 kV Bus a. Apply Fault at the GEN-2021-107345.00 (766240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-107 (766240) 345.0 kV to G21-107-XFM1 (766244) 34.5 kV Two Winding #1 b.2. GEN-2021-107 (766240) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0655 | Single Phase Fault with Stuck Breaker on G16-111-TAP 345.00 (587884) 345 kV Bus a. Apply Fault at the G16-111-TAP 345.00 (587884) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-111-TAP (587884) 345.0 kV to RENO 7 (532771) 345.0 kV Transmission Circuit #1 b.2. G16-111-TAP (587884) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0656 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0657 | Single Phase Fault with Stuck Breaker on GEN-2017-220345.00 (760284) 345 kV Bus a. Apply Fault at the GEN-2017-220345.00 (760284) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-220 (760284) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-220 (760284) 345.0 kV to G17-220-XFM1 (760285) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0658 | Single Phase Fault with Stuck Breaker on G21-096-TAP 345.00 (766141) 345 kV Bus a. Apply Fault at the G21-096-TAP 345.00 (766141) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-096-TAP (766141) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. G21-096-TAP (766141) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0659 | Single Phase Fault with Stuck Breaker on GEN-2018-032345.00 (762680) 345 kV Bus a. Apply Fault at the GEN-2018-032345.00 (762680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-032 (762680) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-032 (762680) 345.0 kV to G18-032XFM1 (762681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0660 | Single Phase Fault with Stuck Breaker on GEN-2021-006345.00 (765350) 345 kV Bus a. Apply Fault at the GEN-2021-006345.00 (765350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-006 (765350) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-006 (765350) 345.0 kV to G21-006-XFM2 (765357) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0661 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583859) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583859) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583859) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583859) 345.0 kV to GEN-2014-001 (583850) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0662 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. UNIONRG6 (532874) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0663 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0664 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. G19-054-TAP (763862) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0665 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 b.2. NEOSHOS2 (533778) 69.0 kV to BAKER 2 (532926) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0666 | Single Phase Fault with Stuck Breaker on G17-005-TAP 161.00 (588504) 161 kV Bus a. Apply Fault at the G17-005-TAP 161.00 (588504) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-005-TAP (588504) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. G17-005-TAP (588504) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0667 | Single Phase Fault with Stuck Breaker on G20-079-TAP 161.00 (764310) 161 kV Bus a. Apply Fault at the G20-079-TAP 161.00 (764310) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-079-TAP (764310) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. G20-079-TAP (764310) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0668 | Single Phase Fault with Stuck Breaker on GEN-2022-006161.00 (767101) 161 kV Bus a. Apply Fault at the GEN-2022-006161.00 (767101) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-006 (767101) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. GEN-2022-006 (767101) 161.0 kV to G22-006XFMR1 (767102) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0669 | Single Phase Fault with Stuck Breaker on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply Fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SC10BEL4 (533063) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. SC10BEL4 (533063) 138.0 kV to FARBER 4 (533042) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0670 | Single Phase Fault with Stuck Breaker on GEN-2017-121138.00 (761838) 138 kV Bus a. Apply Fault at the GEN-2017-121138.00 (761838) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-121 (761838) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. GEN-2017-121 (761838) 138.0 kV to G17-121XFM2 (761842) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0671 | Single Phase Fault with Stuck Breaker on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply Fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TAYLOR 4 (533006) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. TAYLOR 4 (533006) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0672 | Single Phase Fault with Stuck Breaker on SG12COL4 138.00 (533065) 138 kV Bus a. Apply Fault at the SG12COL4 138.00 (533065) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SG12COL4 (533065) 138.0 kV to EVANS N4 (533040) 138.0 kV Transmission Circuit #1 b.2. SG12COL4 (533065) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0673 | Single Phase Fault with Stuck Breaker on WACO N 4 138.00 (533073) 138 kV Bus a. Apply Fault at the WACO N 4 138.00 (533073) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WACO N 4 (533073) 138.0 kV to CENTENN4 (533034) 138.0 kV Transmission Circuit #1 b.2. WACO N 4 (533073) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0674 | Single Phase Fault with Stuck Breaker on MAIZE 4 138.00 (533054) 138 kV Bus a. Apply Fault at the MAIZE 4 138.00 (533054) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAIZE 4 (533054) 138.0 kV to EVANS N4 (533040) 138.0 kV Transmission Circuit #1 b.2. MAIZE 4 (533054) 138.0 kV to CHISHLM4 (533035) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0675 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 45TH ST4 (533074) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #1 b.2. 45TH ST4 (533074) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0676 | Single Phase Fault with Stuck Breaker on STEARMN4 138.00 (533068) 138 kV Bus a. Apply Fault at the STEARMN4 138.00 (533068) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEARMN4 (533068) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. STEARMN4 (533068) 138.0 kV to BOEINGE4 (533030) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0677 | Single Phase Fault with Stuck Breaker on GEN-2017-226138.00 (760641) 138 kV Bus a. Apply Fault at the GEN-2017-226138.00 (760641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-226 (760641) 138.0 kV to G17-226XFMR1 (760642) 34.5 kV Two Winding #1 b.2. GEN-2017-226 (760641) 138.0 kV to G17-227XFMR1 (760662) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0678 | Single Phase Fault with Stuck Breaker on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply Fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKERDG4 (533053) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #1 b.2. LAKERDG4 (533053) 138.0 kV to HOOVERN4 (533049) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0679 | Single Phase Fault with Stuck Breaker on INTERST4 138.00 (533051) 138 kV Bus a. Apply Fault at the INTERST4 138.00 (533051) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTERST4 (533051) 138.0 kV to GILL E 4 (533044) 138.0 kV Transmission Circuit #1 b.2. INTERST4 (533051) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0680 | Single Phase Fault with Stuck Breaker on GEN-2022-004138.00 (767061) 138 kV Bus a. Apply Fault at the GEN-2022-004138.00 (767061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-004 (767061) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #1 b.2. GEN-2022-004 (767061) 138.0 kV to G22-004XFMR1 (767062) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0681 | Single Phase Fault with Stuck Breaker on 64TH 4 138.00 (533066) 138 kV Bus a. Apply Fault at the 64TH 4 138.00 (533066) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 64TH 4 (533066) 138.0 kV to 47TH ST4 (533058) 138.0 kV Transmission Circuit #1 b.2. 64TH 4 (533066) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0682 | Single Phase Fault with Stuck Breaker on SCRANTN3 115.00 (533173) 115 kV Bus a. Apply Fault at the SCRANTN3 115.00 (533173) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCRANTN3 (533173) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 b.2. SCRANTN3 (533173) 115.0 kV to 4CORNER3 (533158) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0683 | Single Phase Fault with Stuck Breaker on FLORENC3 115.00 (533366) 115 kV Bus a. Apply Fault at the FLORENC3 115.00 (533366) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLORENC3 (533366) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0684 | Single Phase Fault with Stuck Breaker on GREEN 2 69.000 (533636) 69 kV Bus a. Apply Fault at the GREEN 2 69.000 (533636) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREEN 2 (533636) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.2. GREEN 2 (533636) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0685 | Single Phase Fault with Stuck Breaker on MCKEE 2 69.000 (533640) 69 kV Bus a. Apply Fault at the MCKEE 2 69.000 (533640) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCKEE 2 (533640) 69.0 kV to MARMATN2 (533639) 69.0 kV Transmission Circuit #1 b.2. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0686 | Single Phase Fault with Stuck Breaker on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply Fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ZILAJCT2 (533654) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.2. ZILAJCT2 (533654) 69.0 kV to ALLEN 2 (533621) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0687 | Single Phase Fault with Stuck Breaker on PARSONS2 69.000 (533704) 69 kV Bus a. Apply Fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARSONS2 (533704) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 b.2. PARSONS2 (533704) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0688 | Single Phase Fault with Stuck Breaker on PECK 2 69.000 (533830) 69 kV Bus a. Apply Fault at the PECK 2 69.000 (533830) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECK 2 (533830) 69.0 kV to HAYSVJS2 (533802) 69.0 kV Transmission Circuit #1 b.2. PECK 2 (533830) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0689 | Single Phase Fault with Stuck Breaker on CANALN 2 69.000 (533790) 69 kV Bus a. Apply Fault at the CANALN 2 69.000 (533790) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALN 2 (533790) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #z1 b.2. CANALN 2 (533790) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0690 | Single Phase Fault with Stuck Breaker on RUTAN 2 69.000 (533838) 69 kV Bus a. Apply Fault at the RUTAN 2 69.000 (533838) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUTAN 2 (533838) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #1 b.2. RUTAN 2 (533838) 69.0 kV to GLENDAL2 (533797) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0691 | Single Phase Fault with Stuck Breaker on WESTLNK2 69.000 (533854) 69 kV Bus a. Apply Fault at the WESTLNK2 69.000 (533854) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTLNK2 (533854) 69.0 kV to COWSKIN2 (533788) 69.0 kV Transmission Circuit #1 b.2. WESTLNK2 (533854) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0692 | Single Phase Fault with Stuck Breaker on GODDTAP2 69.000 (533879) 69 kV Bus a. Apply Fault at the GODDTAP2 69.000 (533879) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GODDTAP2 (533879) 69.0 kV to COWSKIN2 (533788) 69.0 kV Transmission Circuit #1 b.2. GODDTAP2 (533879) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0693 | Single Phase Fault with Stuck Breaker on VULCTP 2 69.000 (533851) 69 kV Bus a. Apply Fault at the VULCTP 2 69.000 (533851) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VULCTP 2 (533851) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #1 b.2. VULCTP 2 (533851) 69.0 kV to LIN 2 (533812) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0694 | Single Phase Fault with Stuck Breaker on OATVILL2 69.000 (533825) 69 kV Bus a. Apply Fault at the OATVILL2 69.000 (533825) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OATVILL2 (533825) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. OATVILL2 (533825) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0695 | Single Phase Fault with Stuck Breaker on MIDLAND2 69.000 (533816) 69 kV Bus a. Apply Fault at the MIDLAND2 69.000 (533816) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDLAND2 (533816) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 b.2. MIDLAND2 (533816) 69.0 kV to HYDRJS2 (533810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0696 | Single Phase Fault with Stuck Breaker on VISTAPK2 69.000 (533849) 69 kV Bus a. Apply Fault at the VISTAPK2 69.000 (533849) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VISTAPK2 (533849) 69.0 kV to HOOVERN2 (533805) 69.0 kV Transmission Circuit #1 b.2. VISTAPK2 (533849) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0697 | Single Phase Fault with Stuck Breaker on WATER1 2 69.000 (533855) 69 kV Bus a. Apply Fault at the WATER1 2 69.000 (533855) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATER1 2 (533855) 69.0 kV to HOOVERN2 (533805) 69.0 kV Transmission Circuit #1 b.2. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0698 | Single Phase Fault with Stuck Breaker on TYLER 2 69.000 (533847) 69 kV Bus a. Apply Fault at the TYLER 2 69.000 (533847) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. TYLER 2 (533847) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0699 | Single Phase Fault with Stuck Breaker on WATER2 2 69.000 (533856) 69 kV Bus a. Apply Fault at the WATER2 2 69.000 (533856) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATER2 2 (533856) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 b.2. WATER2 2 (533856) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0700 | Single Phase Fault with Stuck Breaker on SG8CRAG2 69.000 (533873) 69 kV Bus a. Apply Fault at the SG8CRAG2 69.000 (533873) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SG8CRAG2 (533873) 69.0 kV to LIN 2 (533812) 69.0 kV Transmission Circuit #1 b.2. SG8CRAG2 (533873) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0701 | Single Phase Fault with Stuck Breaker on SENECA 2 69.000 (533839) 69 kV Bus a. Apply Fault at the SENECA 2 69.000 (533839) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SENECA 2 (533839) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.2. SENECA 2 (533839) 69.0 kV to OSAGE 2 (533827) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0702 | Single Phase Fault with Stuck Breaker on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply Fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROLLHLS3 (539643) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0703 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUSSELL3 (539701) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. RUSSELL3 (539701) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0704 | Single Phase Fault with Stuck Breaker on 2ND-KS 3 115.00 (539689) 115 kV Bus a. Apply Fault at the 2ND-KS 3 115.00 (539689) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ND-KS 3 (539689) 115.0 kV to 24-FREY3 (539661) 115.0 kV Transmission Circuit #1 b.2. 2ND-KS 3 (539689) 115.0 kV to GBENDTP3 (539666) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0705 | Single Phase Fault with Stuck Breaker on SSTARTP3 115.00 (539763) 115 kV Bus a. Apply Fault at the SSTARTP3 115.00 (539763) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SSTARTP3 (539763) 115.0 kV to GRNBURG3 (539664) 115.0 kV Transmission Circuit #1 b.2. SSTARTP3 (539763) 115.0 kV to FORD 3 (539758) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0706 | Single Phase Fault with Stuck Breaker on GEN-2019-044115.00 (763758) 115 kV Bus a. Apply Fault at the GEN-2019-044115.00 (763758) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-044 (763758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.2. GEN-2019-044 (763758) 115.0 kV to G19-044-XFM1 (763759) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0707 | Single Phase Fault with Stuck Breaker on GEN-2011-008345.00 (539840) 345 kV Bus a. Apply Fault at the GEN-2011-008345.00 (539840) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2011-008 (539840) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. GEN-2011-008 (539840) 345.0 kV to G-2011-008-3 (539857) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0708 | Single Phase Fault with Stuck Breaker on GEN-2019-058345.00 (763890) 345 kV Bus a. Apply Fault at the GEN-2019-058345.00 (763890) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-058 (763890) 345.0 kV to G19-058-XFM1 (763891) 34.5 kV Two Winding #1 b.2. GEN-2019-058 (763890) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0709 | Single Phase Fault with Stuck Breaker on GEN-2008-124345.00 (579480) 345 kV Bus a. Apply Fault at the GEN-2008-124345.00 (579480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2008-124 (579480) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. GEN-2008-124 (579480) 345.0 kV to G08-124XFMR1 (579481) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0710 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0711 | Single Phase Fault with Stuck Breaker on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply Fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCONGRS5 (541318) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 b.2. NCONGRS5 (541318) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0712 | Single Phase Fault with Stuck Breaker on WESTON 5 161.00 (541351) 161 kV Bus a. Apply Fault at the WESTON 5 161.00 (541351) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTON 5 (541351) 161.0 kV to IATAN5 (541350) 161.0 kV Transmission Circuit #1 b.2. WESTON 5 (541351) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0713 | Single Phase Fault with Stuck Breaker on OAKGRV 5 161.00 (541227) 161 kV Bus a. Apply Fault at the OAKGRV 5 161.00 (541227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKGRV 5 (541227) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 b.2. OAKGRV 5 (541227) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0714 | Single Phase Fault with Stuck Breaker on TIFFANY5 161.00 (543026) 161 kV Bus a. Apply Fault at the TIFFANY5 161.00 (543026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIFFANY5 (543026) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. TIFFANY5 (543026) 161.0 kV to WETHRBY5 (543017) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0715 | Single Phase Fault with Stuck Breaker on FRSTCRK5 161.00 (543039) 161 kV Bus a. Apply Fault at the FRSTCRK5 161.00 (543039) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRSTCRK5 (543039) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. FRSTCRK5 (543039) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0716 | Single Phase Fault with Stuck Breaker on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply Fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0717 | Single Phase Fault with Stuck Breaker on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply Fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LKWOOD 5 (541238) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 b.2. LKWOOD 5 (541238) 161.0 kV to RAYTOWN5 (541219) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0718 | Single Phase Fault with Stuck Breaker on NUCOR5 161.00 (541395) 161 kV Bus a. Apply Fault at the NUCOR5 161.00 (541395) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUCOR5 (541395) 161.0 kV to NUCOR_D1 (541396) 13.8 kV Two Winding #1 b.2. NUCOR5 (541395) 161.0 kV to NUCOR_S1 (541398) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0719 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0720 | Single Phase Fault with Stuck Breaker on WARSAWTP 69.000 (541281) 69 kV Bus a. Apply Fault at the WARSAWTP 69.000 (541281) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARSAWTP (541281) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 b.2. WARSAWTP (541281) 69.0 kV to WARSAW 2 (541277) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0721 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0722 | Single Phase Fault with Stuck Breaker on GEN-2017-195345.00 (762279) 345 kV Bus a. Apply Fault at the GEN-2017-195345.00 (762279) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-195 (762279) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-195 (762279) 345.0 kV to G17-195XFM1 (762280) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0723 | Single Phase Fault with Stuck Breaker on HICKMAN5 161.00 (542994) 161 kV Bus a. Apply Fault at the HICKMAN5 161.00 (542994) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HICKMAN5 (542994) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. HICKMAN5 (542994) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0724 | Single Phase Fault with Stuck Breaker on ANTIOCH5 161.00 (543050) 161 kV Bus a. Apply Fault at the ANTIOCH5 161.00 (543050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. ANTIOCH5 (543050) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0725 | Single Phase Fault with Stuck Breaker on REDEL 5 161.00 (543053) 161 kV Bus a. Apply Fault at the REDEL 5 161.00 (543053) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDEL 5 (543053) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. REDEL 5 (543053) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0726 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0727 | Single Phase Fault with Stuck Breaker on G17-108-TAP 161.00 (761278) 161 kV Bus a. Apply Fault at the G17-108-TAP 161.00 (761278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-108-TAP (761278) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. G17-108-TAP (761278) 161.0 kV to GEN-2021-050 (765750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0728 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #z2 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0729 | Single Phase Fault with Stuck Breaker on G20-007-TAP 345.00 (766261) 345 kV Bus a. Apply Fault at the G20-007-TAP 345.00 (766261) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0730 | Single Phase Fault with Stuck Breaker on TERRACE5 161.00 (542991) 161 kV Bus a. Apply Fault at the TERRACE5 161.00 (542991) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0731 | Single Phase Fault with Stuck Breaker on FOREST 5 161.00 (543001) 161 kV Bus a. Apply Fault at the FOREST 5 161.00 (543001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOREST 5 (543001) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. FOREST 5 (543001) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0732 | Single Phase Fault with Stuck Breaker on ROEPARK5 161.00 (543040) 161 kV Bus a. Apply Fault at the ROEPARK5 161.00 (543040) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROEPARK5 (543040) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 b.2. ROEPARK5 (543040) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0733 | Single Phase Fault with Stuck Breaker on WINJT N5 161.00 (543009) 161 kV Bus a. Apply Fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT N5 (543009) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT N5 (543009) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0734 | Single Phase Fault with Stuck Breaker on WINJT S5 161.00 (543010) 161 kV Bus a. Apply Fault at the WINJT S5 161.00 (543010) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT S5 (543010) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT S5 (543010) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0735 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NKANCTY5 (543018) 161.0 kV to AVONDAL5 (543015) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0736 | Single Phase Fault with Stuck Breaker on LINECRK5 161.00 (543025) 161 kV Bus a. Apply Fault at the LINECRK5 161.00 (543025) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LINECRK5 (543025) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 b.2. LINECRK5 (543025) 161.0 kV to RIVRSID5 (543021) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0737 | Single Phase Fault with Stuck Breaker on GEN-2022-073161.00 (768441) 161 kV Bus a. Apply Fault at the GEN-2022-073161.00 (768441) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-073 (768441) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. GEN-2022-073 (768441) 161.0 kV to G22-073XFMR1 (768442) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0738 | Single Phase Fault with Stuck Breaker on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply Fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTY 2 (543092) 69.0 kV to LAKCTYJ2 (543087) 69.0 kV Transmission Circuit #1 b.2. LAKCTY 2 (543092) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0739 | Single Phase Fault with Stuck Breaker on LAKCTYK2 69.000 (543093) 69 kV Bus a. Apply Fault at the LAKCTYK2 69.000 (543093) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYK2 (543093) 69.0 kV to DUNCNRD2 (543091) 69.0 kV Transmission Circuit #1 b.2. LAKCTYK2 (543093) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0740 | Single Phase Fault with Stuck Breaker on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply Fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 b.2. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0741 | Single Phase Fault with Stuck Breaker on GAT258 2 69.000 (547551) 69 kV Bus a. Apply Fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GAT258 2 (547551) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 b.2. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0742 | Single Phase Fault with Stuck Breaker on JOP430 2 69.000 (547608) 69 kV Bus a. Apply Fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP430 2 (547608) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 b.2. JOP430 2 (547608) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0743 | Single Phase Fault with Stuck Breaker on GAL278T 69.000 (547728) 69 kV Bus a. Apply Fault at the GAL278T 69.000 (547728) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GAL278T (547728) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 b.2. GAL278T (547728) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0744 | Single Phase Fault with Stuck Breaker on RIV406 2 69.000 (547602) 69 kV Bus a. Apply Fault at the RIV406 2 69.000 (547602) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV406 2 (547602) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. RIV406 2 (547602) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0745 | Single Phase Fault with Stuck Breaker on SUB P 69.000 (548827) 69 kV Bus a. Apply Fault at the SUB P 69.000 (548827) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB P (548827) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB P (548827) 69.0 kV to SUB I (548800) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0746 | Single Phase Fault with Stuck Breaker on SUB R 69.000 (548830) 69 kV Bus a. Apply Fault at the SUB R 69.000 (548830) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB R (548830) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SUB R (548830) 69.0 kV to SUB K (548801) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0747 | Single Phase Fault with Stuck Breaker on GEN-2018-031161.00 (762669) 161 kV Bus a. Apply Fault at the GEN-2018-031161.00 (762669) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-031 (762669) 161.0 kV to G18-031XFM1 (762670) 34.5 kV Two Winding #1 b.2. GEN-2018-031 (762669) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0748 | Single Phase Fault with Stuck Breaker on G15052_1 345.00 (562900) 345 kV Bus a. Apply Fault at the G15052_1 345.00 (562900) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15052_1 (562900) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. G15052_1 (562900) 345.0 kV to G15052_2 (562901) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0749 | Single Phase Fault with Stuck Breaker on GEN-2016-046345.00 (587310) 345 kV Bus a. Apply Fault at the GEN-2016-046345.00 (587310) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-046 (587310) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-046 (587310) 345.0 kV to G16-046XFMR1 (587311) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0750 | Single Phase Fault with Stuck Breaker on GEN-2016-050345.00 (587350) 345 kV Bus a. Apply Fault at the GEN-2016-050345.00 (587350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-050 (587350) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-050 (587350) 345.0 kV to G16-050XFMR1 (587351) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0751 | Single Phase Fault with Stuck Breaker on GEN-2017-086345.00 (589240) 345 kV Bus a. Apply Fault at the GEN-2017-086345.00 (589240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-086 (589240) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-086 (589240) 345.0 kV to G17-086XFMR1 (589241) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0752 | Single Phase Fault with Stuck Breaker on GEN-2020-011345.00 (764420) 345 kV Bus a. Apply Fault at the GEN-2020-011345.00 (764420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-011 (764420) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-011 (764420) 345.0 kV to G20-011-SS3 (764433) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0753 | Single Phase Fault with Stuck Breaker on G18-125-TAP 345.00 (763410) 345 kV Bus a. Apply Fault at the G18-125-TAP 345.00 (763410) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0754 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0755 | Single Phase Fault with Stuck Breaker on GEN-2022-054345.00 (768061) 345 kV Bus a. Apply Fault at the GEN-2022-054345.00 (768061) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-054 (768061) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-054 (768061) 345.0 kV to G22-054XFMR1 (768062) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0756 | Single Phase Fault with Stuck Breaker on GEN-2021-030345.00 (765580) 345 kV Bus a. Apply Fault at the GEN-2021-030345.00 (765580) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-030 (765580) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-030 (765580) 345.0 kV to G21-030-XFM1 (765584) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0757 | Single Phase Fault with Stuck Breaker on GEN-2021-069345.00 (765920) 345 kV Bus a. Apply Fault at the GEN-2021-069345.00 (765920) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-069 (765920) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-069 (765920) 345.0 kV to G21-069-XFM1 (765924) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0758 | Single Phase Fault with Stuck Breaker on GEN-2021-070345.00 (765930) 345 kV Bus a. Apply Fault at the GEN-2021-070345.00 (765930) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-070 (765930) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-070 (765930) 345.0 kV to G21-070-XFM1 (765934) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0759 | Single Phase Fault with Stuck Breaker on GEN-2022-007115.00 (767121) 115 kV Bus a. Apply Fault at the GEN-2022-007115.00 (767121) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-007 (767121) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 b.2. GEN-2022-007 (767121) 115.0 kV to G22-007XFMR1 (767122) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0760 | Single Phase Fault with Stuck Breaker on GEN-2022-013345.00 (767241) 345 kV Bus a. Apply Fault at the GEN-2022-013345.00 (767241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-013 (767241) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-013 (767241) 345.0 kV to G22-013XFMR1 (767242) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0761 | Single Phase Fault with Stuck Breaker on GEN-2022-015345.00 (767281) 345 kV Bus a. Apply Fault at the GEN-2022-015345.00 (767281) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-015 (767281) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-015 (767281) 345.0 kV to G22-015XFMR1 (767282) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0762 | Single Phase Fault with Stuck Breaker on GEN-2022-065230.00 (768281) 230 kV Bus a. Apply Fault at the GEN-2022-065230.00 (768281) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-065 (768281) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. GEN-2022-065 (768281) 230.0 kV to G22-065XFMR1 (768282) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0763 | Single Phase Fault with Stuck Breaker on GEN-2022-075345.00 (768481) 345 kV Bus a. Apply Fault at the GEN-2022-075345.00 (768481) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-075 (768481) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-075 (768481) 345.0 kV to G22-075XFMR1 (768482) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0764 | Single Phase Fault with Stuck Breaker on GEN-2022-214138.00 (771261) 138 kV Bus a. Apply Fault at the GEN-2022-214138.00 (771261) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-214 (771261) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 b.2. GEN-2022-214 (771261) 138.0 kV to G22-214XFMR1 (771262) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0765 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0766 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0767 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.2. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0768 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0769 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 7 (531465) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0770 | Single Phase Fault with Stuck Breaker on JEC 6 230.00 (532852) 230 kV Bus a. Apply Fault at the JEC 6 230.00 (532852) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0771 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to RENO 7 (532771) 345.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 b.2. RENO 3 (533416) 115.0 kV to RENO 7 (532771) 345.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0772 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR3 (533268) 115.0 kV to STRANGR7 (532772) 345.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR3 (533268) 115.0 kV to STRANGR7 (532772) 345.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0773 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0774 | Single Phase Fault with Stuck Breaker on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0775 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK3 (533315) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #2 b.2. OTTRCRK3 (533315) 115.0 kV to OTTRCRK4 (532997) 138.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0776 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASO 2 (533793) 69.0 kV to ELPASOE4 (533059) 138.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 b.2. ELPASO 2 (533793) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0777 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0778 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0779 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to PHILL 7 (541200) 345.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0780 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 5 (541202) 161.0 kV to SIBLEY 7 (541201) 345.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0781 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0782 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0783 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. WGARDNR5 (542966) 161.0 kV to W.GRDNR7 (542965) 345.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0784 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTH 7 (542972) 345.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTHN5 (543665) 161.0 kV to HAWTH 7 (542972) 345.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0785 | Single Phase Fault with Stuck Breaker on LAC3_STAR7 345.00 (543667) 345 kV Bus a. Apply Fault at the LAC3_STAR7 345.00 (543667) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC3_STAR7 (543667) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h b.2. LAC3_STAR7 (543667) 345.0 kV to LAC3_Y1 (543662) 6.9 kV Two Winding #y | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0786 | Single Phase Fault with Stuck Breaker on LAC8_STAR7 345.00 (543669) 345 kV Bus a. Apply Fault at the LAC8_STAR7 345.00 (543669) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC8_STAR7 (543669) 345.0 kV to LAC8_Z1 (543672) 4.0 kV Two Winding #z b.2. LAC8_STAR7 (543669) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0787 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 2 (547534) 69.0 kV to ORO110 5 (547467) 161.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 b.2. ORO110 2 (547534) 69.0 kV to WEB436 2 (547527) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0788 | Single Phase Fault with Stuck Breaker on JOP389 2 69.000 (547592) 69 kV Bus a. Apply Fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 b.2. JOP389 2 (547592) 69.0 kV to EXP449T2 (547438) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0789 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 4 (547486) 138.0 kV to VINTAJC4 (510417) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0790 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 2 (547601) 69.0 kV to HOC404 5 (547487) 161.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 b.2. HOC404 2 (547601) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0791 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.2. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0792 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 b.2. KEYSTON3 (640252) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0793 | Single Phase Fault with Stuck Breaker on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply Fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STOCKVL7 (640365) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. STOCKVL7 (640365) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0794 | Single Phase Fault with Stuck Breaker on GILL E 2 (533795) 69 kV Bus a. Apply Fault at the GILL E 2 (533795) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0795 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0796 | Single Phase Fault with Stuck Breaker on GILL W 2 (533796) 69 kV Bus a. Apply Fault at the GILL W 2 (533796) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL W 2 (533796) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0797 | Single Phase Fault with Stuck Breaker on HOOVERS2 (533806) 69 kV Bus a. Apply Fault at the HOOVERS2 (533806) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HOOVERS2 (533806) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0798 | Single Phase Fault with Stuck Breaker on GILL E 4 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 (533044) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0799 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0800 | Single Phase Fault with Stuck Breaker on HOOVERN4 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 (533049) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0801 | Single Phase Fault with Stuck Breaker on ALTOO E2 (533673) 69 kV Bus a. Apply Fault at the ALTOO E2 (533673) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. ALTOO E2 (533673) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0802 | Single Phase Fault with Stuck Breaker on NEOSHON2 (533768) 69 kV Bus a. Apply Fault at the NEOSHON2 (533768) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHON2 (533768) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0803 | Single Phase Fault with Stuck Breaker on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0804 | Single Phase Fault with Stuck Breaker on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0805 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0806 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0807 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0808 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0809 | Single Phase Fault with Stuck Breaker on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0810 | Single Phase Fault with Stuck Breaker on OSAGE J3 (533171) 115 kV Bus a. Apply Fault at the OSAGE J3 (533171) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. OSAGE J3 (533171) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0811 | Single Phase Fault with Stuck Breaker on WEMPORI3 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 (533309) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0812 | Single Phase Fault with Stuck Breaker on MORRIS 7 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 (532770) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MORRIS 7 (532770) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0813 | Single Phase Fault with Stuck Breaker on STILWEL5 (542969) 161 kV Bus a. Apply Fault at the STILWEL5 (542969) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0814 | Single Phase Fault with Stuck Breaker on REDWILO7 (640326) 115 kV Bus a. Apply Fault at the REDWILO7 (640326) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0815 | Single Phase Fault with Stuck Breaker on GENTLMN4 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 (640184) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0816 | Single Phase Fault with Stuck Breaker on SETAB 3 (531464) 115 kV Bus a. Apply Fault at the SETAB 3 (531464) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SETAB 3 (531464) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0817 | Single Phase Fault with Stuck Breaker on MINGO 3 (531429) 115 kV Bus a. Apply Fault at the MINGO 3 (531429) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0818 | Single Phase Fault with Stuck Breaker on SPEARVL3 (539694) 115 kV Bus a. Apply Fault at the SPEARVL3 (539694) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SPEARVL3 (539694) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0819 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0820 | Single Phase Fault with Stuck Breaker on NFTDODG3 (539771) 115 kV Bus a. Apply Fault at the NFTDODG3 (539771) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NFTDODG3 (539771) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0821 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0822 | Single Phase Fault with Stuck Breaker on NASHUA 5 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 (541203) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0823 | Single Phase Fault with Stuck Breaker on PLTCTY 5 (541221) 161 kV Bus a. Apply Fault at the PLTCTY 5 (541221) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. PLTCTY 5 (541221) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0824 | Single Phase Fault with Stuck Breaker on GLADSTN5 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 (543016) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0825 | Single Phase Fault with Stuck Breaker on TWA 5 (541214) 161 kV Bus a. Apply Fault at the TWA 5 (541214) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0826 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0827 | Single Phase Fault with Stuck Breaker on SEDN 2 (541271) 69 kV Bus a. Apply Fault at the SEDN 2 (541271) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SEDN 2 (541271) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0828 | Single Phase Fault with Stuck Breaker on SEDPLT 2 (541275) 69 kV Bus a. Apply Fault at the SEDPLT 2 (541275) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SEDPLT 2 (541275) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0829 | Single Phase Fault with Stuck Breaker on 5GEORGE (300082) 161 kV Bus a. Apply Fault at the 5GEORGE (300082) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0830 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 (344234) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. 5CALIF UE 2 (344234) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0831 | Single Phase Fault with Stuck Breaker on 5MCBAIN T (345071) 161 kV Bus a. Apply Fault at the 5MCBAIN T (345071) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. 5MCBAIN T (345071) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0832 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0833 | Single Phase Fault with Stuck Breaker on FRSTCRK5 (543039) 161 kV Bus a. Apply Fault at the FRSTCRK5 (543039) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. FRSTCRK5 (543039) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0834 | Single Phase Fault with Stuck Breaker on SMTHVL 5 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 (541204) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0835 | Single Phase Fault with Stuck Breaker on BLSPE 5 (541205) 161 kV Bus a. Apply Fault at the BLSPE 5 (541205) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BLSPE 5 (541205) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0836 | Single Phase Fault with Stuck Breaker on NEASTS5 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 (542985) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0837 | Single Phase Fault with Stuck Breaker on GRAND W5 (542988) 161 kV Bus a. Apply Fault at the GRAND W5 (542988) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GRAND W5 (542988) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0838 | Single Phase Fault with Stuck Breaker on NAVY 5 (542989) 161 kV Bus a. Apply Fault at the NAVY 5 (542989) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NAVY 5 (542989) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0839 | Single Phase Fault with Stuck Breaker on AVONDAL5 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 (543015) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0840 | Single Phase Fault with Stuck Breaker on SUB J (548811) 69 kV Bus a. Apply Fault at the SUB J (548811) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SUB J (548811) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0841 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0842 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0843 | Single Phase Fault with Stuck Breaker on LANG 3 (533304) 115 kV Bus a. Apply Fault at the LANG 3 (533304) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. LANG 3 (533304) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0844 | Single Phase Fault with Stuck Breaker on EVANS N4 (533040) 138 kV Bus a. Apply Fault at the EVANS N4 (533040) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0845 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0846 | Single Phase Fault with Stuck Breaker on MILAN_GOAB (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB (539008) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0847 | Single Phase Fault with Stuck Breaker on SUMNER 4 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 (532984) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0848 | Single Phase Fault with Stuck Breaker on GILL W 4 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 (533045) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL W 4 (533045) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT_0849 | Single Phase Fault with Stuck Breaker on GILL S 4 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 (533046) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL S 4 (533046) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0012 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0013 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0015 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0016 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0017 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0018 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0019 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0020 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0021 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0022 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0023 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0024 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0025 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0026 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0027 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0028 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0029 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0030 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0031 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0032 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0033 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0034 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0035 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0036 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0037 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0038 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0039 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0040 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0041 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0042 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0043 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0044 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0045 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0046 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT_0047 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0001 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0002 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0003 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0004 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA17-1 (512688) 22.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0005 | Single Phase Fault with Stuck Breaker on GREC TAP7 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 (512865) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRECSTG_1 (512615) 21.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0006 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0007 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0008 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_GRDA_FAULT_0009 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_OKGE_FAULT_0001 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.3. KAYWNDG1 (515651) 0.7 kV to Generator #1 b.4. KAYWNDG2 (515652) 0.7 kV to Generator #1 b.5. KAYWND11 (515622) 34.5 kV to Load #S1 b.6. KAYWND12 (515623) 34.5 kV to Load #S1 b.7. KAYWIND7 (514825) 345.0 kV to remove bus # b.8. KAYWNDT1 (515619) 12.5 kV to remove bus # b.9. KAYWNDT2 (515620) 12.5 kV to remove bus # b.10. OPENSKY7 (515621) 345.0 kV to remove bus # b.11. KAYWND11 (515622) 34.5 kV to remove bus # b.12. KAYWND12 (515623) 34.5 kV to remove bus # b.13. KAYWNDG1 (515651) 0.7 kV to remove bus # b.14. KAYWNDG2 (515652) 0.7 kV to remove bus # b.15. KAYWNDC1 (515653) 34.5 kV to remove bus # b.16. KAYWNDC2 (515654) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_SPS_FAULT_0001 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DUNES23 (523061) 0.7 kV to Generator #1 b.12. BUFF_DUNES13 (523062) 0.7 kV to Generator #1 b.13. BUFF_DUNES23 (523061) 0.7 kV to remove bus # b.14. BUFF_DUNES13 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNES22 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNES12 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_KACY_FAULT_0001 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_KACY_FAULT_0002 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.3. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 b.4. SHAWNEE5 (543041) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.5. SHAWNEE5 (543041) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_KACY_FAULT_0003 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EDE_FAULT_0001 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.3. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. JOP389 5 (547483) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.7. TIP292 5 (547472) 161.0 kV to Load #1 b.8. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EDE_FAULT_0002 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 7 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Breaker at To Bus #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EDE_FAULT_0003 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 b.3. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EDE_FAULT_0004 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.3. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.6. TIP292 5 (547472) 161.0 kV to Load #1 b.7. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_NPPD_FAULT_0001 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_NPPD_FAULT_0002 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_NPPD_FAULT_0003 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.4. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_NPPD_FAULT_0004 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_SUNC_FAULT_0001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_INDN_FAULT_0001 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_INDN_FAULT_0002 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_INDN_FAULT_0003 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_INDN_FAULT_0004 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_INDN_FAULT_0005 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_INDN_FAULT_0006 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_INDN_FAULT_0007 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_INDN_FAULT_0008 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_INDN_FAULT_0009 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_INDN_FAULT_0010 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0001 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.4. CLBYT1 1 (530645) 13.8 kV to remove bus # b.5. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Load #99 b.12. COLBY 3 (530555) 115.0 kV to Generator #C8 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0002 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. CLBYT1 1 (530645) 13.8 kV to remove bus # b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Generator #C8 b.12. COLBY 3 (530555) 115.0 kV to Load #99 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0003 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0004 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0005 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0006 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.4. GMECG1 1 (530674) 13.8 kV to remove bus # b.5. GMECG2 1 (530675) 13.8 kV to remove bus # b.6. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0007 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMECG1 1 (530674) 13.8 kV to remove bus # b.3. GMECG2 1 (530675) 13.8 kV to remove bus # b.5. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.6. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.7. N HAYS3 (530581) 115.0 kV to remove bus # b.8. VINETAP3 (530693) 115.0 kV to remove bus # b.9. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0008 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to remove bus # b.4. VINETAP3 (530693) 115.0 kV to remove bus # b.5. GMECG1 1 (530674) 13.8 kV to remove bus # b.6. GMECG2 1 (530675) 13.8 kV to remove bus # b.7. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0009 | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 (530553) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. ANGUS 3 (530714) 115.0 kV to GORHAM 3 (530552) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.5. ANGUS 3 (530714) 115.0 kV to Load #1 b.6. PFEIFER 3 (530725) 115.0 kV to Load #1 b.7. ANGUS 3 (530714) 115.0 kV to remove bus # b.8. PFEIFER 3 (530725) 115.0 kV to remove bus # b.9. GORHAM 3 (530552) 115.0 kV to Load #1 b.10. RUSLPMP3 (530684) 115.0 kV to Load #1 b.11. GORHAM 3 (530552) 115.0 kV to remove bus # b.12. RUSLPMP3 (530684) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0010 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0011 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0012 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0013 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0014 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0015 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.4. BUCKE_WTG (530705) 0.7 kV to remove bus # b.5. BUCKW_WTG (530708) 0.7 kV to remove bus # b.6. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.7. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.8. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.9. BUCKW_TERT (530706) 13.8 kV to remove bus # b.10. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.11. BUCKE_TERT (530709) 13.8 kV to remove bus # b.12. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0016 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0017 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0018 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0019 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0020 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0021 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0022 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0023 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0024 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. SMOKYHL6 (530592) 230.0 kV to SMKYP2 6 (530599) 230.0 kV Transmission Circuit #1 b.4. SHG2 34 1 (530715) 34.5 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus # b.6. SMKYP2 6 (530599) 230.0 kV to remove bus # b.7. SHP234 1 (530604) 34.5 kV to remove bus # b.8. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0025 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 38 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus # b.3. SMKYP1 6 (530593) 230.0 kV to remove bus # b.4. SMKYP1G1 (530594) 0.7 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus # b.6. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0026 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.3. SMKYT2 1 (530634) 13.9 kV to Generator #1 b.4. SMKYT2 1 (530634) 13.9 kV to remove bus # b.5. SMKYP1G1 (530594) 0.7 kV to remove bus # b.6. SMKYP1 6 (530593) 230.0 kV to remove bus # b.7. SHP134 1 (530595) 34.5 kV to remove bus # b.8. SMKYT1 1 (530633) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0027 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus # b.3. SMKYP1 6 (530593) 230.0 kV to remove bus # b.4. SMKYP1G1 (530594) 0.7 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0028 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0029 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0030 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0031 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0032 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.3. LACROS 3 (530603) 115.0 kV to remove bus # b.4. NEKOMA 3 (530608) 115.0 kV to remove bus # b.5. ALXNDR 3 (530606) 115.0 kV to remove bus # b.7. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.8. HZRNGPL3 (530609) 115.0 kV to remove bus # b.9. ALEXNDR1 (539702) 34.5 kV to Load #1 b.10. LAXTAP 3 (530602) 115.0 kV to remove bus # b.11. NKMA2 1 (530630) 12.5 kV to remove bus # b.12. ALEXNDR1 (539702) 34.5 kV to remove bus # b.13. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0033 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0034 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.4. LACROS 3 (530603) 115.0 kV to remove bus # b.5. NEKOMA 3 (530608) 115.0 kV to remove bus # b.6. ALXNDR 3 (530606) 115.0 kV to remove bus # b.8. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.9. ALEXNDR1 (539702) 34.5 kV to Load #1 b.10. LAXTAP 3 (530602) 115.0 kV to remove bus # b.11. NKMA2 1 (530630) 12.5 kV to remove bus # b.12. ALEXNDR1 (539702) 34.5 kV to remove bus # b.13. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0035 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0036 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 6 (530686) 230.0 kV to remove bus # b.3. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. PRWINDG1 (530690) 0.7 kV to Generator #1 b.6. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.7. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.8. PRWINDG1 (530690) 0.7 kV to remove bus # b.9. BUFCRKT11 (530691) 12.5 kV to remove bus # b.10. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0037 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0038 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0039 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. COLBY 3 (530555) 115.0 kV to remove bus # b.6. CLBYT1 1 (530645) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0040 | Single Phase Fault with Stuck Breaker on BEACH 3 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 (530557) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HOXIE 3 (530556) 115.0 kV Transmission Circuit #1 b.5. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.6. BEACH 3 (530557) 115.0 kV to remove bus # b.7. HILLCTY3 (531387) 34.5 kV to Generator #1 b.8. HILLCTY3 (531387) 34.5 kV to Generator #2 b.9. HILLCTY3 (531387) 34.5 kV to Generator #3 b.10. HILLCTY3 (531387) 34.5 kV to Generator #4 b.11. HILLCTY3 (531387) 34.5 kV to Generator #5 b.12. HILLCTY3 (531387) 34.5 kV to Generator #6 b.13. HILLCTY3 (531387) 34.5 kV to remove bus # b.14. REDLIN 3 (530605) 115.0 kV to remove bus # b.15. HOXIE 3 (530556) 115.0 kV to remove bus # b.16. REDLIN 3 (530605) 115.0 kV to Load #71 b.17. HOXIE 3 (530556) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0041 | Single Phase Fault with Stuck Breaker on ATWOOD 3 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 (530554) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to remove bus # b.5. ATWOOD 3 (530554) 115.0 kV to Generator #1 b.6. HILLCTY3 (531387) 34.5 kV to Generator #1 b.7. HILLCTY3 (531387) 34.5 kV to Generator #2 b.8. HILLCTY3 (531387) 34.5 kV to Generator #3 b.9. HILLCTY3 (531387) 34.5 kV to Generator #4 b.10. HILLCTY3 (531387) 34.5 kV to Generator #5 b.11. HILLCTY3 (531387) 34.5 kV to Generator #6 b.12. ATWOOD 3 (530554) 115.0 kV to Load #1 b.13. ATWOOD 3 (530554) 115.0 kV to Load #41 b.14. ATWOOD 3 (530554) 115.0 kV to remove bus # b.15. HILLCTY3 (531387) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_MIDW_FAULT_0042 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0001 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.2. JEC U1 (532651) 26.0 kV to remove bus # b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0002 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.2. JEC U2 (532652) 26.0 kV to remove bus # b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0003 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.2. JEC U3 (532653) 26.0 kV to remove bus # b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0004 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0005 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0006 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0007 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #1 b.4. EMPEC121 (532740) 13.8 kV to Generator #2 b.5. EMPEC121 (532740) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0008 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.2. EMPEC121 (532740) 13.8 kV to Generator #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #2 b.4. EMPEC121 (532740) 13.8 kV to remove bus # b.5. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0009 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0010 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.2. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.3. EMPEC7 1 (532744) 18.0 kV to remove bus # b.4. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0011 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0012 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0013 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0014 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0015 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0016 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0017 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0018 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0019 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0020 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0021 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0022 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0023 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0024 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0025 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0026 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0027 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0028 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to remove bus # b.4. RANDLPH5 (543027) 161.0 kV to Load #1 b.5. RANDLPH5 (543027) 161.0 kV to Load #4 b.6. RANDLPH5 (543027) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0029 | Single Phase Fault with Stuck Breaker on Hawthorn South (542973) 161 kV Bus a. Apply Fault at the Hawthorn South (542973) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0030 | Single Phase Fault with Stuck Breaker on Hawthorn 161 kV (542973) 161 kV Bus a. Apply Fault at the Hawthorn 161 kV (542973) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@1 b.2. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0031 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0032 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0033 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0034 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0035 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0036 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. IAT G1 1 (542957) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0037 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0038 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0039 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0040 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. LAC G2 1 (542956) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0041 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0042 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 b.4. NEASTN5 (543666) 161.0 kV to Load #78 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0043 | Single Phase Fault with Stuck Breaker on Stilwell 345 kV (542968) 345 kV Bus a. Apply Fault at the Stilwell 345 kV (542968) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0044 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0045 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0046 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to JEC N 7 (532766) 345.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0047 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0048 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0049 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0050 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0051 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0052 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0053 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0054 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 5.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0055 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0056 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0057 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0058 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0059 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0060 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0061 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0062 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0063 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0064 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0065 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0066 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0067 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0068 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0069 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0070 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0071 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0072 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@1 b.2. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0073 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0074 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0075 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0076 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0077 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IAT G1 1 (542957) 24.0 kV to remove bus # b.2. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0078 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to remove bus # b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0079 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 b.3. LACYGNE2 (543659) 69.0 kV to remove bus # b.4. LAC_LAKE_2 (541541) 69.0 kV to remove bus # b.5. LAC_LAKE_2 (541541) 69.0 kV to Load #K1 b.6. LAC_LAKE_2 (541541) 69.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0080 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0081 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0082 | Single Phase Fault with Stuck Breaker on Northeast North (543666) 161 kV Bus a. Apply Fault at the Northeast North (543666) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NEASTN5 (543666) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to remove bus # b.4. NE CT14 (542971) 13.8 kV to remove bus # b.5. NEASTN5 (543666) 161.0 kV to Load #56 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0083 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NE CT17 (542983) 13.8 kV to remove bus # b.2. NE CT18 (542984) 13.8 kV to remove bus # b.3. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.4. NEASTS5 (542985) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 b.5. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 b.6. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0084 | Single Phase Fault with Stuck Breaker on Stilwell 345 kV (542968) 345 kV Bus a. Apply Fault at the Stilwell 345 kV (542968) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0085 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0086 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Transfer | GROUP3_P4_EVERGY_FAULT_0087 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0001 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0002 | 3 Phase fault on 5ELDON 1 161.00 (344532) 161 kV Bus a. Apply fault at the 5ELDON 1 161.00 (344532) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.2. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.3. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.4. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0003 | 3 Phase fault on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOYMART 1 (344040) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.2. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0004 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0005 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0006 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0007 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0008 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0009 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BOONE (300061) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0010 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0011 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0012 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0013 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0014 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0015 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0016 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0017 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0018 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0019 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0020 | 3 Phase fault on OAKGRV 5 161.00 (541227) 161 kV Bus a. Apply fault at the OAKGRV 5 161.00 (541227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAINVL5 (541226) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 b.2. OAKGRV 5 (541227) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0021 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0022 | 3 Phase fault on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0023 | 3 Phase fault on STALEY 2 69.000 (541261) 69 kV Bus a. Apply fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0024 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0025 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0026 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0027 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0028 | 3 Phase fault on BRMALL 2 69.000 (541283) 69 kV Bus a. Apply fault at the BRMALL 2 69.000 (541283) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMALL 2 (541283) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0029 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0030 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0031 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0032 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0033 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0034 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0035 | 3 Phase fault on SUB E 69.000 (548804) 69 kV Bus a. Apply fault at the SUB E 69.000 (548804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0036 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0037 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0038 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0039 | 3 Phase fault on SUB B 69.000 (548810) 69 kV Bus a. Apply fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0040 | 3 Phase fault on SUB J 69.000 (548811) 69 kV Bus a. Apply fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0041 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0042 | 3 Phase fault on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0043 | 3 Phase fault on STRLNGRD 69.000 (548826) 69 kV Bus a. Apply fault at the STRLNGRD 69.000 (548826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.3. SUB C (548825) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0044 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0045 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0046 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0047 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0048 | 3 Phase fault on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0049 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0050 | 3 Phase fault on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0051 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0052 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0053 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 b.2. ST JOE_CAP5 (541147) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0054 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.3. RNRIDGE_CAP5 (541145) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0055 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0056 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 b.2. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0057 | 3 Phase fault on NAVY 5 161.00 (542989) 161 kV Bus a. Apply fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0058 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0059 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0060 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. BARRY_CAP 5 (542944) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0061 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0062 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0063 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0064 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0065 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0066 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0067 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0068 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0069 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0070 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0071 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0072 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0073 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0074 | 3 Phase fault on MILCKJT2 69.000 (543110) 69 kV Bus a. Apply fault at the MILCKJT2 69.000 (543110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.3. IND WTR2 (543086) 69.0 kV to CEMCITY2 (543090) 69.0 kV Transmission Circuit #1 b.4. IND WTR2 (543086) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.5. TMP LAF2 (543103) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.6. LAFJCT 2 (543104) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.7. MILCKJT2 (543110) 69.0 kV to LAFARGE2 (543111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0075 | 3 Phase fault on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 b.3. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0076 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0077 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0078 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0079 | 3 Phase fault on WPRTTS 2 69.000 (530596) 69 kV Bus a. Apply fault at the WPRTTS 2 69.000 (530596) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.2. GB STH 2 (530569) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.3. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.4. WPRTTS 2 (530596) 69.0 kV to WPRT2 2 (530597) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0080 | 3 Phase fault on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0081 | 3 Phase fault on COLLEG 2 69.000 (530574) 69 kV Bus a. Apply fault at the COLLEG 2 69.000 (530574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 b.2. COLLEG 2 (530574) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0082 | 3 Phase fault on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0083 | 3 Phase fault on NEKOMA 2 69.000 (530564) 69 kV Bus a. Apply fault at the NEKOMA 2 69.000 (530564) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0084 | 3 Phase fault on BKHLTAP2 69.000 (530589) 69 kV Bus a. Apply fault at the BKHLTAP2 69.000 (530589) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.2. SUSANK 2 (530571) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.3. BNK HL 2 (530572) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 b.4. HITHMN 2 (530573) 69.0 kV to BKHLTAP2 (530589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0085 | 3 Phase fault on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0086 | 3 Phase fault on HEIZER 2 69.000 (530563) 69 kV Bus a. Apply fault at the HEIZER 2 69.000 (530563) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0087 | 3 Phase fault on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0088 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0089 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0090 | 3 Phase fault on SEGNTP 3 115.00 (530682) 115 kV Bus a. Apply fault at the SEGNTP 3 115.00 (530682) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEGNTP 3 (530682) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0091 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.5. SEWARD 2 (530565) 69.0 kV to SEWRDMW3 (530679) 115.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0092 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0093 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0094 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0095 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0096 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.2. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.3. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.6. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0097 | 3 Phase fault on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0098 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0099 | 3 Phase fault on HOXIE 3 115.00 (530556) 115 kV Bus a. Apply fault at the HOXIE 3 115.00 (530556) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0100 | 3 Phase fault on ANGELUS 115.00 (530717) 115 kV Bus a. Apply fault at the ANGELUS 115.00 (530717) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.2. SEGNTP 3 (530682) 115.0 kV to SEGUIN 3 (530683) 115.0 kV Transmission Circuit #1 b.3. SEGUIN 3 (530683) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0101 | 3 Phase fault on HUNTSVL3 115.00 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 115.00 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0102 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0103 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0104 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0105 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0106 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0107 | 3 Phase fault on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0108 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0109 | 3 Phase fault on GRHMSUB3 115.00 (531386) 115 kV Bus a. Apply fault at the GRHMSUB3 115.00 (531386) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0110 | 3 Phase fault on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0111 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0112 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0113 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0114 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0115 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0116 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0117 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0118 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0119 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0120 | 3 Phase fault on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0121 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0122 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0123 | 3 Phase fault on COLBY 3 115.00 (530555) 115 kV Bus a. Apply fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBY 3 (530555) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0124 | 3 Phase fault on BEACH 3 115.00 (530557) 115 kV Bus a. Apply fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0125 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0126 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0127 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0128 | 3 Phase fault on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.2. STOCKVL7 (640365) 115.0 kV to STOCKVL8 (640366) 69.0 kV to STOCKVLLET19 (643146) 13.8 kV Three Winding #1 b.4. STOCKVLLET19 (643146) 13.8 kV to STOCKVL8 (640366) 69.0 kV to STOCKVL7 (640365) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0129 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0130 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0131 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0132 | 3 Phase fault on ATHEY 7 115.00 (641244) 115 kV Bus a. Apply fault at the ATHEY 7 115.00 (641244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 b.2. ATHEY 7 (641244) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 b.3. LAMAR___-TS7 (659804) 115.0 kV to CRETE___-TS7 (659813) 115.0 kV Transmission Circuit #1 b.4. CRETE___-TS7 (659813) 115.0 kV to CRETEHE_-TS7 (659823) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0133 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0134 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0135 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0136 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0137 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0138 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0139 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0140 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0141 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0142 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0143 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0144 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0145 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0146 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0147 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0148 | 3 Phase fault on BEVERLY8 69.000 (640083) 69 kV Bus a. Apply fault at the BEVERLY8 69.000 (640083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0149 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0150 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0151 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0152 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0153 | 3 Phase fault on MCCOOK 8 69.000 (640270) 69 kV Bus a. Apply fault at the MCCOOK 8 69.000 (640270) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0154 | 3 Phase fault on STOCKVL8 69.000 (640366) 69 kV Bus a. Apply fault at the STOCKVL8 69.000 (640366) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKVL8 (640366) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0155 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0156 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0157 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0158 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0159 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0160 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G21-021 (765492) | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0161 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0162 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0163 | 3 Phase fault on ANTHONY4 138.00 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 138.00 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0164 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0165 | 3 Phase fault on GRINNEL3 115.00 (531412) 115 kV Bus a. Apply fault at the GRINNEL3 115.00 (531412) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PH RUN 3 (530559) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 b.2. ARNOLD3 (531409) 115.0 kV to GOVE 3 (531411) 115.0 kV Transmission Circuit #1 b.3. ARNOLD3 (531409) 115.0 kV to RANSOM 3 (531414) 115.0 kV Transmission Circuit #1 b.4. GOVE 3 (531411) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0166 | 3 Phase fault on SETAB 3 115.00 (531464) 115 kV Bus a. Apply fault at the SETAB 3 115.00 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0167 | 3 Phase fault on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0168 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0169 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0170 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0171 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0172 | 3 Phase fault on WILLIAM3 115.00 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 115.00 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0173 | 3 Phase fault on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEOTI 3 (531428) 115.0 kV to SELKIRK3 (531434) 115.0 kV Transmission Circuit #1 b.2. LEOTI 3 (531428) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 b.3. SELKIRK3 (531434) 115.0 kV to TRIB SW3 (531438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0174 | 3 Phase fault on ATWODSW3 115.00 (531364) 115 kV Bus a. Apply fault at the ATWODSW3 115.00 (531364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.2. LUDELLT3 (531220) 115.0 kV to LUDELL 3 (531221) 115.0 kV Transmission Circuit #1 b.3. LUDELLT3 (531220) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.4. LUDELLT3 (531220) 115.0 kV to HERNDON3 (531367) 115.0 kV Transmission Circuit #1 b.5. ATWODSW3 (531364) 115.0 kV to NATWOOD3 (531369) 115.0 kV Transmission Circuit #1 b.6. HERNDON3 (531367) 115.0 kV to JOHNSON3 (531371) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0175 | 3 Phase fault on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.3. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0176 | 3 Phase fault on GANO 3 115.00 (531493) 115 kV Bus a. Apply fault at the GANO 3 115.00 (531493) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.3. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0177 | 3 Phase fault on KSAVWTP3 115.00 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 115.00 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0178 | 3 Phase fault on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0179 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0180 | 3 Phase fault on SUNCITY3 115.00 (539697) 115 kV Bus a. Apply fault at the SUNCITY3 115.00 (539697) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.3. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.4. GRNBURG3 (539664) 115.0 kV to GRNBURG1 (539710) 34.5 kV to GRNBUG-T (539910) 13.8 kV Three Winding #1 b.5. SUNCITY3 (539697) 115.0 kV to SUNCITY1 (539733) 34.5 kV to SUNCT-T (539937) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0181 | 3 Phase fault on FORD 3 115.00 (539758) 115 kV Bus a. Apply fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.3. FORD 3 (539758) 115.0 kV to FORD 1 (539765) 34.5 kV to FORD T (539968) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0182 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0183 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0184 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0185 | 3 Phase fault on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0186 | 3 Phase fault on CUDAHY 3 115.00 (539659) 115 kV Bus a. Apply fault at the CUDAHY 3 115.00 (539659) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.2. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.3. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.4. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 b.5. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.6. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0187 | 3 Phase fault on DCBEEF3 115.00 (539645) 115 kV Bus a. Apply fault at the DCBEEF3 115.00 (539645) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0188 | 3 Phase fault on SPEARVL3 115.00 (539694) 115 kV Bus a. Apply fault at the SPEARVL3 115.00 (539694) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0189 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0190 | 3 Phase fault on N-DODGE3 115.00 (539680) 115 kV Bus a. Apply fault at the N-DODGE3 115.00 (539680) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DODG3 (539641) 115.0 kV to N-DODGE3 (539680) 115.0 kV Transmission Circuit #1 b.2. N-DODGE3 (539680) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. N-DODGE3 (539680) 115.0 kV to N-DODGE1 (539720) 34.5 kV to N-DODG-T (539922) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0191 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0192 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0193 | 3 Phase fault on WALDO 3 115.00 (539698) 115 kV Bus a. Apply fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.4. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0194 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.4. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0195 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0196 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0197 | 3 Phase fault on HARPER 4 138.00 (539668) 138 kV Bus a. Apply fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0198 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G11-008 (539858) and G19-063 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0199 | 3 Phase fault on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL3 (539701) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0200 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0201 | 3 Phase fault on BYRONTP4 138.00 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 138.00 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.2. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0202 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0203 | 3 Phase fault on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0204 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0205 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0206 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0207 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0208 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0209 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0210 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0211 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0212 | 3 Phase fault on CARB-KW 3 115.00 (533195) 115 kV Bus a. Apply fault at the CARB-KW 3 115.00 (533195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 b.2. CARB-KW 3 (533195) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0213 | 3 Phase fault on OSAGE J3 115.00 (533171) 115 kV Bus a. Apply fault at the OSAGE J3 115.00 (533171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.2. OSAGE 3 (533170) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 b.3. OSAGE J3 (533171) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.4. OSAGE J3 (533171) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.5. READING3 (533306) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0214 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGCRK3 (533380) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.2. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.4. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0215 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0216 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0217 | 3 Phase fault on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0218 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0219 | 3 Phase fault on MORRIS 3 115.00 (533305) 115 kV Bus a. Apply fault at the MORRIS 3 115.00 (533305) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0220 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0221 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0222 | 3 Phase fault on NW LEAV3 115.00 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 115.00 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0223 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.2. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0224 | 3 Phase fault on STRANGR3 115.00 (533268) 115 kV Bus a. Apply fault at the STRANGR3 115.00 (533268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0225 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0226 | 3 Phase fault on FOWLER 4 138.00 (533043) 138 kV Bus a. Apply fault at the FOWLER 4 138.00 (533043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0227 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0228 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0229 | 3 Phase fault on 47TH ST4 138.00 (533058) 138 kV Bus a. Apply fault at the 47TH ST4 138.00 (533058) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0230 | 3 Phase fault on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0231 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0232 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0233 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0234 | 3 Phase fault on BELAIRE4 138.00 (532988) 138 kV Bus a. Apply fault at the BELAIRE4 138.00 (532988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0235 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0236 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0237 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0238 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0239 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0240 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0241 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0242 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0243 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0244 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0245 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0246 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0247 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0248 | 3 Phase fault on BU11PON4 138.00 (533032) 138 kV Bus a. Apply fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0249 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0250 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0251 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G17-068 (589063). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0252 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0253 | 3 Phase fault on BEECHTP4 138.00 (533028) 138 kV Bus a. Apply fault at the BEECHTP4 138.00 (533028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.2. BEECH 4 (533027) 138.0 kV to BEECHTP4 (533028) 138.0 kV Transmission Circuit #1 b.3. BEECHTP4 (533028) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 b.4. BEECHTP4 (533028) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0254 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0255 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0256 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0257 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0258 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0259 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0260 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0261 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0262 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0263 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0264 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0265 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0266 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0267 | 3 Phase fault on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0268 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0269 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0270 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0271 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0272 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0273 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0274 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0275 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0276 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0277 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0278 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0279 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0280 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0281 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0282 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0283 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0284 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0285 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0286 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0287 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0288 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0289 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0290 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0291 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0292 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0293 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0294 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0295 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0296 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0297 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0298 | 3 Phase fault on MEAD N 2 69.000 (533818) 69 kV Bus a. Apply fault at the MEAD N 2 69.000 (533818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD N 2 (533818) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0299 | 3 Phase fault on 17TH TP2 69.000 (533835) 69 kV Bus a. Apply fault at the 17TH TP2 69.000 (533835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.2. RIVERSD2 (533834) 69.0 kV to 17TH TP2 (533835) 69.0 kV Transmission Circuit #1 b.3. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.4. 17TH TP2 (533835) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.5. 17TH TP2 (533835) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0300 | 3 Phase fault on MOSSMAN2 69.000 (533820) 69 kV Bus a. Apply fault at the MOSSMAN2 69.000 (533820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSSMAN2 (533820) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0301 | 3 Phase fault on MASCOT 2 69.000 (533814) 69 kV Bus a. Apply fault at the MASCOT 2 69.000 (533814) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASCOT 2 (533814) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.2. MASCOT 2 (533814) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0302 | 3 Phase fault on EASTBOR2 69.000 (533792) 69 kV Bus a. Apply fault at the EASTBOR2 69.000 (533792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTBOR2 (533792) 69.0 kV to MINNEHA2 (533817) 69.0 kV Transmission Circuit #1 b.2. EASTBOR2 (533792) 69.0 kV to 64TH 2 (533842) 69.0 kV Transmission Circuit #1 b.3. MINNEHA2 (533817) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0303 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0304 | 3 Phase fault on ARCOTAP2 69.000 (533620) 69 kV Bus a. Apply fault at the ARCOTAP2 69.000 (533620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO 2 (533619) 69.0 kV to ARCOTAP2 (533620) 69.0 kV Transmission Circuit #1 b.2. ARCOTAP2 (533620) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.3. ARCOTAP2 (533620) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.4. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.5. COALCRK2 (533633) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.6. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0305 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0306 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to RA5HIPR2 (533706) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0307 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0308 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0309 | 3 Phase fault on ORCHARD2 69.000 (533643) 69 kV Bus a. Apply fault at the ORCHARD2 69.000 (533643) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.2. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.3. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0310 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0311 | 3 Phase fault on BELL 2 69.000 (533783) 69 kV Bus a. Apply fault at the BELL 2 69.000 (533783) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV to SC9ANSN2 (533866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0312 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 b.2. SC3MILL2 (533552) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 b.3. SC3MILL2 (533552) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 b.4. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0313 | 3 Phase fault on PECK 2 69.000 (533830) 69 kV Bus a. Apply fault at the PECK 2 69.000 (533830) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 b.2. GILL W 2 (533796) 69.0 kV to HAYSVJS2 (533802) 69.0 kV Transmission Circuit #1 b.3. HAYSVJS2 (533802) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0314 | 3 Phase fault on HYDRJS2 69.000 (533810) 69 kV Bus a. Apply fault at the HYDRJS2 69.000 (533810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALN 2 (533790) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 b.2. HYDRA N2 (533807) 69.0 kV to HYDRJS2 (533810) 69.0 kV Transmission Circuit #1 b.3. HYDRJS2 (533810) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 b.4. HYDRJS2 (533810) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0315 | 3 Phase fault on SHERIDN2 69.000 (533841) 69 kV Bus a. Apply fault at the SHERIDN2 69.000 (533841) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0316 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV to RIPLEYE2 (533859) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0317 | 3 Phase fault on BU5FURL2 69.000 (533861) 69 kV Bus a. Apply fault at the BU5FURL2 69.000 (533861) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THUNBRD2 (533603) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 b.2. CHISHLM2 (533786) 69.0 kV to GRANT 2 (533799) 69.0 kV Transmission Circuit #1 b.3. GRANT 2 (533799) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0318 | 3 Phase fault on WESTLNK2 69.000 (533854) 69 kV Bus a. Apply fault at the WESTLNK2 69.000 (533854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.3. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0319 | 3 Phase fault on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0320 | 3 Phase fault on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.2. SUNSET-2 (533844) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0321 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC7CRES2 (533555) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0322 | 3 Phase fault on WILLJCT2 69.000 (533713) 69 kV Bus a. Apply fault at the WILLJCT2 69.000 (533713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 b.2. WILLJCT2 (533713) 69.0 kV to ELKJSS 2 (533718) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0323 | 3 Phase fault on ELPASO 2 69.000 (533793) 69 kV Bus a. Apply fault at the ELPASO 2 69.000 (533793) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 2 (533793) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 b.2. ELPASO 2 (533793) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0324 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0325 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0326 | 3 Phase fault on WATER1 2 69.000 (533855) 69 kV Bus a. Apply fault at the WATER1 2 69.000 (533855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0327 | 3 Phase fault on WATER2 2 69.000 (533856) 69 kV Bus a. Apply fault at the WATER2 2 69.000 (533856) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.2. PLAZA E2 (533829) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0328 | 3 Phase fault on RIPLEYW2 69.000 (533832) 69 kV Bus a. Apply fault at the RIPLEYW2 69.000 (533832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.2. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.3. 21ST 2 (533846) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0329 | 3 Phase fault on INDEPEN2 69.000 (533694) 69 kV Bus a. Apply fault at the INDEPEN2 69.000 (533694) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDEPEN2 (533694) 69.0 kV to MONTGOM2 (533698) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0330 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0331 | 3 Phase fault on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0332 | 3 Phase fault on HYDRJN2 69.000 (533808) 69 kV Bus a. Apply fault at the HYDRJN2 69.000 (533808) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HYDRJN2 (533808) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.2. HYDRJN2 (533808) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0333 | 3 Phase fault on SENECA 2 69.000 (533839) 69 kV Bus a. Apply fault at the SENECA 2 69.000 (533839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.2. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.3. OSAGE 2 (533827) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0334 | 3 Phase fault on MEAD S 2 69.000 (533815) 69 kV Bus a. Apply fault at the MEAD S 2 69.000 (533815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0335 | 3 Phase fault on HAYSVJN2 69.000 (533804) 69 kV Bus a. Apply fault at the HAYSVJN2 69.000 (533804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 b.2. HAYSVJN2 (533804) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0336 | 3 Phase fault on LIN 2 69.000 (533812) 69 kV Bus a. Apply fault at the LIN 2 69.000 (533812) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.2. LIN 2 (533812) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 b.3. SUNSET-2 (533844) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 b.4. SG1CHEN2 (533871) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0337 | 3 Phase fault on MAHANNA2 69.000 (533738) 69 kV Bus a. Apply fault at the MAHANNA2 69.000 (533738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAHANNA2 (533738) 69.0 kV to ADAMS 2 (533746) 69.0 kV Transmission Circuit #1 b.2. MAHANNA2 (533738) 69.0 kV to GRANT J2 (533800) 69.0 kV Transmission Circuit #1 b.3. NEWTON 2 (533745) 69.0 kV to ADAMS 2 (533746) 69.0 kV Transmission Circuit #1 b.4. GRANT J2 (533800) 69.0 kV to RIPLEYW2 (533832) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0338 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0339 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0340 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0341 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0342 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0343 | 3 Phase fault on ASHGRJ22 69.000 (533660) 69 kV Bus a. Apply fault at the ASHGRJ22 69.000 (533660) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.2. ASHGRV22 (533658) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.3. ASHGRJ12 (533659) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #z1 b.4. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0344 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 b.3. EMANHAT6 (532861) 230.0 kV to EMANHAT3 (533326) 115.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0345 | 3 Phase fault on 64TH 4 138.00 (533066) 138 kV Bus a. Apply fault at the 64TH 4 138.00 (533066) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRY 4 (533048) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 b.3. 64TH 4 (533066) 138.0 kV to 64TH 2 (533842) 69.0 kV to 64TH 1 (533113) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0346 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0347 | 3 Phase fault on CANAL 4 138.00 (533033) 138 kV Bus a. Apply fault at the CANAL 4 138.00 (533033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. CANAL 4 (533033) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #1 b.3. CANAL 4 (533033) 138.0 kV to CANALS 2 (533784) 69.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0348 | 3 Phase fault on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0349 | 3 Phase fault on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.3. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.4. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0350 | 3 Phase fault on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0351 | 3 Phase fault on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0352 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.4. MONTGOM1 (533091) 13.2 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0353 | 3 Phase fault on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0354 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0355 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0356 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAUGHN 3 (533308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0357 | 3 Phase fault on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0358 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0359 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0360 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0361 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0362 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0363 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0364 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0365 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0366 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0367 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0368 | 3 Phase fault on BELL 2 69.000 (533783) 69 kV Bus a. Apply fault at the BELL 2 69.000 (533783) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0369 | 3 Phase fault on CANALN 2 69.000 (533790) 69 kV Bus a. Apply fault at the CANALN 2 69.000 (533790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALN 2 (533790) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0370 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0371 | 3 Phase fault on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0372 | 3 Phase fault on MACARTH2 69.000 (533813) 69 kV Bus a. Apply fault at the MACARTH2 69.000 (533813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACARTH2 (533813) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0373 | 3 Phase fault on MONTGOM2 69.000 (533698) 69 kV Bus a. Apply fault at the MONTGOM2 69.000 (533698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0374 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0375 | 3 Phase fault on PARSONS2 69.000 (533704) 69 kV Bus a. Apply fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0376 | 3 Phase fault on TIOGA 2 69.000 (533646) 69 kV Bus a. Apply fault at the TIOGA 2 69.000 (533646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0377 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0378 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0379 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0380 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0381 | 3 Phase fault on KEYSTON7 115.00 (640253) 115 kV Bus a. Apply fault at the KEYSTON7 115.00 (640253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0382 | 3 Phase fault on CHELSA4 138.00 (510410) 138 kV Bus a. Apply fault at the CHELSA4 138.00 (510410) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHELSA4 (510410) 138.0 kV to G22-234-TAP (771660) 138.0 kV Transmission Circuit #1 b.2. ALWUETP4 (510429) 138.0 kV to G22-234-TAP (771660) 138.0 kV Transmission Circuit #1 b.3. N.E.S.-4 (510396) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.4. CHELSA4 (510410) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.5. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0383 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0384 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 (510418) 69.0 kV to VINTAJC4 (510417) 138.0 kV to VINJT1-1 (510367) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0385 | 3 Phase fault on TERRACE5 161.00 (542991) 161 kV Bus a. Apply fault at the TERRACE5 161.00 (542991) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0386 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0387 | 3 Phase fault on BARBER 5 161.00 (546651) 161 kV Bus a. Apply fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0388 | 3 Phase fault on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0389 | 3 Phase fault on GIBBS 5 161.00 (546658) 161 kV Bus a. Apply fault at the GIBBS 5 161.00 (546658) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0390 | 3 Phase fault on PIPER 5 161.00 (546668) 161 kV Bus a. Apply fault at the PIPER 5 161.00 (546668) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0391 | 3 Phase fault on KAW 2 69.000 (546678) 69 kV Bus a. Apply fault at the KAW 2 69.000 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to BARBER 2 (546691) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0392 | 3 Phase fault on BARBER 5 161.00 (546651) 161 kV Bus a. Apply fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0393 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0394 | 3 Phase fault on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0395 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0396 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to 412SUB 5 (512637) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0397 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0398 | 3 Phase fault on 5ELMCRK 161.00 (300993) 161 kV Bus a. Apply fault at the 5ELMCRK 161.00 (300993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ELMCRK (300993) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit #1 b.2. 5ELMCRK (300993) 161.0 kV to CATSAGR5 (512638) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0399 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0400 | 3 Phase fault on NWMAID5 161.00 (512757) 161 kV Bus a. Apply fault at the NWMAID5 161.00 (512757) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0401 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0402 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0403 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0404 | 3 Phase fault on KANSATP5 161.00 (512714) 161 kV Bus a. Apply fault at the KANSATP5 161.00 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 412SUB 5 (512637) 161.0 kV to KANSATP5 (512714) 161.0 kV Transmission Circuit #1 b.2. KANSATP5 (512714) 161.0 kV to KANSAS 5 (512716) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0405 | 3 Phase fault on PENSA 5 161.00 (512654) 161 kV Bus a. Apply fault at the PENSA 5 161.00 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0406 | 3 Phase fault on LOCSTGVKM 5 161.00 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 161.00 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0407 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0408 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0409 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0410 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0411 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0412 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0413 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0414 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0415 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0416 | 3 Phase fault on 2NEWPORT 69.000 (301467) 69 kV Bus a. Apply fault at the 2NEWPORT 69.000 (301467) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MONKEY (301465) 69.0 kV to 2NEWPORT (301467) 69.0 kV Transmission Circuit #1 b.2. 2NEWPORT (301467) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0417 | 3 Phase fault on SAILBOA2 69.000 (510409) 69 kV Bus a. Apply fault at the SAILBOA2 69.000 (510409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAILBOA2 (510409) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0418 | 3 Phase fault on AMERCAST S2 69.000 (512681) 69 kV Bus a. Apply fault at the AMERCAST S2 69.000 (512681) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to AMERCAST S2 (512681) 69.0 kV Transmission Circuit #1 b.2. CPPTAP 2 (512661) 69.0 kV to AMERCAST S2 (512681) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0419 | 3 Phase fault on REDDEN 2 69.000 (512698) 69 kV Bus a. Apply fault at the REDDEN 2 69.000 (512698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 2 (512626) 69.0 kV to REDDEN 2 (512698) 69.0 kV Transmission Circuit #1 b.2. AMERCAST N2 (512683) 69.0 kV to CASTING TAP2 (512685) 69.0 kV Transmission Circuit #1 b.3. CASTING TAP2 (512685) 69.0 kV to REDDEN 2 (512698) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0420 | 3 Phase fault on CLEORTP2 69.000 (512692) 69 kV Bus a. Apply fault at the CLEORTP2 69.000 (512692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLEORA (301460) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 b.2. PENSA 2 (512628) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 b.3. AFTON 2 (512633) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0421 | 3 Phase fault on ESH TP 2 69.000 (512680) 69 kV Bus a. Apply fault at the ESH TP 2 69.000 (512680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2J6 (300829) 69.0 kV to AFTP TP2 (512620) 69.0 kV Transmission Circuit #1 b.2. 2J6 (300829) 69.0 kV to VINEOTP2 (512673) 69.0 kV Transmission Circuit #1 b.3. 2VINITAHQ (300983) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.4. 2ESHOSP (301468) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.5. 2VIN NEO (301478) 69.0 kV to VINEOTP2 (512673) 69.0 kV Transmission Circuit #1 b.6. VINITA-2 (510404) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.7. AFTONTP2 (510415) 69.0 kV to A-CONT 2 (510427) 69.0 kV Transmission Circuit #1 b.8. AFTONTP2 (510415) 69.0 kV to AFTN-EX2 (510428) 69.0 kV Transmission Circuit #1 b.9. AFTONTP2 (510415) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.10. AFTP TP2 (512620) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.11. AFTON 2 (512633) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.12. VINEOTP2 (512673) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0422 | 3 Phase fault on FAIRTAP2 69.000 (512708) 69 kV Bus a. Apply fault at the FAIRTAP2 69.000 (512708) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to FAIRNEO2 (512691) 69.0 kV Transmission Circuit #1 b.2. AFTON 2 (512633) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 b.3. FAIRNEO2 (512691) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 b.4. FAIRTAP2 (512708) 69.0 kV to FRL363 2 (547583) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0423 | 3 Phase fault on MIAMI 2 69.000 (512630) 69 kV Bus a. Apply fault at the MIAMI 2 69.000 (512630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI1 2 (513020) 69.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI3 2 (513024) 69.0 kV Transmission Circuit #1 b.3. MIAMI1 2 (513020) 69.0 kV to MIAMI4 2 (513022) 69.0 kV Transmission Circuit #1 b.4. MIAMI4 2 (513022) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 b.5. MIAMI3 2 (513024) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0424 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0425 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0426 | 3 Phase fault on 2WLKRTP 69.000 (300760) 69 kV Bus a. Apply fault at the 2WLKRTP 69.000 (300760) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSHO (300750) 69.0 kV to 2WLKRTP (300760) 69.0 kV Transmission Circuit #1 b.2. 2WLKRTP (300760) 69.0 kV to 2WLKRVL (300761) 69.0 kV Transmission Circuit #1 b.3. 2WLKRTP (300760) 69.0 kV to 2SENECA (300830) 69.0 kV Transmission Circuit #1 b.4. 2SENECA (300830) 69.0 kV to 2MIAETP (300852) 69.0 kV Transmission Circuit #1 b.5. 2MIAETP (300852) 69.0 kV to MIAMI 2 (512630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0427 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0428 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0429 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0430 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0431 | 3 Phase fault on TONECE7 345.00 (512750) 345 kV Bus a. Apply fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0432 | 3 Phase fault on KERR BRK1 5 161.00 (512770) 161 kV Bus a. Apply fault at the KERR BRK1 5 161.00 (512770) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK1 5 (512770) 161.0 kV to KERR GR3 (512634) 115.0 kV to KERR1 1 (512846) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0433 | 3 Phase fault on KERR BRK4 5 161.00 (512771) 161 kV Bus a. Apply fault at the KERR BRK4 5 161.00 (512771) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR BRK4 5 (512771) 161.0 kV to KERR GR3 (512634) 115.0 kV to KERR2 1 (512847) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0434 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0435 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0436 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0437 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0438 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0439 | 3 Phase fault on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0440 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0441 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0442 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0443 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0444 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. HOC404A1 (547715) 12.5 kV to HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0445 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0446 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0447 | 3 Phase fault on 5MCBAIN T 161.00 (345071) 161 kV Bus a. Apply fault at the 5MCBAIN T 161.00 (345071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0448 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0449 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0450 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0451 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0452 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0453 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0454 | 3 Phase fault on 5APCH TP 161.00 (344026) 161 kV Bus a. Apply fault at the 5APCH TP 161.00 (344026) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0455 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MPLTAP (300036) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 b.3. 5MPLTAP (300036) 161.0 kV to 5LATHROP (344923) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0456 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0457 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0458 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0459 | 3 Phase fault on 5LOYMART 1 161.00 (344040) 161 kV Bus a. Apply fault at the 5LOYMART 1 161.00 (344040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOYMART 1 (344040) 161.0 kV to 5LOYMART 2 (344041) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0460 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0461 | 3 Phase fault on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GUTHRIE 1 (344677) 161.0 kV to 5GUTHRIE 2 (344678) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0462 | 3 Phase fault on 5JC ZION 161.00 (344814) 161 kV Bus a. Apply fault at the 5JC ZION 161.00 (344814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JC ZION (344814) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #z b.2. 2JC ZION (346089) 69.0 kV to 5JC ZION (344814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0463 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0464 | 3 Phase fault on J1490_POI 345.00 (44888) 345 kV Bus a. Apply fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J1490_POI (44888) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0465 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0466 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0467 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to VSC2_3 (992003) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0468 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0469 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0470 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BOONE (300061) 161.0 kV to 5MCBAINB1 (300501) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0471 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BOONE (300061) 161.0 kV to 5MLRSBGB1 (300519) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0472 | 3 Phase fault on 5CALIF 161.00 (300063) 161 kV Bus a. Apply fault at the 5CALIF 161.00 (300063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF (300063) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0473 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0474 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0475 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0476 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0477 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0478 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0479 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0480 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0481 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0482 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0483 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0484 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0485 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0486 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0487 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0488 | 3 Phase fault on 5OSBORN 161.00 (300107) 161 kV Bus a. Apply fault at the 5OSBORN 161.00 (300107) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSBORN (300107) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0489 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0490 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0491 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0492 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0493 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2MOCITY (300304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0494 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0495 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0496 | 3 Phase fault on 2ASHLND 69.000 (300492) 69 kV Bus a. Apply fault at the 2ASHLND 69.000 (300492) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHLND (300492) 69.0 kV to 2BOONE (300493) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0497 | 3 Phase fault on 2BOONE 69.000 (300493) 69 kV Bus a. Apply fault at the 2BOONE 69.000 (300493) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOONE (300493) 69.0 kV to 2DEERPK (300497) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0498 | 3 Phase fault on 2BOONE 69.000 (300493) 69 kV Bus a. Apply fault at the 2BOONE 69.000 (300493) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOONE (300493) 69.0 kV to 2GRINDSTN (343006) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0499 | 3 Phase fault on 5MCBAINB1 161.00 (300501) 161 kV Bus a. Apply fault at the 5MCBAINB1 161.00 (300501) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAINB1 (300501) 161.0 kV to 5MCBAINB2 (301489) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0500 | 3 Phase fault on 5MLRSBGB1 161.00 (300519) 161 kV Bus a. Apply fault at the 5MLRSBGB1 161.00 (300519) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MLRSBGB1 (300519) 161.0 kV to 5MLRSBGB2 (301498) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0501 | 3 Phase fault on 2DRESDN 69.000 (300528) 69 kV Bus a. Apply fault at the 2DRESDN 69.000 (300528) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DRESDN (300528) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0502 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0503 | 3 Phase fault on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0504 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0505 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0506 | 3 Phase fault on 2HUGHSV 69.000 (300533) 69 kV Bus a. Apply fault at the 2HUGHSV 69.000 (300533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HUGHSV (300533) 69.0 kV to 2SWSPJC (300543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0507 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0508 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0509 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0510 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0511 | 3 Phase fault on 2SMTHTN 69.000 (300542) 69 kV Bus a. Apply fault at the 2SMTHTN 69.000 (300542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMTHTN (300542) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0512 | 3 Phase fault on 2CALIF 69.000 (300550) 69 kV Bus a. Apply fault at the 2CALIF 69.000 (300550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 2FORTNA (300554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0513 | 3 Phase fault on 2CALIF 69.000 (300550) 69 kV Bus a. Apply fault at the 2CALIF 69.000 (300550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 2PRARIE (300561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0514 | 3 Phase fault on 2CALIF 69.000 (300550) 69 kV Bus a. Apply fault at the 2CALIF 69.000 (300550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 2ST_MARTINS (301442) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0515 | 3 Phase fault on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FORTNA (300554) 69.0 kV to 2NEEDY (300559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0516 | 3 Phase fault on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FORTNA (300554) 69.0 kV to 2SYRACS (300564) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0517 | 3 Phase fault on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FORTNA (300554) 69.0 kV to 2VERSAL (300565) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0518 | 3 Phase fault on 5GRAVOIB1 161.00 (300555) 161 kV Bus a. Apply fault at the 5GRAVOIB1 161.00 (300555) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRAVOIB1 (300555) 161.0 kV to 5GRAVOIB2 (300574) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0519 | 3 Phase fault on 2HIGHPT 69.000 (300556) 69 kV Bus a. Apply fault at the 2HIGHPT 69.000 (300556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HIGHPT (300556) 69.0 kV to 2BARNET (300618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0520 | 3 Phase fault on 2PILOTG 69.000 (300560) 69 kV Bus a. Apply fault at the 2PILOTG 69.000 (300560) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PILOTG (300560) 69.0 kV to 2PRARIE (300561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0521 | 3 Phase fault on 2VERSAL 69.000 (300565) 69 kV Bus a. Apply fault at the 2VERSAL 69.000 (300565) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERSAL (300565) 69.0 kV to 2BARNET (300618) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0522 | 3 Phase fault on 2BARNET 69.000 (300618) 69 kV Bus a. Apply fault at the 2BARNET 69.000 (300618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BARNET (300618) 69.0 kV to 2MTPLSTC (300633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0523 | 3 Phase fault on 2SCRUGG 69.000 (300637) 69 kV Bus a. Apply fault at the 2SCRUGG 69.000 (300637) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SCRUGG (300637) 69.0 kV to 2ST_MARTINS (301442) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0524 | 3 Phase fault on 2BLLMYTP 69.000 (300647) 69 kV Bus a. Apply fault at the 2BLLMYTP 69.000 (300647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLLMYTP (300647) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0525 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0526 | 3 Phase fault on 2LAMR 69.000 (300651) 69 kV Bus a. Apply fault at the 2LAMR 69.000 (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0527 | 3 Phase fault on 2LAMR 69.000 (300651) 69 kV Bus a. Apply fault at the 2LAMR 69.000 (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2LAMARPT (300685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0528 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0529 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0530 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0531 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0532 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0533 | 3 Phase fault on 2MIAETP 69.000 (300852) 69 kV Bus a. Apply fault at the 2MIAETP 69.000 (300852) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MIAETP (300852) 69.0 kV to 2MIAENEO (301461) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0534 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0535 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0536 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0537 | 3 Phase fault on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PLATCTY (301552) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0538 | 3 Phase fault on 5REBEL 161.00 (343007) 161 kV Bus a. Apply fault at the 5REBEL 161.00 (343007) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REBEL (343007) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0539 | 3 Phase fault on 2APCH FLT 69.000 (344027) 69 kV Bus a. Apply fault at the 2APCH FLT 69.000 (344027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2APCH FLT (344027) 69.0 kV to 2JC RAINB (346082) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0540 | 3 Phase fault on 2APCH FLT 69.000 (344027) 69 kV Bus a. Apply fault at the 2APCH FLT 69.000 (344027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2APCH FLT (344027) 69.0 kV to 2JC SCRGG (346084) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0541 | 3 Phase fault on 5APCH FLT 161.00 (344028) 161 kV Bus a. Apply fault at the 5APCH FLT 161.00 (344028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0542 | 3 Phase fault on 5JC ZION TP 161.00 (344815) 161 kV Bus a. Apply fault at the 5JC ZION TP 161.00 (344815) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JC ZION TP (344815) 161.0 kV to 5MARIOSA (345027) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0543 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0544 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0545 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2MACON_AM (346096) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0546 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2DUPONT (346169) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0547 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2ROTH TAP (346170) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0548 | 3 Phase fault on 2MOBERLY 69.000 (345222) 69 kV Bus a. Apply fault at the 2MOBERLY 69.000 (345222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 2SPRK TAP (346171) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0549 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0550 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0551 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to KERR BRK1 5 (512770) 161.0 kV Transmission Circuit #z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0552 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to KERR BRK4 5 (512771) 161.0 kV Transmission Circuit #z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0553 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0554 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to G21-047-TAP (765721) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0555 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0556 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0557 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0558 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0559 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0560 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0561 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0562 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0563 | 3 Phase fault on N HAYS3 115.00 (530581) 115 kV Bus a. Apply fault at the N HAYS3 115.00 (530581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0564 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0565 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0566 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0567 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0568 | 3 Phase fault on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0569 | 3 Phase fault on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0570 | 3 Phase fault on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0571 | 3 Phase fault on VINETAP3 115.00 (530693) 115 kV Bus a. Apply fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0572 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINEDE_S (530722) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0573 | 3 Phase fault on GEM_SW 3 115.00 (530713) 115 kV Bus a. Apply fault at the GEM_SW 3 115.00 (530713) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEM_SW 3 (530713) 115.0 kV to COLBY_PUMP3 (530716) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0574 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0575 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0576 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0577 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0578 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0579 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0580 | 3 Phase fault on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0581 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0582 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0583 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0584 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0585 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0586 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0587 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0588 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0589 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0590 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0591 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips WAVERGEN (532957). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0592 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0593 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0594 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0595 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0596 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0597 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to TCBURNS4 (532994) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0598 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0599 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0600 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0601 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0602 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0603 | 3 Phase fault on CENTENN4 138.00 (533034) 138 kV Bus a. Apply fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0604 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0605 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G17-068 (589063). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0606 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G17-068 (589063). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0607 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0608 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0609 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0610 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0611 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0612 | 3 Phase fault on WACO S 4 138.00 (533071) 138 kV Bus a. Apply fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0613 | 3 Phase fault on WACO 4 138.00 (533072) 138 kV Bus a. Apply fault at the WACO 4 138.00 (533072) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0614 | 3 Phase fault on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0615 | 3 Phase fault on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0616 | 3 Phase fault on LANG 3 115.00 (533304) 115 kV Bus a. Apply fault at the LANG 3 115.00 (533304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0617 | 3 Phase fault on READING3 115.00 (533306) 115 kV Bus a. Apply fault at the READING3 115.00 (533306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. READING3 (533306) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0618 | 3 Phase fault on FLORENC3 115.00 (533366) 115 kV Bus a. Apply fault at the FLORENC3 115.00 (533366) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0619 | 3 Phase fault on SPRGCRK3 115.00 (533380) 115 kV Bus a. Apply fault at the SPRGCRK3 115.00 (533380) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0620 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0621 | 3 Phase fault on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0622 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0623 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0624 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0625 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to BURLIND2 (533625) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0626 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to CC1BURL2 (533628) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0627 | 3 Phase fault on ALTAMNT2 69.000 (533671) 69 kV Bus a. Apply fault at the ALTAMNT2 69.000 (533671) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0628 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODESH2 (533699) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0629 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0630 | 3 Phase fault on YELLOWJ2 69.000 (533692) 69 kV Bus a. Apply fault at the YELLOWJ2 69.000 (533692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YELLOWJ2 (533692) 69.0 kV to NEW ALB2 (533701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0631 | 3 Phase fault on LABETTE2 69.000 (533695) 69 kV Bus a. Apply fault at the LABETTE2 69.000 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0632 | 3 Phase fault on NEODJCT2 69.000 (533700) 69 kV Bus a. Apply fault at the NEODJCT2 69.000 (533700) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEODJCT2 (533700) 69.0 kV to RA6BROO2 (533707) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0633 | 3 Phase fault on NEW ALB2 69.000 (533701) 69 kV Bus a. Apply fault at the NEW ALB2 69.000 (533701) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEW ALB2 (533701) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0634 | 3 Phase fault on ORDNCE 2 69.000 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 69.000 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0635 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0636 | 3 Phase fault on CANALS 2 69.000 (533784) 69 kV Bus a. Apply fault at the CANALS 2 69.000 (533784) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0637 | 3 Phase fault on CANALS 2 69.000 (533784) 69 kV Bus a. Apply fault at the CANALS 2 69.000 (533784) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0638 | 3 Phase fault on CHENEY 2 69.000 (533785) 69 kV Bus a. Apply fault at the CHENEY 2 69.000 (533785) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHENEY 2 (533785) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0639 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0640 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCAN 2 (533850) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0641 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0642 | 3 Phase fault on GLENDAL2 69.000 (533797) 69 kV Bus a. Apply fault at the GLENDAL2 69.000 (533797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL2 (533797) 69.0 kV to OLIVER 2 (533826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0643 | 3 Phase fault on GLENDAL2 69.000 (533797) 69 kV Bus a. Apply fault at the GLENDAL2 69.000 (533797) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDAL2 (533797) 69.0 kV to RUTAN 2 (533838) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0644 | 3 Phase fault on HAYSV 2 69.000 (533803) 69 kV Bus a. Apply fault at the HAYSV 2 69.000 (533803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYSV 2 (533803) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0645 | 3 Phase fault on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0646 | 3 Phase fault on HOOVERS2 69.000 (533806) 69 kV Bus a. Apply fault at the HOOVERS2 69.000 (533806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0647 | 3 Phase fault on LIN 2 69.000 (533812) 69 kV Bus a. Apply fault at the LIN 2 69.000 (533812) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0648 | 3 Phase fault on OAKLAWN2 69.000 (533824) 69 kV Bus a. Apply fault at the OAKLAWN2 69.000 (533824) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAWN2 (533824) 69.0 kV to OLIVER 2 (533826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0649 | 3 Phase fault on PLAZA E2 69.000 (533829) 69 kV Bus a. Apply fault at the PLAZA E2 69.000 (533829) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0650 | 3 Phase fault on RIPLEYW2 69.000 (533832) 69 kV Bus a. Apply fault at the RIPLEYW2 69.000 (533832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIPLEYW2 (533832) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0651 | 3 Phase fault on GALE TP2 69.000 (533845) 69 kV Bus a. Apply fault at the GALE TP2 69.000 (533845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALE TP2 (533845) 69.0 kV to SG4ANDL2 (533872) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0652 | 3 Phase fault on GALE TP2 69.000 (533845) 69 kV Bus a. Apply fault at the GALE TP2 69.000 (533845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALE TP2 (533845) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0653 | 3 Phase fault on PLAZA M2 69.000 (533857) 69 kV Bus a. Apply fault at the PLAZA M2 69.000 (533857) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0654 | 3 Phase fault on GODDTAP2 69.000 (533879) 69 kV Bus a. Apply fault at the GODDTAP2 69.000 (533879) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GODDTAP2 (533879) 69.0 kV to GODDARD2 (533880) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0655 | 3 Phase fault on RAGO 4 138.00 (539000) 138 kV Bus a. Apply fault at the RAGO 4 138.00 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0656 | 3 Phase fault on NW-DGTP3 115.00 (539628) 115 kV Bus a. Apply fault at the NW-DGTP3 115.00 (539628) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW-DGTP3 (539628) 115.0 kV to W-DODGE3 (539699) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0657 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0658 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0659 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0660 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0661 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0662 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0663 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0664 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G11-008 (539858), G19-058 (763895) and G19-063 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0665 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G11-008 (539858), G19-058 (763895) and G19-063 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0666 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G11-008 (539858) and G19-063 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0667 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0668 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0669 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0670 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0671 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0672 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0673 | 3 Phase fault on WBURGE_CAP5 161.00 (541148) 161 kV Bus a. Apply fault at the WBURGE_CAP5 161.00 (541148) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE_CAP5 (541148) 161.0 kV to WBURGE 5 (541228) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0674 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0675 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0676 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0677 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0678 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0679 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0680 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0681 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0682 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0683 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0684 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0685 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0686 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0687 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0688 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0689 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0690 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to POPE (541349) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0691 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0692 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0693 | 3 Phase fault on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0694 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0695 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0696 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0697 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0698 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0699 | 3 Phase fault on KCI 5 161.00 (541212) 161 kV Bus a. Apply fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCI 5 (541212) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0700 | 3 Phase fault on KCI 5 161.00 (541212) 161 kV Bus a. Apply fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCI 5 (541212) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0701 | 3 Phase fault on FRLVW 5 161.00 (541213) 161 kV Bus a. Apply fault at the FRLVW 5 161.00 (541213) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRLVW 5 (541213) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0702 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0703 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0704 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0705 | 3 Phase fault on RAYTOWN5 161.00 (541219) 161 kV Bus a. Apply fault at the RAYTOWN5 161.00 (541219) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0706 | 3 Phase fault on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0707 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0708 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0709 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0710 | 3 Phase fault on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 5 (541229) 161.0 kV to LEX161 5 (541232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0711 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0712 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0713 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0714 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0715 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0716 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0717 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0718 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0719 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0720 | 3 Phase fault on EAST 5 161.00 (541254) 161 kV Bus a. Apply fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0721 | 3 Phase fault on IND PRK5 161.00 (541256) 161 kV Bus a. Apply fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0722 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0723 | 3 Phase fault on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY2 (541262) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0724 | 3 Phase fault on KNOSTER2 69.000 (541270) 69 kV Bus a. Apply fault at the KNOSTER2 69.000 (541270) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOSTER2 (541270) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0725 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to KELHYS 2 (541273) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0726 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0727 | 3 Phase fault on SEDS 2 69.000 (541272) 69 kV Bus a. Apply fault at the SEDS 2 69.000 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0728 | 3 Phase fault on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0729 | 3 Phase fault on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0730 | 3 Phase fault on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0731 | 3 Phase fault on COLECMP2 69.000 (541276) 69 kV Bus a. Apply fault at the COLECMP2 69.000 (541276) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLECMP2 (541276) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0732 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0733 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0734 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0735 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBW5 (541336) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0736 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0737 | 3 Phase fault on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161.0 kV to WAFBE5 (541338) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0738 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0739 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0740 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0741 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0742 | 3 Phase fault on IATAN5 161.00 (541350) 161 kV Bus a. Apply fault at the IATAN5 161.00 (541350) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0743 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0744 | 3 Phase fault on MONSERTP 69.000 (541524) 69 kV Bus a. Apply fault at the MONSERTP 69.000 (541524) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONSERTP (541524) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0745 | 3 Phase fault on KNOSTERTP 69.000 (541534) 69 kV Bus a. Apply fault at the KNOSTERTP 69.000 (541534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOSTERTP (541534) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0746 | 3 Phase fault on LAMONTETP 69.000 (541535) 69 kV Bus a. Apply fault at the LAMONTETP 69.000 (541535) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMONTETP (541535) 69.0 kV to LAMONTE (541536) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0747 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0748 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0749 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0750 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY_CAP 5 (542944) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0751 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0752 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0753 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0754 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0755 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0756 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0757 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0758 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0759 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0760 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0761 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0762 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0763 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0764 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0765 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0766 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0767 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0768 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0769 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0770 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0771 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0772 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0773 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0774 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0775 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0776 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0777 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0778 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0779 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 4.75 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 4.75 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0780 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0781 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0782 | 3 Phase fault on TROOST 5 161.00 (542986) 161 kV Bus a. Apply fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0783 | 3 Phase fault on TROOST 5 161.00 (542986) 161 kV Bus a. Apply fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0784 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0785 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0786 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0787 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0788 | 3 Phase fault on CROSTWN5 161.00 (542990) 161 kV Bus a. Apply fault at the CROSTWN5 161.00 (542990) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSTWN5 (542990) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0789 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0790 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0791 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0792 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0793 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to ROEPARK5 (543040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0794 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0795 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0796 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0797 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0798 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0799 | 3 Phase fault on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0800 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0801 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0802 | 3 Phase fault on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0803 | 3 Phase fault on CLAYCM15 161.00 (543022) 161 kV Bus a. Apply fault at the CLAYCM15 161.00 (543022) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLAYCM15 (543022) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0804 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0805 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0806 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0807 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0808 | 3 Phase fault on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to ROEPARK5 (543040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0809 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0810 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0811 | 3 Phase fault on OXFORD 5 161.00 (543046) 161 kV Bus a. Apply fault at the OXFORD 5 161.00 (543046) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 5 (543046) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0812 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0813 | 3 Phase fault on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0814 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0815 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0816 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0817 | 3 Phase fault on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSTVAL5 (543077) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0818 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0819 | 3 Phase fault on SUGRCRK_N2 69.000 (543089) 69 kV Bus a. Apply fault at the SUGRCRK_N2 69.000 (543089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_N2 (543089) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0820 | 3 Phase fault on DUNCNRD2 69.000 (543091) 69 kV Bus a. Apply fault at the DUNCNRD2 69.000 (543091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0821 | 3 Phase fault on LIBRTYS2 69.000 (543095) 69 kV Bus a. Apply fault at the LIBRTYS2 69.000 (543095) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0822 | 3 Phase fault on SUGRCK_TP_W269.000 (543164) 69 kV Bus a. Apply fault at the SUGRCK_TP_W269.000 (543164) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0823 | 3 Phase fault on KAW 5 161.00 (546214) 161 kV Bus a. Apply fault at the KAW 5 161.00 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0824 | 3 Phase fault on KAW 5 161.00 (546214) 161 kV Bus a. Apply fault at the KAW 5 161.00 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0825 | 3 Phase fault on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to MILLST 5 (546224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0826 | 3 Phase fault on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0827 | 3 Phase fault on SCAM66 2 69.000 (547409) 69 kV Bus a. Apply fault at the SCAM66 2 69.000 (547409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCAM66 2 (547409) 69.0 kV to SCM66T 2 (547455) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0828 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0829 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to SEK225 2 (547413) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0830 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to SMN425 2 (547414) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0831 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to SHR444 2 (547415) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0832 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0833 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to CHE299 2 (547417) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0834 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to CHE300 2 (547418) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0835 | 3 Phase fault on CHE299T2 69.000 (547416) 69 kV Bus a. Apply fault at the CHE299T2 69.000 (547416) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE299T2 (547416) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0836 | 3 Phase fault on CHE300 2 69.000 (547418) 69 kV Bus a. Apply fault at the CHE300 2 69.000 (547418) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHE300 2 (547418) 69.0 kV to TWN388 2 (547419) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0837 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0838 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0839 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0840 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0841 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0842 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0843 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0844 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0845 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0846 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0847 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0848 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0849 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0850 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0851 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0852 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0853 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0854 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0855 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0856 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0857 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0858 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0859 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0860 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0861 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0862 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0863 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0864 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0865 | 3 Phase fault on GAT258 2 69.000 (547551) 69 kV Bus a. Apply fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0866 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0867 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0868 | 3 Phase fault on GAL278 2 69.000 (547555) 69 kV Bus a. Apply fault at the GAL278 2 69.000 (547555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAL278 2 (547555) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0869 | 3 Phase fault on COM381T2 69.000 (547579) 69 kV Bus a. Apply fault at the COM381T2 69.000 (547579) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COM381T2 (547579) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0870 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0871 | 3 Phase fault on JOP389 2 69.000 (547592) 69 kV Bus a. Apply fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0872 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0873 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0874 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0875 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0876 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0877 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0878 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0879 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0880 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0881 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0882 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0883 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 7 (640167) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0884 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0885 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0886 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0887 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0888 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0889 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0890 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0891 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0892 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0893 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0894 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0895 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0896 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0897 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0898 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0899 | 3 Phase fault on MALONEY7 115.00 (640265) 115 kV Bus a. Apply fault at the MALONEY7 115.00 (640265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0900 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0901 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0902 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0903 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0904 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0905 | 3 Phase fault on OGALALANPPD7115.00 (640304) 115 kV Bus a. Apply fault at the OGALALANPPD7115.00 (640304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA_-TS7 (659801) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0906 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0907 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0908 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0909 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0910 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0911 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | The Grand Prairie Wind Units (645065, 645066, 645067 and 645068) become unstable following the fault clearance and protection trips the units. Reducing the critical clearing time to 3.0 cycles mitigates the issue. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0912 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0913 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0914 | 3 Phase fault on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-053 (763849). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0915 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT11_2 (543663) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0916 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT12_2 (543664) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0917 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5KINGDMB1 (300090) 161.0 kV to 7KINGDM (300043) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0918 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0919 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF3 (301506) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0920 | 3 Phase fault on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0921 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BARNET (300618) 69.0 kV to 5BARNET (300057) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0922 | 3 Phase fault on 5BOONE 161.00 (300061) 161 kV Bus a. Apply fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BOONE (300493) 69.0 kV to 5BOONE (300061) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0923 | 3 Phase fault on 5CALIF 161.00 (300063) 161 kV Bus a. Apply fault at the 5CALIF 161.00 (300063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CALIF (300550) 69.0 kV to 5CALIF (300063) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0924 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLARK (300802) 69.0 kV to 5CLARK (300070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0925 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0926 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0927 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0928 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHRP (300302) 69.0 kV to 5LATHRP (300091) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0929 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0930 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0931 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0932 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0933 | 3 Phase fault on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PLATCTY (300307) 69.0 kV to 5PLATCTY (301552) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0934 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0935 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0936 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0937 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0938 | 3 Phase fault on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PERCHE (343004) 161.0 kV to 2PERCHE (343005) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0939 | 3 Phase fault on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PERCHE (343004) 161.0 kV to 2PERCHE2 (343052) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0940 | 3 Phase fault on 5GRINDSTN 161.00 (343014) 161 kV Bus a. Apply fault at the 5GRINDSTN 161.00 (343014) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GRINDSTN (343006) 69.0 kV to 5GRINDSTN (343014) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0941 | 3 Phase fault on 5APCH FLT 161.00 (344028) 161 kV Bus a. Apply fault at the 5APCH FLT 161.00 (344028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0942 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0943 | 3 Phase fault on 5LATHROP 161.00 (344923) 161 kV Bus a. Apply fault at the 5LATHROP 161.00 (344923) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHROP (346093) 69.0 kV to 5LATHROP (344923) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0944 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0945 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0946 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0947 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0948 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0949 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0950 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0951 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to CATOOSA4 (509790) 138.0 kV to CATTER1 1 (512833) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0952 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to CATOOSA4 (509790) 138.0 kV to CATTER2 1 (512834) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0953 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0954 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0955 | 3 Phase fault on PENSA 5 161.00 (512654) 161 kV Bus a. Apply fault at the PENSA 5 161.00 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to PENSA 2 (512628) 69.0 kV to PENSA 1 (512841) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0956 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0957 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0958 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0959 | 3 Phase fault on WAKTASW4 138.00 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 138.00 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 (520434) 138.0 kV to WAKITA 2 (521085) 69.0 kV to WAKITA_13.8 (520435) 13.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0960 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0961 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0962 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0963 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0964 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0965 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0966 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0967 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0968 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0969 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0970 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0971 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0972 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0973 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0974 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0975 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0976 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0977 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 2X1 (532840) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0978 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0979 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0980 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0981 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0982 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0983 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0984 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0985 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0986 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0987 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0988 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0989 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0990 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0991 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0992 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0993 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MCDOWEL3 (533335) 115.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0994 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0995 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0996 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0997 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0998 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_0999 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1000 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1001 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1002 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1003 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1004 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1005 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1006 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1007 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1008 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1009 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1010 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1011 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1012 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1013 | 3 Phase fault on 17TH 4 138.00 (533064) 138 kV Bus a. Apply fault at the 17TH 4 138.00 (533064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1014 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1015 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1016 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1017 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1018 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1019 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1020 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1021 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1022 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1023 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1024 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1025 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN2 (533876) 69.0 kV to FRANKLIN5 (532938) 161.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1026 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1027 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1028 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1029 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1030 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1031 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1032 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1033 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1034 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1035 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1036 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1037 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 2 (541269) 69.0 kV to WBURGE 5 (541228) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1038 | 3 Phase fault on ODESSA 5 161.00 (541229) 161 kV Bus a. Apply fault at the ODESSA 5 161.00 (541229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ODESSA 2 (541267) 69.0 kV to ODESSA 5 (541229) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1039 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1040 | 3 Phase fault on LEX161 5 161.00 (541232) 161 kV Bus a. Apply fault at the LEX161 5 161.00 (541232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX69 2 (541264) 69.0 kV to LEX161 5 (541232) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1041 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1042 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1043 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1044 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to LBRTYST5 (541248) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1045 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1046 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1047 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1048 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1049 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to ATLNTIC3 (533279) 115.0 kV to ATLNT2X1 (533916) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1050 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to ATLNTIC3 (533279) 115.0 kV to ATLNT1X1 (533915) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1051 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1052 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1053 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1054 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1055 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1056 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1057 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1058 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1059 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1060 | 3 Phase fault on IATAN 7 345.00 (542982) 345 kV Bus a. Apply fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1061 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1062 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1063 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1064 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1065 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1066 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1067 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1068 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1069 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1070 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1071 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1072 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1073 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1074 | 3 Phase fault on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1075 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG8 (640101) 69.0 kV to CAMBRIG7 (640100) 115.0 kV to CAMBRIDGET19 (643028) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1076 | 3 Phase fault on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENDERS 8 (640168) 69.0 kV to ENDERS 7 (640167) 115.0 kV to ENDERS T1 9 (643055) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1077 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1078 | 3 Phase fault on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1079 | 3 Phase fault on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT8 (640288) 69.0 kV to N.PLATT7 (640287) 115.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1080 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1081 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1082 | 3 Phase fault on VSC2_3 345.00 (992003) 345 kV Bus a. Apply fault at the VSC2_3 345.00 (992003) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VSC2_3 (992003) 345.0 kV to VSC2_2 (992002) 276.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1083 | 3 Phase fault on VSC2_3 345.00 (992003) 345 kV Bus a. Apply fault at the VSC2_3 345.00 (992003) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VSC2_3 (992003) 345.0 kV to VSC2_6 (992006) 276.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1084 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1085 | 3 Phase fault on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1086 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1087 | 3 Phase fault on JOP430 2 69.000 (547608) 69 kV Bus a. Apply fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP430 2 (547608) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1088 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1089 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1090 | 3 Phase fault on SUB M 69.000 (548815) 69 kV Bus a. Apply fault at the SUB M 69.000 (548815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1091 | 3 Phase fault on SUB N 69.000 (548821) 69 kV Bus a. Apply fault at the SUB N 69.000 (548821) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1092 | 3 Phase fault on SUB C 69.000 (548825) 69 kV Bus a. Apply fault at the SUB C 69.000 (548825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB C (548825) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT_1093 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0001 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0002 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0003 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0004 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0005 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0006 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0007 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0008 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0009 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0010 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0011 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0013 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0014 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0015 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0016 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0017 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0018 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0019 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0020 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0021 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0022 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0023 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0024 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0025 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0026 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0027 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0028 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0029 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips WAVERGEN (532957). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0030 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G11-008 (539858), G19-058 (763895) and G19-063 (763926). | Protection disabled with no impact to stability.
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0031 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0032 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0033 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0035 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0036 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0037 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0038 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0039 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0040 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0041 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0042 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0043 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0044 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0045 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0046 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0047 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0048 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0049 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0050 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT_0051 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0001 | Single Phase Fault with Stuck Breaker on 5GRINDSTN 161.00 (343014) 161 kV Bus a. Apply Fault at the 5GRINDSTN 161.00 (343014) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BOONE (300061) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 b.2. 2GRINDSTN (343006) 69.0 kV to 5GRINDSTN (343014) 161.0 kV Two Winding #1 b.3. 5REBEL (343007) 161.0 kV to 5GRINDSTN (343014) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0002 | Single Phase Fault with Stuck Breaker on 5PERCHE 161.00 (343004) 161 kV Bus a. Apply Fault at the 5PERCHE 161.00 (343004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5PERCHE (343004) 161.0 kV Transmission Circuit #1 b.2. 5PERCHE (343004) 161.0 kV to 2PERCHE (343005) 69.0 kV Two Winding #1 b.3. 5PERCHE (343004) 161.0 kV to 2PERCHE2 (343052) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0003 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0007 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0008 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0010 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 b.2. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 b.3. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0011 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0012 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0013 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0014 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0015 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0016 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-100-TAP (768980) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0017 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0018 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0019 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0020 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0021 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0022 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0023 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0024 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0025 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0026 | Single Phase Fault with Stuck Breaker on BLSPE 5 161.00 (541205) 161 kV Bus a. Apply Fault at the BLSPE 5 161.00 (541205) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 b.3. BLSPE 5 (541205) 161.0 kV to DUNCAN 5 (541235) 161.0 kV Transmission Circuit #1 b.4. BLSPE 5 (541205) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 b.5. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0027 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-100-TAP (768980) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0028 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0029 | Single Phase Fault with Stuck Breaker on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply Fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.3. SALSBRY5 (543062) 161.0 kV to Load #1 b.4. SALSBRY5 (543062) 161.0 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0030 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0031 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0032 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0033 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0034 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0035 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NEAST_DG1 (543160) 4.2 kV to NE CT11 (542958) 13.8 kV Two Winding #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 b.6. NEASTN5 (543666) 161.0 kV to Load #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0036 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEAST_DG1 (543160) 4.2 kV to NE CT11 (542958) 13.8 kV Two Winding #1 b.3. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0037 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # b.6. NEASTN5 (543666) 161.0 kV to Load #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0038 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NE CT17 (542983) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT18 (542984) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0039 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NE CT17 (542983) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT18 (542984) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0040 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0041 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0042 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0043 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 b.2. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0044 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0045 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0046 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0047 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0048 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0049 | Single Phase Fault with Stuck Breaker on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply Fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT7 1 (542963) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.2. HAWCT8 1 (542964) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.3. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0050 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to Load #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0051 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NRTHST_B90_1 (543082) 13.8 kV to Load #90 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0052 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NRTHST_B34_1 (543081) 13.8 kV to Load #34 b.3. NEASTN5 (543666) 161.0 kV to Load #78 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0053 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NRTHST_B34_1 (543081) 13.8 kV to Load #34 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0054 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # b.2. NEASTN5 (543666) 161.0 kV to Load #78 b.3. NRTHST_B90_1 (543082) 13.8 kV to Load #90 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0055 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0056 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0057 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0058 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0059 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.4. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0060 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0061 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0062 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0063 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0064 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0065 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0066 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0067 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0068 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 b.2. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0069 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0070 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0071 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0072 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0073 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0074 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0075 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0076 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0077 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0078 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0079 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0080 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0081 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0082 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0083 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0084 | Single Phase Fault with Stuck Breaker on COLBY 3 115.00 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0085 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.3. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0086 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 b.2. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 b.4. BEVERLY7 (640082) 115.0 kV to BEVERLY8 (640083) 69.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0087 | Single Phase Fault with Stuck Breaker on ENDERS 7 115.00 (640167) 115 kV Bus a. Apply Fault at the ENDERS 7 115.00 (640167) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 b.2. ENDERS 7 (640167) 115.0 kV to ATHEY 7 (641244) 115.0 kV Transmission Circuit #1 b.3. ENDERS 7 (640167) 115.0 kV to GRANTNB_-TS7 (659800) 115.0 kV Transmission Circuit #1 b.4. ENDERS 7 (640167) 115.0 kV to ENDERS 8 (640168) 69.0 kV to ENDERS T1 9 (643055) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0088 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to MCCOOK G (640017) 13.8 kV Two Winding #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.4. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.5. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 b.6. MCCOOK 7 (640269) 115.0 kV to MCCOOK 8 (640270) 69.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0089 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.3. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #2 b.4. REDWILO7 (640326) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.5. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0090 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.3. N.PLATTG (640018) 13.8 kV to N.PLATT9 (640289) 34.5 kV to N.PLATT7 (640287) 115.0 kV Three Winding #1 b.4. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 b.6. N.PLATT7 (640287) 115.0 kV to N.PLATT8 (640288) 69.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 b.7. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to N.PLATTG (640018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0091 | Single Phase Fault with Stuck Breaker on N.PLATT7 115.00 (640287) 115 kV Bus a. Apply Fault at the N.PLATT7 115.00 (640287) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. MALONEY7 (640265) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.3. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.4. N.PLATT7 (640287) 115.0 kV to STOCKVL7 (640365) 115.0 kV Transmission Circuit #1 b.5. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 b.6. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 b.7. N.PLATT7 (640287) 115.0 kV to N.PLATT8 (640288) 69.0 kV to NORTHPLT T29 (643106) 13.8 kV Three Winding #1 b.8. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to N.PLATTG (640018) 13.8 kV Three Winding #1 b.9. N.PLATT7 (640287) 115.0 kV to N.PLATT9 (640289) 34.5 kV to NORTHPLT T79 (643107) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0092 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 b.3. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0093 | Single Phase Fault with Stuck Breaker on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply Fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.6. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.7. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.8. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.9. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 b.10. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.11. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.12. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.13. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.14. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0094 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.4. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.7. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.8. HARPER 4 (539668) 138.0 kV to HARPER 1 (539713) 34.5 kV to HARPER-T (539913) 8.7 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0095 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0096 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0097 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0098 | Single Phase Fault with Stuck Breaker on SPRVILL-EHVB230.00 (539117) 230 kV Bus a. Apply Fault at the SPRVILL-EHVB230.00 (539117) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.3. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.4. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.8. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0099 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0100 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.2. SPRVILL-EHVB (539117) 230.0 kV to SPRVILL-EHV2 (539132) 230.0 kV Transmission Circuit #1 b.3. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.4. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.6. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.9. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHV2 (539132) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0101 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERTER1 (531468) 13.8 kV to SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV Three Winding #1 b.2. SPERVIL7 (531469) 345.0 kV to SPEARVL6 (539695) 230.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.3. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0102 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 b.4. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0103 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0104 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0105 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0106 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0107 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0108 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0109 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0110 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 1 (531259) 13.8 kV to SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0111 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0112 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0113 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-065-TAP (768280) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0114 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0115 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0116 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0117 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCGEN1 (531447) 22.0 kV to HOLCOMB3 (531448) 115.0 kV Two Winding #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 b.5. HOLCOMB3 (531448) 115.0 kV to Load #S1 b.6. HOLCOMB3 (531448) 115.0 kV to Load #S2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0118 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0119 | Single Phase Fault with Stuck Breaker on FTDODGE3 115.00 (539671) 115 kV Bus a. Apply Fault at the FTDODGE3 115.00 (539671) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DCBEEF3 (539645) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #1 b.2. DCBEEF3 (539645) 115.0 kV to EDODGE 3 (539740) 115.0 kV Transmission Circuit #1 b.3. FTDODGP1 (539670) 15.0 kV to FTDODGE3 (539671) 115.0 kV Two Winding #1 b.4. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.5. FTDODGE3 (539671) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #2 b.6. FTDODGE3 (539671) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.7. FTDODGE3 (539671) 115.0 kV to FTDDGDV1 (539715) 34.5 kV to FTDODG-T (539915) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0120 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0121 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.2. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0122 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0123 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0124 | Single Phase Fault with Stuck Breaker on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply Fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GRTBENDT (539921) 7.2 kV to GRTBEND1 (539719) 34.5 kV to GRTBEND3 (539678) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0125 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.4. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0126 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0127 | Single Phase Fault with Stuck Breaker on SPRINGH3 115.00 (533267) 115 kV Bus a. Apply Fault at the SPRINGH3 115.00 (533267) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.4. SPRINGH3 (533267) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0128 | Single Phase Fault with Stuck Breaker on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply Fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.3. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.4. SPRINGH3 (533267) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0129 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 b.4. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 2X1 (532840) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0130 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0131 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0132 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0133 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0134 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0135 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC6 1 (532743) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0136 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0137 | Single Phase Fault with Stuck Breaker on GEARY 7 345.00 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.3. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0138 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.3. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0139 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0140 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0141 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0142 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0143 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0144 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0145 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0146 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0147 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0148 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0149 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0150 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0151 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0152 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0153 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0154 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0155 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0156 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0157 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to GEN-2016-174 (588250) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0158 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0159 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0160 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0161 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0162 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0163 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0164 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0165 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0166 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0167 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0168 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0169 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. BLUMILS5 (543004) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0170 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0171 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.3. BLUEMLS2 (543116) 69.0 kV to BLUMILS5 (543004) 161.0 kV to BLUMILS_TER1 (543117) 12.5 kV Three Winding #3 b.4. BLUMILS_TER1 (543117) 12.5 kV to BLUMILS5 (543004) 161.0 kV to BLUEMLS2 (543116) 69.0 kV Three Winding #3 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0172 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY (548806) 69.0 kV to Load #T2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0173 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0174 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0175 | Single Phase Fault with Stuck Breaker on BLUVLY 69.000 (548806) 69 kV Bus a. Apply Fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.3. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.4. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 b.5. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 b.6. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 b.7. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 b.8. BLUVLY (548806) 69.0 kV to Load #T1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0176 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.3. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0177 | Single Phase Fault with Stuck Breaker on SUB N-161 161.00 (548820) 161 kV Bus a. Apply Fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0178 | Single Phase Fault with Stuck Breaker on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply Fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 b.2. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0179 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0180 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0181 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0182 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0183 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0184 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0185 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0186 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0187 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0188 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0189 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0190 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0191 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0192 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0193 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0194 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0195 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0196 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP5 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0197 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0198 | Single Phase Fault with Stuck Breaker on AFTON 5 161.00 (512632) 161 kV Bus a. Apply Fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.4. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0199 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.2. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.3. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0200 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.2. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.3. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.6. 1CHOTCT2 (300033) 16.0 kV to Load #P2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0201 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.2. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.3. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0202 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 1CHOTST3 (300031) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #10 b.5. 1CHOTCT1 (300032) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #11 b.6. 1CHOTCT2 (300033) 16.0 kV to 5CHOTEAU1 (300069) 161.0 kV Two Winding #12 b.7. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.8. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.9. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0203 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0204 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.6. 1CHOTCT4 (300020) 16.0 kV to Load #P1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0205 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 1CHOTCT4 (300020) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #21 b.2. 1CHOTCT5 (300021) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #22 b.3. 1CHOTST6 (300024) 16.0 kV to 5CHOTEAU2 (301348) 161.0 kV Two Winding #20 b.4. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 b.5. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.6. 1CHOTCT5 (300021) 16.0 kV to Load #P2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0206 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.3. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.4. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0207 | Single Phase Fault with Stuck Breaker on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply Fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.5. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0208 | Single Phase Fault with Stuck Breaker on 5APCH FLT 161.00 (344028) 161 kV Bus a. Apply Fault at the 5APCH FLT 161.00 (344028) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.2. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.4. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.5. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0209 | Single Phase Fault with Stuck Breaker on 5BARNET 161.00 (300057) 161 kV Bus a. Apply Fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.3. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.4. 2BARNET (300618) 69.0 kV to 5BARNET (300057) 161.0 kV Two Winding #1 b.5. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.6. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0210 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 161.00 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 161.00 (344234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5CALIF (300063) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.4. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.5. 1CALIF (346027) 34.5 kV to 5CALIF UE 2 (344234) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0211 | Single Phase Fault with Stuck Breaker on 5JC ZION 161.00 (344814) 161 kV Bus a. Apply Fault at the 5JC ZION 161.00 (344814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.2. 5MARIOSA (345027) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.3. 5JC ZION (344814) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #z b.4. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.5. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.6. 2JC ZION (346089) 69.0 kV to 5JC ZION (344814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0212 | Single Phase Fault with Stuck Breaker on 5ELDON 2 161.00 (344533) 161 kV Bus a. Apply Fault at the 5ELDON 2 161.00 (344533) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.3. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.4. 2BARNET (300618) 69.0 kV to 5BARNET (300057) 161.0 kV Two Winding #1 b.5. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.6. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.7. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.8. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 b.9. 1ELDON 2 (346045) 34.5 kV to 5ELDON 2 (344533) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0213 | Single Phase Fault with Stuck Breaker on 5ELDON 2 161.00 (344533) 161 kV Bus a. Apply Fault at the 5ELDON 2 161.00 (344533) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.2. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.3. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.4. 4OSAGE (345400) 138.0 kV to 4OSG_1&2TAP (345401) 138.0 kV Transmission Circuit #z b.5. 4OSAGE (345400) 138.0 kV to 4OSG_5&6TAP (345406) 138.0 kV Transmission Circuit #1 b.6. 4OSAGE (345400) 138.0 kV to 4OSG_7&8TAP (345407) 138.0 kV Transmission Circuit #1 b.7. 4OSAGE (345400) 138.0 kV to 1OSAGE (346116) 34.5 kV Two Winding #1 b.8. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.9. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 b.10. 1ELDON 2 (346045) 34.5 kV to 5ELDON 2 (344533) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0214 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 161.00 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 161.00 (344234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CALIF (300063) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.2. 2CALIF (300550) 69.0 kV to 5CALIF (300063) 161.0 kV Two Winding #2 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.4. 5CALIF UE 1 (344233) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #z b.5. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.6. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 b.7. 1CALIF (346027) 34.5 kV to 5CALIF UE 2 (344234) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0215 | Single Phase Fault with Stuck Breaker on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply Fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0216 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.4. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.5. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0217 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0218 | Single Phase Fault with Stuck Breaker on RIV167 5 161.00 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0219 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0220 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 b.3. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.4. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0221 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0222 | Single Phase Fault with Stuck Breaker on FIR417 5 161.00 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 161.00 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0223 | Single Phase Fault with Stuck Breaker on OAK432 5 161.00 (547494) 161 kV Bus a. Apply Fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0224 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. OAK432 5 (547494) 161.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0225 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0226 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0227 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0228 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0229 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0230 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0231 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0232 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0233 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0234 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0235 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0236 | Single Phase Fault with Stuck Breaker on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply Fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.2. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.6. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z b.7. 5OVERTON (345409) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #1 b.8. 5OVERTON 2 (345411) 161.0 kV to 2OVERTON (346117) 69.0 kV Two Winding #2 b.9. 5OVERTON 2 (345411) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0237 | Single Phase Fault with Stuck Breaker on 5APCH TP 161.00 (344026) 161 kV Bus a. Apply Fault at the 5APCH TP 161.00 (344026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5APCH TP (344026) 161.0 kV Transmission Circuit #1 b.2. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.3. 5APCH TP (344026) 161.0 kV to 5CALIF UE 2 (344234) 161.0 kV Transmission Circuit #1 b.4. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.5. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0238 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0239 | Single Phase Fault with Stuck Breaker on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply Fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5LOYMART 1 (344040) 161.0 kV to 5LOYMART 2 (344041) 161.0 kV Transmission Circuit #z b.3. 5LOYMART 1 (344040) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.4. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.5. 5J994 SUB (344656) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.6. 5GUTHRIE 1 (344677) 161.0 kV to 5GUTHRIE 2 (344678) 161.0 kV Transmission Circuit #z b.7. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.8. 1LOYMART 1 (346010) 12.5 kV to 5LOYMART 1 (344040) 161.0 kV Two Winding #1 b.9. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0240 | Single Phase Fault with Stuck Breaker on 5ELDON 2 161.00 (344533) 161 kV Bus a. Apply Fault at the 5ELDON 2 161.00 (344533) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BARNET (300057) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #1 b.2. 5ELDON 1 (344532) 161.0 kV to 5ELDON 2 (344533) 161.0 kV Transmission Circuit #z b.3. 5ELDON 1 (344532) 161.0 kV to 5OSAGE (345402) 161.0 kV Transmission Circuit #1 b.4. 4OSAGE (345400) 138.0 kV to 4OSG_1&2TAP (345401) 138.0 kV Transmission Circuit #z b.5. 4OSAGE (345400) 138.0 kV to 4OSG_3&4TAP (345404) 138.0 kV Transmission Circuit #z b.6. 4OSAGE (345400) 138.0 kV to 4OSG_5&6TAP (345406) 138.0 kV Transmission Circuit #1 b.7. 4OSAGE (345400) 138.0 kV to 4OSG_7&8TAP (345407) 138.0 kV Transmission Circuit #1 b.8. 4OSAGE (345400) 138.0 kV to 1OSAGE (346116) 34.5 kV Two Winding #1 b.9. 4OSAGE (345400) 138.0 kV to 1OSAGE (346116) 34.5 kV Two Winding #2 b.10. 5OSAGE (345402) 161.0 kV to 4OSAGE (345400) 138.0 kV Two Winding #1 b.11. 1ELDON 1 (346044) 34.5 kV to 5ELDON 1 (344532) 161.0 kV Two Winding #1 b.12. 1ELDON 2 (346045) 34.5 kV to 5ELDON 2 (344533) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0241 | Single Phase Fault with Stuck Breaker on 5GUTHRIE 1 161.00 (344677) 161 kV Bus a. Apply Fault at the 5GUTHRIE 1 161.00 (344677) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LOYMART 1 (344040) 161.0 kV to 5LOYMART 2 (344041) 161.0 kV Transmission Circuit #z b.2. 5LOYMART 1 (344040) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.3. 5J994 SUB (344656) 161.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Transmission Circuit #1 b.4. 5GUTHRIE 1 (344677) 161.0 kV to 5GUTHRIE 2 (344678) 161.0 kV Transmission Circuit #z b.5. 5GUTHRIE 2 (344678) 161.0 kV to 5MONTGMRY 1 (345231) 161.0 kV Transmission Circuit #1 b.6. 5GUTHRIE 2 (344678) 161.0 kV to 5MOREAU 1 (345239) 161.0 kV Transmission Circuit #1 b.7. 1LOYMART 1 (346010) 12.5 kV to 5LOYMART 1 (344040) 161.0 kV Two Winding #1 b.8. 2GUTHRIE (346063) 69.0 kV to 5GUTHRIE 1 (344677) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0242 | Single Phase Fault with Stuck Breaker on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply Fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 b.4. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 b.5. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.6. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 b.7. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0243 | Single Phase Fault with Stuck Breaker on 5JC ZION 161.00 (344814) 161 kV Bus a. Apply Fault at the 5JC ZION 161.00 (344814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5APCH TP (344026) 161.0 kV to 5APCH FLT (344028) 161.0 kV Transmission Circuit #1 b.2. 2APCH FLT (344027) 69.0 kV to 5APCH FLT (344028) 161.0 kV Two Winding #1 b.3. 5APCH FLT (344028) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #1 b.4. 5JC ZION (344814) 161.0 kV to 5JC ZION TP (344815) 161.0 kV Transmission Circuit #z b.5. 2JC ZION (346089) 69.0 kV to 5JC ZION (344814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0244 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0245 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.4. NE CT17 (542983) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT18 (542984) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0246 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0247 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0248 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0249 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0250 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0251 | Single Phase Fault with Stuck Breaker on NEKOMA 3 115.00 (530608) 115 kV Bus a. Apply Fault at the NEKOMA 3 115.00 (530608) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.4. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.6. NKMA2 1 (530630) 12.5 kV to NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0252 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.3. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0253 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.4. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.5. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0254 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.3. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 b.4. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0255 | Single Phase Fault with Stuck Breaker on WSPRTTP2 69.000 (530587) 69 kV Bus a. Apply Fault at the WSPRTTP2 69.000 (530587) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GT BND 2 (530570) 69.0 kV to WSPRTTP2 (530587) 69.0 kV Transmission Circuit #1 b.4. GT BND 2 (530570) 69.0 kV to WPRTTS 2 (530596) 69.0 kV Transmission Circuit #1 b.5. WSPRTTP2 (530587) 69.0 kV to WSTPRT 2 (530588) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0256 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0257 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0258 | Single Phase Fault with Stuck Breaker on GB NTH 2 69.000 (530568) 69 kV Bus a. Apply Fault at the GB NTH 2 69.000 (530568) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. GB NTH 2 (530568) 69.0 kV to GT BND 2 (530570) 69.0 kV Transmission Circuit #1 b.3. GB NTH 2 (530568) 69.0 kV to SUSANK 2 (530571) 69.0 kV Transmission Circuit #1 b.4. GB NTH 2 (530568) 69.0 kV to COLLEG 2 (530574) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0259 | Single Phase Fault with Stuck Breaker on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. RULETON3 (531357) 115.0 kV to LAWNRID3 (531368) 115.0 kV Transmission Circuit #1 b.5. BIRDCTY3 (531365) 115.0 kV to STFRAN 3 (531370) 115.0 kV Transmission Circuit #1 b.6. BIRDCTY3 (531365) 115.0 kV to MCDONLD3 (531487) 115.0 kV Transmission Circuit #1 b.7. LAWNRID3 (531368) 115.0 kV to STFRANT3 (531471) 115.0 kV Transmission Circuit #1 b.8. STFRAN 3 (531370) 115.0 kV to STFRANT3 (531471) 115.0 kV Transmission Circuit #1 b.9. CSTFRAN3 (531441) 115.0 kV to STFRANT3 (531471) 115.0 kV Transmission Circuit #1 b.10. MCDONLD3 (531487) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.11. BVERVLLY (531488) 115.0 kV to ONEOK 3 (531489) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0260 | Single Phase Fault with Stuck Breaker on ATWOOD 3 115.00 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 115.00 (530554) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. LUDELLT3 (531220) 115.0 kV to LUDELL 3 (531221) 115.0 kV Transmission Circuit #1 b.5. LUDELLT3 (531220) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.6. LUDELLT3 (531220) 115.0 kV to HERNDON3 (531367) 115.0 kV Transmission Circuit #1 b.7. ATWODSW3 (531364) 115.0 kV to NATWOOD3 (531369) 115.0 kV Transmission Circuit #1 b.8. HERNDON3 (531367) 115.0 kV to JOHNSON3 (531371) 115.0 kV Transmission Circuit #1 b.9. JOHNSON3 (531371) 115.0 kV to OBER T 3 (531457) 115.0 kV Transmission Circuit #1 b.10. NORCATR3 (531372) 115.0 kV to RHOADES3 (531373) 115.0 kV Transmission Circuit #1 b.11. NORCATR3 (531372) 115.0 kV to OBER T 3 (531457) 115.0 kV Transmission Circuit #1 b.12. OBER T 3 (531457) 115.0 kV to OBERLIN3 (531458) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0261 | Single Phase Fault with Stuck Breaker on GEM_SW 3 115.00 (530713) 115 kV Bus a. Apply Fault at the GEM_SW 3 115.00 (530713) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. SEGNTP 3 (530682) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.3. GEM_SW 3 (530713) 115.0 kV to COLBY_PUMP3 (530716) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0262 | Single Phase Fault with Stuck Breaker on SEGNTP 3 115.00 (530682) 115 kV Bus a. Apply Fault at the SEGNTP 3 115.00 (530682) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.3. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.4. SEGNTP 3 (530682) 115.0 kV to SEGUIN 3 (530683) 115.0 kV Transmission Circuit #1 b.5. SEGNTP 3 (530682) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.6. SEGUIN 3 (530683) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0263 | Single Phase Fault with Stuck Breaker on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply Fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.2. PH RUN 3 (530559) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 b.3. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. SEGNTP 3 (530682) 115.0 kV to SEGUIN 3 (530683) 115.0 kV Transmission Circuit #1 b.5. SEGUIN 3 (530683) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0264 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.5. BEACH 3 (530557) 115.0 kV to HILLCTY3 (531387) 34.5 kV Two Winding #1 b.6. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.7. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0265 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0266 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0267 | Single Phase Fault with Stuck Breaker on GMEC 3 115.00 (530676) 115 kV Bus a. Apply Fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0268 | Single Phase Fault with Stuck Breaker on SALINE 3 115.00 (530551) 115 kV Bus a. Apply Fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0269 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.5. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.6. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.7. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0270 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0271 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0272 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0273 | Single Phase Fault with Stuck Breaker on NESCTY 3 115.00 (530607) 115 kV Bus a. Apply Fault at the NESCTY 3 115.00 (530607) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NESCTY 3 (530607) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NESCTY 3 (530607) 115.0 kV to NESS-CT1 (539722) 34.5 kV to NES-CT-T (539924) 13.8 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0274 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.9. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.10. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0275 | Single Phase Fault with Stuck Breaker on ALXNDR 3 115.00 (530606) 115 kV Bus a. Apply Fault at the ALXNDR 3 115.00 (530606) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.3. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.4. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.5. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.6. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.8. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.9. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.10. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0276 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0277 | Single Phase Fault with Stuck Breaker on PH RUN 3 115.00 (530559) 115 kV Bus a. Apply Fault at the PH RUN 3 115.00 (530559) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PH RUN 3 (530559) 115.0 kV to ANGELUS (530717) 115.0 kV Transmission Circuit #1 b.2. PH RUN 3 (530559) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 b.3. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. ARNOLD3 (531409) 115.0 kV to GOVE 3 (531411) 115.0 kV Transmission Circuit #1 b.5. ARNOLD3 (531409) 115.0 kV to RANSOM 3 (531414) 115.0 kV Transmission Circuit #1 b.6. GOVE 3 (531411) 115.0 kV to GRINNEL3 (531412) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0278 | Single Phase Fault with Stuck Breaker on GODLNDT3 115.00 (531443) 115 kV Bus a. Apply Fault at the GODLNDT3 115.00 (531443) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. BREWSTR3 (531351) 115.0 kV to GOODLND3 (531353) 115.0 kV Transmission Circuit #1 b.3. BREWSTR3 (531351) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.4. GOODLND3 (531353) 115.0 kV to GODLNDT3 (531443) 115.0 kV Transmission Circuit #1 b.5. RULETON3 (531357) 115.0 kV to GODLNDT3 (531443) 115.0 kV Transmission Circuit #1 b.6. GODLNDT3 (531443) 115.0 kV to GOODCTY3 (531444) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0279 | Single Phase Fault with Stuck Breaker on MINGO 3 115.00 (531429) 115 kV Bus a. Apply Fault at the MINGO 3 115.00 (531429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. PH RUN 3 (530559) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0280 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.5. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0281 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.5. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.7. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0282 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0283 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0284 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0285 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0286 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0287 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0288 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0289 | Single Phase Fault with Stuck Breaker on SHAYS_230 230.00 (530610) 230 kV Bus a. Apply Fault at the SHAYS_230 230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0290 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 b.8. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0291 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-065-TAP (768280) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0292 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0293 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0294 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.3. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0295 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0296 | Single Phase Fault with Stuck Breaker on BUFLOCRK6 230.00 (530688) 230 kV Bus a. Apply Fault at the BUFLOCRK6 230.00 (530688) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.3. BUFLOCRK1 (530689) 34.5 kV to PRWNDCL1 (530701) 34.5 kV Transmission Circuit #1 b.4. PRWINDG1 (530690) 0.7 kV to PRWNDCL1 (530701) 34.5 kV Two Winding #1 b.5. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.8. BUFLOCRK6 (530688) 230.0 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0297 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0298 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0299 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0300 | Single Phase Fault with Stuck Breaker on COLBY 3 115.00 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to Load #1 b.2. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0301 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0302 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0303 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0304 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0305 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0306 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLM1G (640010) 23.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0307 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0308 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.3. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0309 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0310 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0311 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0312 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0313 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0314 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.3. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0315 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0316 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0317 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0318 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0319 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0320 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0321 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0322 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0323 | Single Phase Fault with Stuck Breaker on BARBER 5 161.00 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.3. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.4. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.5. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.6. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0324 | Single Phase Fault with Stuck Breaker on WOLCOTT5 161.00 (546669) 161 kV Bus a. Apply Fault at the WOLCOTT5 161.00 (546669) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.2. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.3. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0325 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0326 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.3. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.4. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 b.7. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0327 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0328 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0329 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0330 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0331 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0332 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0333 | Single Phase Fault with Stuck Breaker on J1490_POI 345.00 (44888) 345 kV Bus a. Apply Fault at the J1490_POI 345.00 (44888) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1490_POI (44888) 345.0 kV to 7MONTGMRY (345230) 345.0 kV Transmission Circuit #1 b.2. J1490_POI (44888) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0334 | Single Phase Fault with Stuck Breaker on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply Fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 b.2. 7KINGDM (300043) 345.0 kV to 5KINGDMB1 (300090) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0335 | Single Phase Fault with Stuck Breaker on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply Fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to VSC2_3 (992003) 345.0 kV Transmission Circuit #1 b.2. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0336 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to 7HUBEN (300042) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to 5MORGANXF2 (301622) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0337 | Single Phase Fault with Stuck Breaker on 5BOONE 161.00 (300061) 161 kV Bus a. Apply Fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5BOONE (300061) 161.0 kV to 5MLRSBGB1 (300519) 161.0 kV Transmission Circuit #1 b.2. 5BOONE (300061) 161.0 kV to 2BOONE (300493) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0338 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 b.2. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0339 | Single Phase Fault with Stuck Breaker on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply Fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LATHRP (300091) 161.0 kV to 5MPLTAP (300036) 161.0 kV Transmission Circuit #1 b.2. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0340 | Single Phase Fault with Stuck Breaker on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply Fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #z1 b.2. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0341 | Single Phase Fault with Stuck Breaker on 5NORTON 161.00 (300105) 161 kV Bus a. Apply Fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTON (300105) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #z1 b.2. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0342 | Single Phase Fault with Stuck Breaker on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply Fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 b.2. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0343 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to 2SEDALI (300541) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0344 | Single Phase Fault with Stuck Breaker on 5MCBAINB1 161.00 (300501) 161 kV Bus a. Apply Fault at the 5MCBAINB1 161.00 (300501) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB1 (300501) 161.0 kV to 5MCBAINB2 (301489) 161.0 kV Transmission Circuit #z1 b.2. 5MCBAINB1 (300501) 161.0 kV to 5BOONE (300061) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0345 | Single Phase Fault with Stuck Breaker on 2GEOGT1 69.000 (300529) 69 kV Bus a. Apply Fault at the 2GEOGT1 69.000 (300529) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT1 (300529) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT1 (300529) 69.0 kV to 2HUGHSV (300533) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0346 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0347 | Single Phase Fault with Stuck Breaker on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply Fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0348 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 b.2. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0349 | Single Phase Fault with Stuck Breaker on 5CALIF 161.00 (300063) 161 kV Bus a. Apply Fault at the 5CALIF 161.00 (300063) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CALIF (300550) 69.0 kV to 5CALIF (300063) 161.0 kV Two Winding #2 b.2. 2CALIF (300550) 69.0 kV to 2FORTNA (300554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0350 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0351 | Single Phase Fault with Stuck Breaker on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply Fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 b.2. 5LAMAR (300794) 161.0 kV to 2LAMR (300651) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0352 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to 5JASPER (300950) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0353 | Single Phase Fault with Stuck Breaker on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply Fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PLATCTY (301552) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #z1 b.2. 5PLATCTY (301552) 161.0 kV to 2PLATCTY (300307) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0354 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MOCITYB1 (301563) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0355 | Single Phase Fault with Stuck Breaker on MIDLTNT4 138.00 (514804) 138 kV Bus a. Apply Fault at the MIDLTNT4 138.00 (514804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.2. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0356 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0357 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0358 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0359 | Single Phase Fault with Stuck Breaker on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0360 | Single Phase Fault with Stuck Breaker on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply Fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to JAGGER 3 (531360) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0361 | Single Phase Fault with Stuck Breaker on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply Fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEOTI 3 (531428) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 b.2. LEOTI 3 (531428) 115.0 kV to SELKIRK3 (531434) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0362 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 b.2. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0363 | Single Phase Fault with Stuck Breaker on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply Fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 b.2. SCOTCTY3 (531433) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0364 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0365 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 b.2. SETAB 3 (531464) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0366 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #2 b.2. SPERVIL7 (531469) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0367 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0368 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0369 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0370 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0371 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0372 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0373 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0374 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0375 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0376 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0377 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0378 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to G21-096-TAP (766141) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0379 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0380 | Single Phase Fault with Stuck Breaker on BURNS 7 345.00 (532803) 345 kV Bus a. Apply Fault at the BURNS 7 345.00 (532803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURNS 7 (532803) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. BURNS 7 (532803) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0381 | Single Phase Fault with Stuck Breaker on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0382 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 7 (532770) 345.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 b.2. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0383 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 b.2. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0384 | Single Phase Fault with Stuck Breaker on BAKER 2 69.000 (532926) 69 kV Bus a. Apply Fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0385 | Single Phase Fault with Stuck Breaker on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 b.2. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0386 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. MARMTNW5 (532935) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0387 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.2. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0388 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to LITCH 5 (532932) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0389 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to MIDLTNT4 (514804) 138.0 kV Transmission Circuit #1 b.2. CRESWLN4 (532981) 138.0 kV to CRESWLS2 (533573) 69.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0390 | Single Phase Fault with Stuck Breaker on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply Fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 4 (532982) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0391 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0392 | Single Phase Fault with Stuck Breaker on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply Fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.2. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0393 | Single Phase Fault with Stuck Breaker on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0394 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 4 (532996) 138.0 kV to TIOGA 2 (533646) 69.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0395 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK4 (532997) 138.0 kV to BUTLER 4 (532987) 138.0 kV Transmission Circuit #1 b.2. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0396 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. ALTOONA4 (533001) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0397 | Single Phase Fault with Stuck Breaker on DEARING4 138.00 (533002) 138 kV Bus a. Apply Fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0398 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0399 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONTGOM4 (533004) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0400 | Single Phase Fault with Stuck Breaker on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply Fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0401 | Single Phase Fault with Stuck Breaker on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply Fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0402 | Single Phase Fault with Stuck Breaker on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply Fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to HALSTD 4 (533011) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0403 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.2. NEOSHOS4 (533020) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0404 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.2. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0405 | Single Phase Fault with Stuck Breaker on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply Fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0406 | Single Phase Fault with Stuck Breaker on BU11PON4 138.00 (533032) 138 kV Bus a. Apply Fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BU11PON4 (533032) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0407 | Single Phase Fault with Stuck Breaker on CENTENN4 138.00 (533034) 138 kV Bus a. Apply Fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0408 | Single Phase Fault with Stuck Breaker on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0409 | Single Phase Fault with Stuck Breaker on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply Fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0410 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0411 | Single Phase Fault with Stuck Breaker on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply Fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0412 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0413 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to EVANS N4 (533040) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0414 | Single Phase Fault with Stuck Breaker on FARBER 4 138.00 (533042) 138 kV Bus a. Apply Fault at the FARBER 4 138.00 (533042) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0415 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0416 | Single Phase Fault with Stuck Breaker on GILL W 4 138.00 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.2. GILL W 4 (533045) 138.0 kV to GILL E 4 (533044) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0417 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.2. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0418 | Single Phase Fault with Stuck Breaker on GILL 4 138.00 (533047) 138 kV Bus a. Apply Fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL 4 (533047) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0419 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0420 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERS4 (533050) 138.0 kV to HOOVERN4 (533049) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0421 | Single Phase Fault with Stuck Breaker on 47TH ST4 138.00 (533058) 138 kV Bus a. Apply Fault at the 47TH ST4 138.00 (533058) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0422 | Single Phase Fault with Stuck Breaker on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. ROSEHIL4 (533062) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0423 | Single Phase Fault with Stuck Breaker on WACO S 4 138.00 (533071) 138 kV Bus a. Apply Fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WACO S 4 (533071) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #1 b.2. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0424 | Single Phase Fault with Stuck Breaker on WACO 4 138.00 (533072) 138 kV Bus a. Apply Fault at the WACO 4 138.00 (533072) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 b.2. WACO 4 (533072) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0425 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0426 | Single Phase Fault with Stuck Breaker on 4CORNER3 115.00 (533158) 115 kV Bus a. Apply Fault at the 4CORNER3 115.00 (533158) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 4CORNER3 (533158) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.2. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0427 | Single Phase Fault with Stuck Breaker on OSAGE J3 115.00 (533171) 115 kV Bus a. Apply Fault at the OSAGE J3 115.00 (533171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OSAGE J3 (533171) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.2. OSAGE J3 (533171) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0428 | Single Phase Fault with Stuck Breaker on EAST ST3 115.00 (533301) 115 kV Bus a. Apply Fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.2. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0429 | Single Phase Fault with Stuck Breaker on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply Fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0430 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LANG 3 (533304) 115.0 kV to LANG 7 (532769) 345.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 b.2. LANG 3 (533304) 115.0 kV to EAST ST3 (533301) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0431 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 3 (533305) 115.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 b.2. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0432 | Single Phase Fault with Stuck Breaker on READING3 115.00 (533306) 115 kV Bus a. Apply Fault at the READING3 115.00 (533306) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. READING3 (533306) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 b.2. READING3 (533306) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0433 | Single Phase Fault with Stuck Breaker on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply Fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE3 (533307) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0434 | Single Phase Fault with Stuck Breaker on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply Fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0435 | Single Phase Fault with Stuck Breaker on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.2. WEMPORI3 (533309) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0436 | Single Phase Fault with Stuck Breaker on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply Fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WMBROSJ3 (533311) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0437 | Single Phase Fault with Stuck Breaker on BURLJCT2 69.000 (533626) 69 kV Bus a. Apply Fault at the BURLJCT2 69.000 (533626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0438 | Single Phase Fault with Stuck Breaker on CC2SHAR2 69.000 (533629) 69 kV Bus a. Apply Fault at the CC2SHAR2 69.000 (533629) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC2SHAR2 (533629) 69.0 kV to CC5SHAR1 (533888) 12.5 kV Two Winding #1 b.2. CC2SHAR2 (533629) 69.0 kV to CC6SHAR1 (533889) 12.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0439 | Single Phase Fault with Stuck Breaker on CC3WEST2 69.000 (533630) 69 kV Bus a. Apply Fault at the CC3WEST2 69.000 (533630) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC3WEST2 (533630) 69.0 kV to BURLJCT2 (533626) 69.0 kV Transmission Circuit #1 b.2. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0440 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0441 | Single Phase Fault with Stuck Breaker on UN1ELSM2 69.000 (533647) 69 kV Bus a. Apply Fault at the UN1ELSM2 69.000 (533647) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UN1ELSM2 (533647) 69.0 kV to MARMATN2 (533639) 69.0 kV Transmission Circuit #1 b.2. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0442 | Single Phase Fault with Stuck Breaker on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply Fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0443 | Single Phase Fault with Stuck Breaker on LABETTS2 69.000 (533696) 69 kV Bus a. Apply Fault at the LABETTS2 69.000 (533696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0444 | Single Phase Fault with Stuck Breaker on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply Fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0445 | Single Phase Fault with Stuck Breaker on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply Fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0446 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 b.2. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0447 | Single Phase Fault with Stuck Breaker on BELL 2 69.000 (533783) 69 kV Bus a. Apply Fault at the BELL 2 69.000 (533783) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELL 2 (533783) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 b.2. BELL 2 (533783) 69.0 kV to SC3MILL2 (533552) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0448 | Single Phase Fault with Stuck Breaker on CANAL 4 138.00 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 138.00 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALS 2 (533784) 69.0 kV to CANAL 4 (533033) 138.0 kV to CANAL 1 (533101) 9.5 kV Three Winding #1 b.2. CANALS 2 (533784) 69.0 kV to CANALN 2 (533790) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0449 | Single Phase Fault with Stuck Breaker on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply Fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0450 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.2. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0451 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL W 2 (533796) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 b.2. GILL W 2 (533796) 69.0 kV to GILL E 4 (533044) 138.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0452 | Single Phase Fault with Stuck Breaker on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply Fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILLJCT2 (533798) 69.0 kV to GILL E 2 (533795) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0453 | Single Phase Fault with Stuck Breaker on HAYSVJS2 69.000 (533802) 69 kV Bus a. Apply Fault at the HAYSVJS2 69.000 (533802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYSVJS2 (533802) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #1 b.2. HAYSVJS2 (533802) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0454 | Single Phase Fault with Stuck Breaker on HAYSVJN2 69.000 (533804) 69 kV Bus a. Apply Fault at the HAYSVJN2 69.000 (533804) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAYSVJN2 (533804) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #1 b.2. HAYSVJN2 (533804) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0455 | Single Phase Fault with Stuck Breaker on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply Fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0456 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERS2 (533806) 69.0 kV to HOOVERS4 (533050) 138.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 b.2. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0457 | Single Phase Fault with Stuck Breaker on HYDRJN2 69.000 (533808) 69 kV Bus a. Apply Fault at the HYDRJN2 69.000 (533808) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDRJN2 (533808) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 b.2. HYDRJN2 (533808) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0458 | Single Phase Fault with Stuck Breaker on HYDRJS2 69.000 (533810) 69 kV Bus a. Apply Fault at the HYDRJS2 69.000 (533810) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HYDRJS2 (533810) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 b.2. HYDRJS2 (533810) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0459 | Single Phase Fault with Stuck Breaker on LIN 2 69.000 (533812) 69 kV Bus a. Apply Fault at the LIN 2 69.000 (533812) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.2. LIN 2 (533812) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0460 | Single Phase Fault with Stuck Breaker on MACARTH2 69.000 (533813) 69 kV Bus a. Apply Fault at the MACARTH2 69.000 (533813) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MACARTH2 (533813) 69.0 kV to GILL E 2 (533795) 69.0 kV Transmission Circuit #1 b.2. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0461 | Single Phase Fault with Stuck Breaker on BLF-CRK4 138.00 (539002) 138 kV Bus a. Apply Fault at the BLF-CRK4 138.00 (539002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLF-CRK4 (539002) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0462 | Single Phase Fault with Stuck Breaker on CLDWELL4 138.00 (539003) 138 kV Bus a. Apply Fault at the CLDWELL4 138.00 (539003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLDWELL4 (539003) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0463 | Single Phase Fault with Stuck Breaker on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. MILAN_GOAB (539008) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0464 | Single Phase Fault with Stuck Breaker on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply Fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0465 | Single Phase Fault with Stuck Breaker on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply Fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.2. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0466 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to GRTBEND3 (539678) 115.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0467 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.2. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0468 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0469 | Single Phase Fault with Stuck Breaker on FORD 3 115.00 (539758) 115 kV Bus a. Apply Fault at the FORD 3 115.00 (539758) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORD 3 (539758) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.2. FORD 3 (539758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0470 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.2. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0471 | Single Phase Fault with Stuck Breaker on NFTDODG3 115.00 (539771) 115 kV Bus a. Apply Fault at the NFTDODG3 115.00 (539771) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NFTDODG3 (539771) 115.0 kV to FTDODGE3 (539671) 115.0 kV Transmission Circuit #2 b.2. NFTDODG3 (539771) 115.0 kV to SPRVL 3 (539759) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0472 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0473 | Single Phase Fault with Stuck Breaker on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply Fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345.0 kV to GEN-2008-124 (579480) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0474 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0475 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0476 | Single Phase Fault with Stuck Breaker on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 b.2. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0477 | Single Phase Fault with Stuck Breaker on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. SMTHVL 5 (541204) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0478 | Single Phase Fault with Stuck Breaker on KCI 5 161.00 (541212) 161 kV Bus a. Apply Fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KCI 5 (541212) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. KCI 5 (541212) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0479 | Single Phase Fault with Stuck Breaker on FRLVW 5 161.00 (541213) 161 kV Bus a. Apply Fault at the FRLVW 5 161.00 (541213) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRLVW 5 (541213) 161.0 kV to KCI 5 (541212) 161.0 kV Transmission Circuit #1 b.2. FRLVW 5 (541213) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0480 | Single Phase Fault with Stuck Breaker on TWA 5 161.00 (541214) 161 kV Bus a. Apply Fault at the TWA 5 161.00 (541214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 b.2. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0481 | Single Phase Fault with Stuck Breaker on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply Fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 b.2. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0482 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0483 | Single Phase Fault with Stuck Breaker on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply Fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. PLTCTY 5 (541221) 161.0 kV to KCI 5 (541212) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0484 | Single Phase Fault with Stuck Breaker on GRAINVL5 161.00 (541226) 161 kV Bus a. Apply Fault at the GRAINVL5 161.00 (541226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAINVL5 (541226) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 b.2. GRAINVL5 (541226) 161.0 kV to OAKGRV 5 (541227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0485 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRIDGE5 (541230) 161.0 kV to FRSTCRK5 (543039) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0486 | Single Phase Fault with Stuck Breaker on LEX161 5 161.00 (541232) 161 kV Bus a. Apply Fault at the LEX161 5 161.00 (541232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. LEX161 5 (541232) 161.0 kV to LEX69 2 (541264) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0487 | Single Phase Fault with Stuck Breaker on RICHMND5 161.00 (541236) 161 kV Bus a. Apply Fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to LEX161 5 (541232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0488 | Single Phase Fault with Stuck Breaker on BLSPW 5 161.00 (541237) 161 kV Bus a. Apply Fault at the BLSPW 5 161.00 (541237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLSPW 5 (541237) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0489 | Single Phase Fault with Stuck Breaker on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply Fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDEAST5 (541241) 161.0 kV to G22-100-TAP (768980) 161.0 kV Transmission Circuit #1 b.2. SEDEAST5 (541241) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0490 | Single Phase Fault with Stuck Breaker on LBRTYWT5 161.00 (541247) 161 kV Bus a. Apply Fault at the LBRTYWT5 161.00 (541247) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYWT5 (541247) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 b.2. LBRTYWT5 (541247) 161.0 kV to HLLMRK 5 (541215) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0491 | Single Phase Fault with Stuck Breaker on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply Fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. LBRTYST5 (541248) 161.0 kV to LIBRTYS2 (543095) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0492 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 b.2. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0493 | Single Phase Fault with Stuck Breaker on STALEY 2 69.000 (541261) 69 kV Bus a. Apply Fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STALEY 2 (541261) 69.0 kV to RNRDGE 2 (541260) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0494 | Single Phase Fault with Stuck Breaker on LIBERTY2 69.000 (541262) 69 kV Bus a. Apply Fault at the LIBERTY2 69.000 (541262) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY2 (541262) 69.0 kV to PLUMRRD2 (543114) 69.0 kV Transmission Circuit #1 b.2. LIBERTY2 (541262) 69.0 kV to SIBLEY 2 (541263) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0495 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 b.2. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0496 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0497 | Single Phase Fault with Stuck Breaker on KELHYS 2 69.000 (541273) 69 kV Bus a. Apply Fault at the KELHYS 2 69.000 (541273) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELHYS 2 (541273) 69.0 kV to SEDN 2 (541271) 69.0 kV Transmission Circuit #1 b.2. KELHYS 2 (541273) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0498 | Single Phase Fault with Stuck Breaker on PITTCRN2 69.000 (541274) 69 kV Bus a. Apply Fault at the PITTCRN2 69.000 (541274) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTCRN2 (541274) 69.0 kV to SEDS 2 (541272) 69.0 kV Transmission Circuit #1 b.2. PITTCRN2 (541274) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0499 | Single Phase Fault with Stuck Breaker on SEDPLT 2 69.000 (541275) 69 kV Bus a. Apply Fault at the SEDPLT 2 69.000 (541275) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDPLT 2 (541275) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 b.2. SEDPLT 2 (541275) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0500 | Single Phase Fault with Stuck Breaker on COLECMP2 69.000 (541276) 69 kV Bus a. Apply Fault at the COLECMP2 69.000 (541276) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLECMP2 (541276) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 b.2. COLECMP2 (541276) 69.0 kV to SEDPLT 2 (541275) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0501 | Single Phase Fault with Stuck Breaker on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply Fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAFBE_SW5 (541337) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. WAFBE_SW5 (541337) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0502 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 b.2. S.HARP 5 (541341) 161.0 kV to ARCHIE 5 (541207) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0503 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0504 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0505 | Single Phase Fault with Stuck Breaker on KNOSTERTP 69.000 (541534) 69 kV Bus a. Apply Fault at the KNOSTERTP 69.000 (541534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOSTERTP (541534) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 b.2. KNOSTERTP (541534) 69.0 kV to MONSERTP (541524) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0506 | Single Phase Fault with Stuck Breaker on LAMONTETP 69.000 (541535) 69 kV Bus a. Apply Fault at the LAMONTETP 69.000 (541535) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMONTETP (541535) 69.0 kV to SEDN 2 (541271) 69.0 kV Transmission Circuit #1 b.2. LAMONTETP (541535) 69.0 kV to KNOSTERTP (541534) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0507 | Single Phase Fault with Stuck Breaker on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply Fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0508 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to ATLNTIC7 (542940) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0509 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0510 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 b.2. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0511 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0512 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0513 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LAC G1 1 (542955) 22.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0514 | Single Phase Fault with Stuck Breaker on TROOST 5 161.00 (542986) 161 kV Bus a. Apply Fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 b.2. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0515 | Single Phase Fault with Stuck Breaker on GRAND 5 161.00 (542987) 161 kV Bus a. Apply Fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0516 | Single Phase Fault with Stuck Breaker on GRAND W5 161.00 (542988) 161 kV Bus a. Apply Fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0517 | Single Phase Fault with Stuck Breaker on NAVY 5 161.00 (542989) 161 kV Bus a. Apply Fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NAVY 5 (542989) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0518 | Single Phase Fault with Stuck Breaker on CROSTWN5 161.00 (542990) 161 kV Bus a. Apply Fault at the CROSTWN5 161.00 (542990) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSTWN5 (542990) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. CROSTWN5 (542990) 161.0 kV to TROOST 5 (542986) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0519 | Single Phase Fault with Stuck Breaker on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply Fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDTOWN5 (542996) 161.0 kV to TROOST 5 (542986) 161.0 kV Transmission Circuit #1 b.2. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0520 | Single Phase Fault with Stuck Breaker on LEEDS 5 161.00 (542997) 161 kV Bus a. Apply Fault at the LEEDS 5 161.00 (542997) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEEDS 5 (542997) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0521 | Single Phase Fault with Stuck Breaker on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply Fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0522 | Single Phase Fault with Stuck Breaker on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0523 | Single Phase Fault with Stuck Breaker on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to AVONDAL5 (543015) 161.0 kV Transmission Circuit #1 b.2. GLADSTN5 (543016) 161.0 kV to GLADSTN_CAP5 (542946) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0524 | Single Phase Fault with Stuck Breaker on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply Fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 b.2. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0525 | Single Phase Fault with Stuck Breaker on BARRY 5 161.00 (543019) 161 kV Bus a. Apply Fault at the BARRY 5 161.00 (543019) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRY 5 (543019) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. BARRY 5 (543019) 161.0 kV to BARRY_CAP 5 (542944) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0526 | Single Phase Fault with Stuck Breaker on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply Fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMGHAM5 (543020) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.2. BRMGHAM5 (543020) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0527 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV to NASHUA 7 (542980) 345.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 b.2. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0528 | Single Phase Fault with Stuck Breaker on SHOLCRK5 161.00 (543029) 161 kV Bus a. Apply Fault at the SHOLCRK5 161.00 (543029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHOLCRK5 (543029) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. SHOLCRK5 (543029) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0529 | Single Phase Fault with Stuck Breaker on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply Fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 b.2. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0530 | Single Phase Fault with Stuck Breaker on COURTNY2 69.000 (543085) 69 kV Bus a. Apply Fault at the COURTNY2 69.000 (543085) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0531 | Single Phase Fault with Stuck Breaker on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply Fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. LAKCTYJ2 (543087) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0532 | Single Phase Fault with Stuck Breaker on BLUSPRG2 69.000 (543088) 69 kV Bus a. Apply Fault at the BLUSPRG2 69.000 (543088) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUSPRG2 (543088) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 b.2. BLUSPRG2 (543088) 69.0 kV to LAKCTY 2 (543092) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0533 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCNRD2 (543091) 69.0 kV to DUNCAN 5 (541235) 161.0 kV Two Winding #1 b.2. DUNCNRD2 (543091) 69.0 kV to LAKCTYK2 (543093) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0534 | Single Phase Fault with Stuck Breaker on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply Fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUGRCK_TP_E2 (543165) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 b.2. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0535 | Single Phase Fault with Stuck Breaker on DAKOTA_5 161.00 (543650) 161 kV Bus a. Apply Fault at the DAKOTA_5 161.00 (543650) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAKOTA_5 (543650) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #1 b.2. DAKOTA_5 (543650) 161.0 kV to CNTRVIL5 (543065) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0536 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0537 | Single Phase Fault with Stuck Breaker on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply Fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0538 | Single Phase Fault with Stuck Breaker on COL 94 2 69.000 (547530) 69 kV Bus a. Apply Fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0539 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 2 (547539) 69.0 kV to JOP145 5 (547470) 161.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 b.2. JOP145 2 (547539) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0540 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to RIV4525 (547469) 161.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 b.2. RIV167 2 (547541) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0541 | Single Phase Fault with Stuck Breaker on BAX271 2 69.000 (547554) 69 kV Bus a. Apply Fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.2. BAX271 2 (547554) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0542 | Single Phase Fault with Stuck Breaker on GLF339 2 69.000 (547690) 69 kV Bus a. Apply Fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLF339 2 (547690) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0543 | Single Phase Fault with Stuck Breaker on SUB I 69.000 (548800) 69 kV Bus a. Apply Fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 b.2. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0544 | Single Phase Fault with Stuck Breaker on SUB K 69.000 (548801) 69 kV Bus a. Apply Fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0545 | Single Phase Fault with Stuck Breaker on SUB H 69.000 (548802) 69 kV Bus a. Apply Fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB H (548802) 69.0 kV to COURTNY2 (543085) 69.0 kV Transmission Circuit #1 b.2. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0546 | Single Phase Fault with Stuck Breaker on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0547 | Single Phase Fault with Stuck Breaker on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply Fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0548 | Single Phase Fault with Stuck Breaker on SUB B 69.000 (548810) 69 kV Bus a. Apply Fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 b.2. SUB B (548810) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0549 | Single Phase Fault with Stuck Breaker on SUB J 69.000 (548811) 69 kV Bus a. Apply Fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB J (548811) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0550 | Single Phase Fault with Stuck Breaker on G15052_T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15052_T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15052_T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15052_T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0551 | Single Phase Fault with Stuck Breaker on G16-046-TAP 345.00 (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP 345.00 (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0552 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0553 | Single Phase Fault with Stuck Breaker on GEN-2022-161345.00 (562477) 345 kV Bus a. Apply Fault at the GEN-2022-161345.00 (562477) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-161 (562477) 345.0 kV to GEN-2014-001 (583850) 345.0 kV Transmission Circuit #z1 b.2. GEN-2022-161 (562477) 345.0 kV to G22-161XFMR2 (770205) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0554 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583850) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583850) 345.0 kV to GEN-2014-001 (583859) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583850) 345.0 kV to GEN-2022-161 (562477) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0555 | Single Phase Fault with Stuck Breaker on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply Fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-074 (587680) 345.0 kV to G16-074XFMR1 (587681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0556 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR1 (588361) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0557 | Single Phase Fault with Stuck Breaker on G16-153-TAP 345.00 (588364) 345 kV Bus a. Apply Fault at the G16-153-TAP 345.00 (588364) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-153-TAP (588364) 345.0 kV to GEN-2016-153 (588360) 345.0 kV Transmission Circuit #1 b.2. G16-153-TAP (588364) 345.0 kV to GEN-2017-086 (589240) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0558 | Single Phase Fault with Stuck Breaker on GEN-2017-005161.00 (588500) 161 kV Bus a. Apply Fault at the GEN-2017-005161.00 (588500) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-005 (588500) 161.0 kV to G17-005XFMR1 (588501) 34.5 kV Two Winding #1 b.2. GEN-2017-005 (588500) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0559 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0560 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0561 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0562 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0563 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0564 | Single Phase Fault with Stuck Breaker on GI-95_POI 345.00 (709500) 345 kV Bus a. Apply Fault at the GI-95_POI 345.00 (709500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI-95_POI (709500) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. GI-95_POI (709500) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0565 | Single Phase Fault with Stuck Breaker on GEN-2017-183345.00 (761376) 345 kV Bus a. Apply Fault at the GEN-2017-183345.00 (761376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-183 (761376) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-183 (761376) 345.0 kV to G17-184XFMR2 (761401) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0566 | Single Phase Fault with Stuck Breaker on GEN-2018-125345.00 (763406) 345 kV Bus a. Apply Fault at the GEN-2018-125345.00 (763406) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-125 (763406) 345.0 kV to G18-125-XFM1 (763407) 34.5 kV Two Winding #1 b.2. GEN-2018-125 (763406) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0567 | Single Phase Fault with Stuck Breaker on GEN-2018-128345.00 (763417) 345 kV Bus a. Apply Fault at the GEN-2018-128345.00 (763417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-128 (763417) 345.0 kV to G18-128-XFM1 (763418) 34.5 kV Two Winding #1 b.2. GEN-2018-128 (763417) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0568 | Single Phase Fault with Stuck Breaker on GEN-2019-030345.00 (763670) 345 kV Bus a. Apply Fault at the GEN-2019-030345.00 (763670) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-030 (763670) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 b.2. GEN-2019-030 (763670) 345.0 kV to G19-030-XFM1 (763671) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0569 | Single Phase Fault with Stuck Breaker on G19-053/055 230.00 (763846) 230 kV Bus a. Apply Fault at the G19-053/055 230.00 (763846) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-053/055 (763846) 230.0 kV to G19-055-XFM1 (763869) 34.5 kV Two Winding #1 b.2. G19-053/055 (763846) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0570 | Single Phase Fault with Stuck Breaker on G19-055-TAP 230.00 (763850) 230 kV Bus a. Apply Fault at the G19-055-TAP 230.00 (763850) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-055-TAP (763850) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 b.2. G19-055-TAP (763850) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0571 | Single Phase Fault with Stuck Breaker on G19-054/068 230.00 (763857) 230 kV Bus a. Apply Fault at the G19-054/068 230.00 (763857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054/068 (763857) 230.0 kV to G19-054-XFM1 (763858) 34.5 kV Two Winding #1 b.2. G19-054/068 (763857) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0572 | Single Phase Fault with Stuck Breaker on GEN-2020-072161.00 (764345) 161 kV Bus a. Apply Fault at the GEN-2020-072161.00 (764345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-072 (764345) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-072 (764345) 161.0 kV to G20-072-XFM1 (764348) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0573 | Single Phase Fault with Stuck Breaker on GEN-2020-090345.00 (765190) 345 kV Bus a. Apply Fault at the GEN-2020-090345.00 (765190) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-090 (765190) 345.0 kV to G20-090-XFM1 (765193) 34.5 kV Two Winding #1 b.2. GEN-2020-090 (765190) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0574 | Single Phase Fault with Stuck Breaker on G20-090-TAP 345.00 (765200) 345 kV Bus a. Apply Fault at the G20-090-TAP 345.00 (765200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-090-TAP (765200) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. G20-090-TAP (765200) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0575 | Single Phase Fault with Stuck Breaker on GEN-2021-029345.00 (765570) 345 kV Bus a. Apply Fault at the GEN-2021-029345.00 (765570) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-029 (765570) 345.0 kV to G21-029-XFM1 (765574) 34.5 kV Two Winding #1 b.2. GEN-2021-029 (765570) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0576 | Single Phase Fault with Stuck Breaker on G21-029-TAP 345.00 (765571) 345 kV Bus a. Apply Fault at the G21-029-TAP 345.00 (765571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-029-TAP (765571) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. G21-029-TAP (765571) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0577 | Single Phase Fault with Stuck Breaker on GEN-2021-068345.00 (765910) 345 kV Bus a. Apply Fault at the GEN-2021-068345.00 (765910) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-068 (765910) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-068 (765910) 345.0 kV to G21-068-XFM1 (765914) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0578 | Single Phase Fault with Stuck Breaker on G21-068-TAP 345.00 (765911) 345 kV Bus a. Apply Fault at the G21-068-TAP 345.00 (765911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-068-TAP (765911) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. G21-068-TAP (765911) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0579 | Single Phase Fault with Stuck Breaker on GEN-2020-007345.00 (766260) 345 kV Bus a. Apply Fault at the GEN-2020-007345.00 (766260) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-007 (766260) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-007 (766260) 345.0 kV to G20-007-XFM1 (766264) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0580 | Single Phase Fault with Stuck Breaker on G22-007-TAP 115.00 (767120) 115 kV Bus a. Apply Fault at the G22-007-TAP 115.00 (767120) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-007-TAP (767120) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.2. G22-007-TAP (767120) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0581 | Single Phase Fault with Stuck Breaker on G22-013-TAP 345.00 (767240) 345 kV Bus a. Apply Fault at the G22-013-TAP 345.00 (767240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-013-TAP (767240) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G22-013-TAP (767240) 345.0 kV to GEN-2022-013 (767241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0582 | Single Phase Fault with Stuck Breaker on G22-015-TAP 345.00 (767280) 345 kV Bus a. Apply Fault at the G22-015-TAP 345.00 (767280) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. G22-015-TAP (767280) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0583 | Single Phase Fault with Stuck Breaker on G22-065-TAP 230.00 (768280) 230 kV Bus a. Apply Fault at the G22-065-TAP 230.00 (768280) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-065-TAP (768280) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. G22-065-TAP (768280) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0584 | Single Phase Fault with Stuck Breaker on G22-075-TAP 345.00 (768480) 345 kV Bus a. Apply Fault at the G22-075-TAP 345.00 (768480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-075-TAP (768480) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G22-075-TAP (768480) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0585 | Single Phase Fault with Stuck Breaker on G22-100-TAP 161.00 (768980) 161 kV Bus a. Apply Fault at the G22-100-TAP 161.00 (768980) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-100-TAP (768980) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. G22-100-TAP (768980) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0586 | Single Phase Fault with Stuck Breaker on G22-214-TAP 138.00 (771260) 138 kV Bus a. Apply Fault at the G22-214-TAP 138.00 (771260) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-214-TAP (771260) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 b.2. G22-214-TAP (771260) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0587 | Single Phase Fault with Stuck Breaker on 5BOONE 161.00 (300061) 161 kV Bus a. Apply Fault at the 5BOONE 161.00 (300061) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BOONE (300493) 69.0 kV to 5BOONE (300061) 161.0 kV Two Winding #1 b.2. 2BOONE (300493) 69.0 kV to 2DEERPK (300497) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0588 | Single Phase Fault with Stuck Breaker on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply Fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEORGE (300531) 69.0 kV to 2GEOGT2 (300530) 69.0 kV Transmission Circuit #1 b.2. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0589 | Single Phase Fault with Stuck Breaker on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply Fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 b.2. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0590 | Single Phase Fault with Stuck Breaker on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply Fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PLATCTY (300307) 69.0 kV to 5PLATCTY (301552) 161.0 kV Two Winding #1 b.2. 2PLATCTY (300307) 69.0 kV to 2HOOVER (300298) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0591 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.2. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0592 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 b.2. 5JASPER (300950) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0593 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0594 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0595 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0596 | Single Phase Fault with Stuck Breaker on COLBY 3 115.00 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 115.00 (530555) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0597 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0598 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0599 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0600 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0601 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LANG 7 (532769) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0602 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 7 (532770) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0603 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0604 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.2. NEOSHON4 (533022) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0605 | Single Phase Fault with Stuck Breaker on CANAL 4 138.00 (533033) 138 kV Bus a. Apply Fault at the CANAL 4 138.00 (533033) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANAL 4 (533033) 138.0 kV to BOEINGW4 (533055) 138.0 kV Transmission Circuit #1 b.2. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0606 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASOE4 (533059) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #z1 b.2. ELPASOE4 (533059) 138.0 kV to 47TH ST4 (533058) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0607 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 b.2. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0608 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 b.2. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0609 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 b.2. CRESWLS2 (533573) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0610 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 2 (533646) 69.0 kV to COALCRK2 (533633) 69.0 kV Transmission Circuit #1 b.2. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0611 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.2. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0612 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0613 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0614 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0615 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0616 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0617 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0618 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0619 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0620 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0621 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0622 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9B (999002) 13.8 kV Three Winding #2 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0623 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T1 9 (643017) 13.8 kV Three Winding #1 b.2. BEVERLY8 (640083) 69.0 kV to BEVERLY7 (640082) 115.0 kV to BEVERLY T2 9 (643018) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0624 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0625 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0626 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T1 9 (643099) 13.8 kV Three Winding #1 b.2. MCCOOK 8 (640270) 69.0 kV to MCCOOK 7 (640269) 115.0 kV to MCCOOK T3 9 (643100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0627 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO7 (640326) 115.0 kV to BEVERLY7 (640082) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0628 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD7 (640381) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0629 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0630 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT4 (532992) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0631 | Single Phase Fault with Stuck Breaker on SHERIDN2 69.000 (533841) 69 kV Bus a. Apply Fault at the SHERIDN2 69.000 (533841) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHERIDN2 (533841) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0632 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. HARPER 4 (539668) 138.0 kV to ANTHONY4 (539001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0633 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 b.2. SUB M (548815) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0634 | Single Phase Fault with Stuck Breaker on MCCOOK 7 115.00 (640269) 115 kV Bus a. Apply Fault at the MCCOOK 7 115.00 (640269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOK 7 (640269) 115.0 kV to CAMBRIG7 (640100) 115.0 kV Transmission Circuit #1 b.2. MCCOOK 7 (640269) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0635 | Single Phase Fault with Stuck Breaker on 7THOMHL 345.00 (300049) 345 kV Bus a. Apply Fault at the 7THOMHL 345.00 (300049) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7THOMHL (300049) 345.0 kV to 5THOMHLXF4 (301510) 161.0 kV Two Winding #4 b.2. 7THOMHL (300049) 345.0 kV to 5THOMHLXF3 (301506) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0636 | Single Phase Fault with Stuck Breaker on VSC2_3 345.00 (992003) 345 kV Bus a. Apply Fault at the VSC2_3 345.00 (992003) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VSC2_3 (992003) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 b.2. VSC2_3 (992003) 345.0 kV to VSC2_6 (992006) 276.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0637 | Single Phase Fault with Stuck Breaker on 5MLRSBGB1 161.00 (300519) 161 kV Bus a. Apply Fault at the 5MLRSBGB1 161.00 (300519) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MLRSBGB1 (300519) 161.0 kV to 5MLRSBGB2 (301498) 161.0 kV Transmission Circuit #z1 b.2. 5MLRSBGB1 (300519) 161.0 kV to 5BOONE (300061) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0638 | Single Phase Fault with Stuck Breaker on 5NORTONTP 161.00 (301567) 161 kV Bus a. Apply Fault at the 5NORTONTP 161.00 (301567) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NORTONTP (301567) 161.0 kV to 5GEORGE (300082) 161.0 kV Transmission Circuit #1 b.2. 5NORTONTP (301567) 161.0 kV to 5NORTON (300105) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0639 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0640 | Single Phase Fault with Stuck Breaker on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply Fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5LEVASY (300320) 161.0 kV to 5PITTSV (300110) 161.0 kV Transmission Circuit #1 b.2. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0641 | Single Phase Fault with Stuck Breaker on G20-072-TAP 161.00 (764355) 161 kV Bus a. Apply Fault at the G20-072-TAP 161.00 (764355) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-072-TAP (764355) 161.0 kV to 5SEDALA (300117) 161.0 kV Transmission Circuit #1 b.2. G20-072-TAP (764355) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0642 | Single Phase Fault with Stuck Breaker on 5MCBAINB2 161.00 (301489) 161 kV Bus a. Apply Fault at the 5MCBAINB2 161.00 (301489) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5MCBAINB2 (301489) 161.0 kV to 5MCBAINB1 (300501) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0643 | Single Phase Fault with Stuck Breaker on 2SYLVAN 69.000 (300545) 69 kV Bus a. Apply Fault at the 2SYLVAN 69.000 (300545) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SYLVAN (300545) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2SYLVAN (300545) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0644 | Single Phase Fault with Stuck Breaker on 2FORTNA 69.000 (300554) 69 kV Bus a. Apply Fault at the 2FORTNA 69.000 (300554) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2FORTNA (300554) 69.0 kV to 2CALIF (300550) 69.0 kV Transmission Circuit #1 b.2. 2FORTNA (300554) 69.0 kV to 2SYRACS (300564) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0645 | Single Phase Fault with Stuck Breaker on 2PRARIE 69.000 (300561) 69 kV Bus a. Apply Fault at the 2PRARIE 69.000 (300561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PRARIE (300561) 69.0 kV to 2CALIF (300550) 69.0 kV Transmission Circuit #1 b.2. 2PRARIE (300561) 69.0 kV to 2PILOTG (300560) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0646 | Single Phase Fault with Stuck Breaker on 2ST_MARTINS 69.000 (301442) 69 kV Bus a. Apply Fault at the 2ST_MARTINS 69.000 (301442) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ST_MARTINS (301442) 69.0 kV to 2CALIF (300550) 69.0 kV Transmission Circuit #1 b.2. 2ST_MARTINS (301442) 69.0 kV to 2SCRUGG (300637) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0647 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0648 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0649 | Single Phase Fault with Stuck Breaker on G18-128-TAP 345.00 (763421) 345 kV Bus a. Apply Fault at the G18-128-TAP 345.00 (763421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-128-TAP (763421) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. G18-128-TAP (763421) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0650 | Single Phase Fault with Stuck Breaker on GEN-2021-076345.00 (765990) 345 kV Bus a. Apply Fault at the GEN-2021-076345.00 (765990) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-076 (765990) 345.0 kV to G21-076-XFM1 (765994) 34.5 kV Two Winding #1 b.2. GEN-2021-076 (765990) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0651 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 7 (532773) 345.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0652 | Single Phase Fault with Stuck Breaker on CNTRLPL3 115.00 (531485) 115 kV Bus a. Apply Fault at the CNTRLPL3 115.00 (531485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CNTRLPL3 (531485) 115.0 kV to LEOTI 3 (531428) 115.0 kV Transmission Circuit #1 b.2. CNTRLPL3 (531485) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0653 | Single Phase Fault with Stuck Breaker on G19-030-TAP 345.00 (763677) 345 kV Bus a. Apply Fault at the G19-030-TAP 345.00 (763677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-030-TAP (763677) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G19-030-TAP (763677) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0654 | Single Phase Fault with Stuck Breaker on GEN-2021-107345.00 (766240) 345 kV Bus a. Apply Fault at the GEN-2021-107345.00 (766240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-107 (766240) 345.0 kV to G21-107-XFM1 (766244) 34.5 kV Two Winding #1 b.2. GEN-2021-107 (766240) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0655 | Single Phase Fault with Stuck Breaker on G16-111-TAP 345.00 (587884) 345 kV Bus a. Apply Fault at the G16-111-TAP 345.00 (587884) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-111-TAP (587884) 345.0 kV to RENO 7 (532771) 345.0 kV Transmission Circuit #1 b.2. G16-111-TAP (587884) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0656 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0657 | Single Phase Fault with Stuck Breaker on GEN-2017-220345.00 (760284) 345 kV Bus a. Apply Fault at the GEN-2017-220345.00 (760284) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-220 (760284) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-220 (760284) 345.0 kV to G17-220-XFM1 (760285) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0658 | Single Phase Fault with Stuck Breaker on G21-096-TAP 345.00 (766141) 345 kV Bus a. Apply Fault at the G21-096-TAP 345.00 (766141) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G21-096-TAP (766141) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. G21-096-TAP (766141) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0659 | Single Phase Fault with Stuck Breaker on GEN-2018-032345.00 (762680) 345 kV Bus a. Apply Fault at the GEN-2018-032345.00 (762680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-032 (762680) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-032 (762680) 345.0 kV to G18-032XFM1 (762681) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0660 | Single Phase Fault with Stuck Breaker on GEN-2021-006345.00 (765350) 345 kV Bus a. Apply Fault at the GEN-2021-006345.00 (765350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-006 (765350) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-006 (765350) 345.0 kV to G21-006-XFM2 (765357) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0661 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583859) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583859) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583859) 345.0 kV to BURNS 7 (532803) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583859) 345.0 kV to GEN-2014-001 (583850) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0662 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. UNIONRG6 (532874) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0663 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0664 | Single Phase Fault with Stuck Breaker on G19-054-TAP 230.00 (763862) 230 kV Bus a. Apply Fault at the G19-054-TAP 230.00 (763862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G19-054-TAP (763862) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. G19-054-TAP (763862) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0665 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 b.2. NEOSHOS2 (533778) 69.0 kV to BAKER 2 (532926) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0666 | Single Phase Fault with Stuck Breaker on G17-005-TAP 161.00 (588504) 161 kV Bus a. Apply Fault at the G17-005-TAP 161.00 (588504) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-005-TAP (588504) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. G17-005-TAP (588504) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0667 | Single Phase Fault with Stuck Breaker on G20-079-TAP 161.00 (764310) 161 kV Bus a. Apply Fault at the G20-079-TAP 161.00 (764310) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-079-TAP (764310) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. G20-079-TAP (764310) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0668 | Single Phase Fault with Stuck Breaker on GEN-2022-006161.00 (767101) 161 kV Bus a. Apply Fault at the GEN-2022-006161.00 (767101) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-006 (767101) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. GEN-2022-006 (767101) 161.0 kV to G22-006XFMR1 (767102) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0669 | Single Phase Fault with Stuck Breaker on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply Fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SC10BEL4 (533063) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. SC10BEL4 (533063) 138.0 kV to FARBER 4 (533042) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0670 | Single Phase Fault with Stuck Breaker on GEN-2017-121138.00 (761838) 138 kV Bus a. Apply Fault at the GEN-2017-121138.00 (761838) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-121 (761838) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. GEN-2017-121 (761838) 138.0 kV to G17-121XFM2 (761842) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0671 | Single Phase Fault with Stuck Breaker on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply Fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TAYLOR 4 (533006) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. TAYLOR 4 (533006) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0672 | Single Phase Fault with Stuck Breaker on SG12COL4 138.00 (533065) 138 kV Bus a. Apply Fault at the SG12COL4 138.00 (533065) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SG12COL4 (533065) 138.0 kV to EVANS N4 (533040) 138.0 kV Transmission Circuit #1 b.2. SG12COL4 (533065) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0673 | Single Phase Fault with Stuck Breaker on WACO N 4 138.00 (533073) 138 kV Bus a. Apply Fault at the WACO N 4 138.00 (533073) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WACO N 4 (533073) 138.0 kV to CENTENN4 (533034) 138.0 kV Transmission Circuit #1 b.2. WACO N 4 (533073) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0674 | Single Phase Fault with Stuck Breaker on MAIZE 4 138.00 (533054) 138 kV Bus a. Apply Fault at the MAIZE 4 138.00 (533054) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAIZE 4 (533054) 138.0 kV to EVANS N4 (533040) 138.0 kV Transmission Circuit #1 b.2. MAIZE 4 (533054) 138.0 kV to CHISHLM4 (533035) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0675 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 45TH ST4 (533074) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #1 b.2. 45TH ST4 (533074) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0676 | Single Phase Fault with Stuck Breaker on STEARMN4 138.00 (533068) 138 kV Bus a. Apply Fault at the STEARMN4 138.00 (533068) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEARMN4 (533068) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.2. STEARMN4 (533068) 138.0 kV to BOEINGE4 (533030) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0677 | Single Phase Fault with Stuck Breaker on GEN-2017-226138.00 (760641) 138 kV Bus a. Apply Fault at the GEN-2017-226138.00 (760641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-226 (760641) 138.0 kV to G17-226XFMR1 (760642) 34.5 kV Two Winding #1 b.2. GEN-2017-226 (760641) 138.0 kV to G17-227XFMR1 (760662) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0678 | Single Phase Fault with Stuck Breaker on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply Fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKERDG4 (533053) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #1 b.2. LAKERDG4 (533053) 138.0 kV to HOOVERN4 (533049) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0679 | Single Phase Fault with Stuck Breaker on INTERST4 138.00 (533051) 138 kV Bus a. Apply Fault at the INTERST4 138.00 (533051) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTERST4 (533051) 138.0 kV to GILL E 4 (533044) 138.0 kV Transmission Circuit #1 b.2. INTERST4 (533051) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0680 | Single Phase Fault with Stuck Breaker on GEN-2022-004138.00 (767061) 138 kV Bus a. Apply Fault at the GEN-2022-004138.00 (767061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-004 (767061) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #1 b.2. GEN-2022-004 (767061) 138.0 kV to G22-004XFMR1 (767062) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0681 | Single Phase Fault with Stuck Breaker on 64TH 4 138.00 (533066) 138 kV Bus a. Apply Fault at the 64TH 4 138.00 (533066) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 64TH 4 (533066) 138.0 kV to 47TH ST4 (533058) 138.0 kV Transmission Circuit #1 b.2. 64TH 4 (533066) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0682 | Single Phase Fault with Stuck Breaker on SCRANTN3 115.00 (533173) 115 kV Bus a. Apply Fault at the SCRANTN3 115.00 (533173) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCRANTN3 (533173) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 b.2. SCRANTN3 (533173) 115.0 kV to 4CORNER3 (533158) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0683 | Single Phase Fault with Stuck Breaker on FLORENC3 115.00 (533366) 115 kV Bus a. Apply Fault at the FLORENC3 115.00 (533366) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLORENC3 (533366) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0684 | Single Phase Fault with Stuck Breaker on GREEN 2 69.000 (533636) 69 kV Bus a. Apply Fault at the GREEN 2 69.000 (533636) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREEN 2 (533636) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.2. GREEN 2 (533636) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0685 | Single Phase Fault with Stuck Breaker on MCKEE 2 69.000 (533640) 69 kV Bus a. Apply Fault at the MCKEE 2 69.000 (533640) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCKEE 2 (533640) 69.0 kV to MARMATN2 (533639) 69.0 kV Transmission Circuit #1 b.2. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0686 | Single Phase Fault with Stuck Breaker on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply Fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ZILAJCT2 (533654) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.2. ZILAJCT2 (533654) 69.0 kV to ALLEN 2 (533621) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0687 | Single Phase Fault with Stuck Breaker on PARSONS2 69.000 (533704) 69 kV Bus a. Apply Fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARSONS2 (533704) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 b.2. PARSONS2 (533704) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0688 | Single Phase Fault with Stuck Breaker on PECK 2 69.000 (533830) 69 kV Bus a. Apply Fault at the PECK 2 69.000 (533830) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECK 2 (533830) 69.0 kV to HAYSVJS2 (533802) 69.0 kV Transmission Circuit #1 b.2. PECK 2 (533830) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0689 | Single Phase Fault with Stuck Breaker on CANALN 2 69.000 (533790) 69 kV Bus a. Apply Fault at the CANALN 2 69.000 (533790) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANALN 2 (533790) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #z1 b.2. CANALN 2 (533790) 69.0 kV to WASSALL2 (533852) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0690 | Single Phase Fault with Stuck Breaker on RUTAN 2 69.000 (533838) 69 kV Bus a. Apply Fault at the RUTAN 2 69.000 (533838) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUTAN 2 (533838) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #1 b.2. RUTAN 2 (533838) 69.0 kV to GLENDAL2 (533797) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0691 | Single Phase Fault with Stuck Breaker on WESTLNK2 69.000 (533854) 69 kV Bus a. Apply Fault at the WESTLNK2 69.000 (533854) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTLNK2 (533854) 69.0 kV to COWSKIN2 (533788) 69.0 kV Transmission Circuit #1 b.2. WESTLNK2 (533854) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0692 | Single Phase Fault with Stuck Breaker on GODDTAP2 69.000 (533879) 69 kV Bus a. Apply Fault at the GODDTAP2 69.000 (533879) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GODDTAP2 (533879) 69.0 kV to COWSKIN2 (533788) 69.0 kV Transmission Circuit #1 b.2. GODDTAP2 (533879) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0693 | Single Phase Fault with Stuck Breaker on VULCTP 2 69.000 (533851) 69 kV Bus a. Apply Fault at the VULCTP 2 69.000 (533851) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VULCTP 2 (533851) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #1 b.2. VULCTP 2 (533851) 69.0 kV to LIN 2 (533812) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0694 | Single Phase Fault with Stuck Breaker on OATVILL2 69.000 (533825) 69 kV Bus a. Apply Fault at the OATVILL2 69.000 (533825) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OATVILL2 (533825) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. OATVILL2 (533825) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0695 | Single Phase Fault with Stuck Breaker on MIDLAND2 69.000 (533816) 69 kV Bus a. Apply Fault at the MIDLAND2 69.000 (533816) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDLAND2 (533816) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 b.2. MIDLAND2 (533816) 69.0 kV to HYDRJS2 (533810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0696 | Single Phase Fault with Stuck Breaker on VISTAPK2 69.000 (533849) 69 kV Bus a. Apply Fault at the VISTAPK2 69.000 (533849) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VISTAPK2 (533849) 69.0 kV to HOOVERN2 (533805) 69.0 kV Transmission Circuit #1 b.2. VISTAPK2 (533849) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0697 | Single Phase Fault with Stuck Breaker on WATER1 2 69.000 (533855) 69 kV Bus a. Apply Fault at the WATER1 2 69.000 (533855) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATER1 2 (533855) 69.0 kV to HOOVERN2 (533805) 69.0 kV Transmission Circuit #1 b.2. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0698 | Single Phase Fault with Stuck Breaker on TYLER 2 69.000 (533847) 69 kV Bus a. Apply Fault at the TYLER 2 69.000 (533847) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. TYLER 2 (533847) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0699 | Single Phase Fault with Stuck Breaker on WATER2 2 69.000 (533856) 69 kV Bus a. Apply Fault at the WATER2 2 69.000 (533856) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATER2 2 (533856) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 b.2. WATER2 2 (533856) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0700 | Single Phase Fault with Stuck Breaker on SG8CRAG2 69.000 (533873) 69 kV Bus a. Apply Fault at the SG8CRAG2 69.000 (533873) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SG8CRAG2 (533873) 69.0 kV to LIN 2 (533812) 69.0 kV Transmission Circuit #1 b.2. SG8CRAG2 (533873) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0701 | Single Phase Fault with Stuck Breaker on SENECA 2 69.000 (533839) 69 kV Bus a. Apply Fault at the SENECA 2 69.000 (533839) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SENECA 2 (533839) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 b.2. SENECA 2 (533839) 69.0 kV to OSAGE 2 (533827) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0702 | Single Phase Fault with Stuck Breaker on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply Fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROLLHLS3 (539643) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0703 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUSSELL3 (539701) 115.0 kV to ELLSWTP3 (539642) 115.0 kV Transmission Circuit #1 b.2. RUSSELL3 (539701) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0704 | Single Phase Fault with Stuck Breaker on 2ND-KS 3 115.00 (539689) 115 kV Bus a. Apply Fault at the 2ND-KS 3 115.00 (539689) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ND-KS 3 (539689) 115.0 kV to 24-FREY3 (539661) 115.0 kV Transmission Circuit #1 b.2. 2ND-KS 3 (539689) 115.0 kV to GBENDTP3 (539666) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0705 | Single Phase Fault with Stuck Breaker on SSTARTP3 115.00 (539763) 115 kV Bus a. Apply Fault at the SSTARTP3 115.00 (539763) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SSTARTP3 (539763) 115.0 kV to GRNBURG3 (539664) 115.0 kV Transmission Circuit #1 b.2. SSTARTP3 (539763) 115.0 kV to FORD 3 (539758) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0706 | Single Phase Fault with Stuck Breaker on GEN-2019-044115.00 (763758) 115 kV Bus a. Apply Fault at the GEN-2019-044115.00 (763758) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-044 (763758) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.2. GEN-2019-044 (763758) 115.0 kV to G19-044-XFM1 (763759) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0707 | Single Phase Fault with Stuck Breaker on GEN-2011-008345.00 (539840) 345 kV Bus a. Apply Fault at the GEN-2011-008345.00 (539840) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2011-008 (539840) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. GEN-2011-008 (539840) 345.0 kV to G-2011-008-3 (539857) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0708 | Single Phase Fault with Stuck Breaker on GEN-2019-058345.00 (763890) 345 kV Bus a. Apply Fault at the GEN-2019-058345.00 (763890) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2019-058 (763890) 345.0 kV to G19-058-XFM1 (763891) 34.5 kV Two Winding #1 b.2. GEN-2019-058 (763890) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0709 | Single Phase Fault with Stuck Breaker on GEN-2008-124345.00 (579480) 345 kV Bus a. Apply Fault at the GEN-2008-124345.00 (579480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2008-124 (579480) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. GEN-2008-124 (579480) 345.0 kV to G08-124XFMR1 (579481) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0710 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0711 | Single Phase Fault with Stuck Breaker on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply Fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCONGRS5 (541318) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 b.2. NCONGRS5 (541318) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0712 | Single Phase Fault with Stuck Breaker on WESTON 5 161.00 (541351) 161 kV Bus a. Apply Fault at the WESTON 5 161.00 (541351) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTON 5 (541351) 161.0 kV to IATAN5 (541350) 161.0 kV Transmission Circuit #1 b.2. WESTON 5 (541351) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0713 | Single Phase Fault with Stuck Breaker on OAKGRV 5 161.00 (541227) 161 kV Bus a. Apply Fault at the OAKGRV 5 161.00 (541227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKGRV 5 (541227) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 b.2. OAKGRV 5 (541227) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0714 | Single Phase Fault with Stuck Breaker on TIFFANY5 161.00 (543026) 161 kV Bus a. Apply Fault at the TIFFANY5 161.00 (543026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIFFANY5 (543026) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. TIFFANY5 (543026) 161.0 kV to WETHRBY5 (543017) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0715 | Single Phase Fault with Stuck Breaker on FRSTCRK5 161.00 (543039) 161 kV Bus a. Apply Fault at the FRSTCRK5 161.00 (543039) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRSTCRK5 (543039) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. FRSTCRK5 (543039) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0716 | Single Phase Fault with Stuck Breaker on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply Fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. ORRICK 5 (541244) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0717 | Single Phase Fault with Stuck Breaker on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply Fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LKWOOD 5 (541238) 161.0 kV to BLSPW 5 (541237) 161.0 kV Transmission Circuit #1 b.2. LKWOOD 5 (541238) 161.0 kV to RAYTOWN5 (541219) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0718 | Single Phase Fault with Stuck Breaker on NUCOR5 161.00 (541395) 161 kV Bus a. Apply Fault at the NUCOR5 161.00 (541395) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUCOR5 (541395) 161.0 kV to NUCOR_D1 (541396) 13.8 kV Two Winding #1 b.2. NUCOR5 (541395) 161.0 kV to NUCOR_S1 (541398) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0719 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0720 | Single Phase Fault with Stuck Breaker on WARSAWTP 69.000 (541281) 69 kV Bus a. Apply Fault at the WARSAWTP 69.000 (541281) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARSAWTP (541281) 69.0 kV to COLECMP2 (541276) 69.0 kV Transmission Circuit #1 b.2. WARSAWTP (541281) 69.0 kV to WARSAW 2 (541277) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0721 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0722 | Single Phase Fault with Stuck Breaker on GEN-2017-195345.00 (762279) 345 kV Bus a. Apply Fault at the GEN-2017-195345.00 (762279) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-195 (762279) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-195 (762279) 345.0 kV to G17-195XFM1 (762280) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0723 | Single Phase Fault with Stuck Breaker on HICKMAN5 161.00 (542994) 161 kV Bus a. Apply Fault at the HICKMAN5 161.00 (542994) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HICKMAN5 (542994) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. HICKMAN5 (542994) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0724 | Single Phase Fault with Stuck Breaker on ANTIOCH5 161.00 (543050) 161 kV Bus a. Apply Fault at the ANTIOCH5 161.00 (543050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. ANTIOCH5 (543050) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0725 | Single Phase Fault with Stuck Breaker on REDEL 5 161.00 (543053) 161 kV Bus a. Apply Fault at the REDEL 5 161.00 (543053) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDEL 5 (543053) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. REDEL 5 (543053) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0726 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0727 | Single Phase Fault with Stuck Breaker on G17-108-TAP 161.00 (761278) 161 kV Bus a. Apply Fault at the G17-108-TAP 161.00 (761278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-108-TAP (761278) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. G17-108-TAP (761278) 161.0 kV to GEN-2021-050 (765750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0728 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #z2 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0729 | Single Phase Fault with Stuck Breaker on G20-007-TAP 345.00 (766261) 345 kV Bus a. Apply Fault at the G20-007-TAP 345.00 (766261) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-007-TAP (766261) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. G20-007-TAP (766261) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0730 | Single Phase Fault with Stuck Breaker on TERRACE5 161.00 (542991) 161 kV Bus a. Apply Fault at the TERRACE5 161.00 (542991) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0731 | Single Phase Fault with Stuck Breaker on FOREST 5 161.00 (543001) 161 kV Bus a. Apply Fault at the FOREST 5 161.00 (543001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOREST 5 (543001) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. FOREST 5 (543001) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0732 | Single Phase Fault with Stuck Breaker on ROEPARK5 161.00 (543040) 161 kV Bus a. Apply Fault at the ROEPARK5 161.00 (543040) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROEPARK5 (543040) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 b.2. ROEPARK5 (543040) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0733 | Single Phase Fault with Stuck Breaker on WINJT N5 161.00 (543009) 161 kV Bus a. Apply Fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT N5 (543009) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT N5 (543009) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0734 | Single Phase Fault with Stuck Breaker on WINJT S5 161.00 (543010) 161 kV Bus a. Apply Fault at the WINJT S5 161.00 (543010) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT S5 (543010) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT S5 (543010) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0735 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NKANCTY5 (543018) 161.0 kV to AVONDAL5 (543015) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0736 | Single Phase Fault with Stuck Breaker on LINECRK5 161.00 (543025) 161 kV Bus a. Apply Fault at the LINECRK5 161.00 (543025) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LINECRK5 (543025) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 b.2. LINECRK5 (543025) 161.0 kV to RIVRSID5 (543021) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0737 | Single Phase Fault with Stuck Breaker on GEN-2022-073161.00 (768441) 161 kV Bus a. Apply Fault at the GEN-2022-073161.00 (768441) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-073 (768441) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. GEN-2022-073 (768441) 161.0 kV to G22-073XFMR1 (768442) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0738 | Single Phase Fault with Stuck Breaker on LAKCTY 2 69.000 (543092) 69 kV Bus a. Apply Fault at the LAKCTY 2 69.000 (543092) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTY 2 (543092) 69.0 kV to LAKCTYJ2 (543087) 69.0 kV Transmission Circuit #1 b.2. LAKCTY 2 (543092) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0739 | Single Phase Fault with Stuck Breaker on LAKCTYK2 69.000 (543093) 69 kV Bus a. Apply Fault at the LAKCTYK2 69.000 (543093) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKCTYK2 (543093) 69.0 kV to DUNCNRD2 (543091) 69.0 kV Transmission Circuit #1 b.2. LAKCTYK2 (543093) 69.0 kV to BLUSPRG2 (543088) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0740 | Single Phase Fault with Stuck Breaker on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply Fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 b.2. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0741 | Single Phase Fault with Stuck Breaker on GAT258 2 69.000 (547551) 69 kV Bus a. Apply Fault at the GAT258 2 69.000 (547551) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GAT258 2 (547551) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 b.2. GAT258 2 (547551) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0742 | Single Phase Fault with Stuck Breaker on JOP430 2 69.000 (547608) 69 kV Bus a. Apply Fault at the JOP430 2 69.000 (547608) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP430 2 (547608) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 b.2. JOP430 2 (547608) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0743 | Single Phase Fault with Stuck Breaker on GAL278T 69.000 (547728) 69 kV Bus a. Apply Fault at the GAL278T 69.000 (547728) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GAL278T (547728) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 b.2. GAL278T (547728) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0744 | Single Phase Fault with Stuck Breaker on RIV406 2 69.000 (547602) 69 kV Bus a. Apply Fault at the RIV406 2 69.000 (547602) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV406 2 (547602) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. RIV406 2 (547602) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0745 | Single Phase Fault with Stuck Breaker on SUB P 69.000 (548827) 69 kV Bus a. Apply Fault at the SUB P 69.000 (548827) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB P (548827) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB P (548827) 69.0 kV to SUB I (548800) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0746 | Single Phase Fault with Stuck Breaker on SUB R 69.000 (548830) 69 kV Bus a. Apply Fault at the SUB R 69.000 (548830) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB R (548830) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SUB R (548830) 69.0 kV to SUB K (548801) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0747 | Single Phase Fault with Stuck Breaker on GEN-2018-031161.00 (762669) 161 kV Bus a. Apply Fault at the GEN-2018-031161.00 (762669) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-031 (762669) 161.0 kV to G18-031XFM1 (762670) 34.5 kV Two Winding #1 b.2. GEN-2018-031 (762669) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0748 | Single Phase Fault with Stuck Breaker on G15052_1 345.00 (562900) 345 kV Bus a. Apply Fault at the G15052_1 345.00 (562900) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15052_1 (562900) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. G15052_1 (562900) 345.0 kV to G15052_2 (562901) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0749 | Single Phase Fault with Stuck Breaker on GEN-2016-046345.00 (587310) 345 kV Bus a. Apply Fault at the GEN-2016-046345.00 (587310) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-046 (587310) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-046 (587310) 345.0 kV to G16-046XFMR1 (587311) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0750 | Single Phase Fault with Stuck Breaker on GEN-2016-050345.00 (587350) 345 kV Bus a. Apply Fault at the GEN-2016-050345.00 (587350) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-050 (587350) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-050 (587350) 345.0 kV to G16-050XFMR1 (587351) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0751 | Single Phase Fault with Stuck Breaker on GEN-2017-086345.00 (589240) 345 kV Bus a. Apply Fault at the GEN-2017-086345.00 (589240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-086 (589240) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-086 (589240) 345.0 kV to G17-086XFMR1 (589241) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0752 | Single Phase Fault with Stuck Breaker on GEN-2020-011345.00 (764420) 345 kV Bus a. Apply Fault at the GEN-2020-011345.00 (764420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-011 (764420) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-011 (764420) 345.0 kV to G20-011-SS3 (764433) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0753 | Single Phase Fault with Stuck Breaker on G18-125-TAP 345.00 (763410) 345 kV Bus a. Apply Fault at the G18-125-TAP 345.00 (763410) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0754 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0755 | Single Phase Fault with Stuck Breaker on GEN-2022-054345.00 (768061) 345 kV Bus a. Apply Fault at the GEN-2022-054345.00 (768061) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-054 (768061) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-054 (768061) 345.0 kV to G22-054XFMR1 (768062) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0756 | Single Phase Fault with Stuck Breaker on GEN-2021-030345.00 (765580) 345 kV Bus a. Apply Fault at the GEN-2021-030345.00 (765580) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-030 (765580) 345.0 kV to G21-029-TAP (765571) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-030 (765580) 345.0 kV to G21-030-XFM1 (765584) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0757 | Single Phase Fault with Stuck Breaker on GEN-2021-069345.00 (765920) 345 kV Bus a. Apply Fault at the GEN-2021-069345.00 (765920) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-069 (765920) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-069 (765920) 345.0 kV to G21-069-XFM1 (765924) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0758 | Single Phase Fault with Stuck Breaker on GEN-2021-070345.00 (765930) 345 kV Bus a. Apply Fault at the GEN-2021-070345.00 (765930) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-070 (765930) 345.0 kV to G21-068-TAP (765911) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-070 (765930) 345.0 kV to G21-070-XFM1 (765934) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0759 | Single Phase Fault with Stuck Breaker on GEN-2022-007115.00 (767121) 115 kV Bus a. Apply Fault at the GEN-2022-007115.00 (767121) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-007 (767121) 115.0 kV to G22-007-TAP (767120) 115.0 kV Transmission Circuit #1 b.2. GEN-2022-007 (767121) 115.0 kV to G22-007XFMR1 (767122) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0760 | Single Phase Fault with Stuck Breaker on GEN-2022-013345.00 (767241) 345 kV Bus a. Apply Fault at the GEN-2022-013345.00 (767241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-013 (767241) 345.0 kV to G22-013-TAP (767240) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-013 (767241) 345.0 kV to G22-013XFMR1 (767242) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0761 | Single Phase Fault with Stuck Breaker on GEN-2022-015345.00 (767281) 345 kV Bus a. Apply Fault at the GEN-2022-015345.00 (767281) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-015 (767281) 345.0 kV to G22-015-TAP (767280) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-015 (767281) 345.0 kV to G22-015XFMR1 (767282) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0762 | Single Phase Fault with Stuck Breaker on GEN-2022-065230.00 (768281) 230 kV Bus a. Apply Fault at the GEN-2022-065230.00 (768281) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-065 (768281) 230.0 kV to G22-065-TAP (768280) 230.0 kV Transmission Circuit #1 b.2. GEN-2022-065 (768281) 230.0 kV to G22-065XFMR1 (768282) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0763 | Single Phase Fault with Stuck Breaker on GEN-2022-075345.00 (768481) 345 kV Bus a. Apply Fault at the GEN-2022-075345.00 (768481) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-075 (768481) 345.0 kV to G22-075-TAP (768480) 345.0 kV Transmission Circuit #1 b.2. GEN-2022-075 (768481) 345.0 kV to G22-075XFMR1 (768482) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0764 | Single Phase Fault with Stuck Breaker on GEN-2022-214138.00 (771261) 138 kV Bus a. Apply Fault at the GEN-2022-214138.00 (771261) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2022-214 (771261) 138.0 kV to G22-214-TAP (771260) 138.0 kV Transmission Circuit #1 b.2. GEN-2022-214 (771261) 138.0 kV to G22-214XFMR1 (771262) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0765 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 b.2. MIAMI 2 (512630) 69.0 kV to MIAMI 5 (512631) 161.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0766 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to CHOUTEAUCRK5 (513570) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0767 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.2. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0768 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 b.2. HEIZER 2 (530563) 69.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0769 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 7 (531465) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0770 | Single Phase Fault with Stuck Breaker on JEC 6 230.00 (532852) 230 kV Bus a. Apply Fault at the JEC 6 230.00 (532852) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0771 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to RENO 7 (532771) 345.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 b.2. RENO 3 (533416) 115.0 kV to RENO 7 (532771) 345.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0772 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR3 (533268) 115.0 kV to STRANGR7 (532772) 345.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR3 (533268) 115.0 kV to STRANGR7 (532772) 345.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0773 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0774 | Single Phase Fault with Stuck Breaker on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0775 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK3 (533315) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #2 b.2. OTTRCRK3 (533315) 115.0 kV to OTTRCRK4 (532997) 138.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0776 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELPASO 2 (533793) 69.0 kV to ELPASOE4 (533059) 138.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 b.2. ELPASO 2 (533793) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0777 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0778 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0779 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to PHILL 7 (541200) 345.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0780 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 5 (541202) 161.0 kV to SIBLEY 7 (541201) 345.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0781 | Single Phase Fault with Stuck Breaker on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply Fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. DUNCAN 5 (541235) 161.0 kV to BLSPE 5 (541205) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0782 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0783 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. WGARDNR5 (542966) 161.0 kV to W.GRDNR7 (542965) 345.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0784 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTH 7 (542972) 345.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTHN5 (543665) 161.0 kV to HAWTH 7 (542972) 345.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0785 | Single Phase Fault with Stuck Breaker on LAC3_STAR7 345.00 (543667) 345 kV Bus a. Apply Fault at the LAC3_STAR7 345.00 (543667) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC3_STAR7 (543667) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h b.2. LAC3_STAR7 (543667) 345.0 kV to LAC3_Y1 (543662) 6.9 kV Two Winding #y | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0786 | Single Phase Fault with Stuck Breaker on LAC8_STAR7 345.00 (543669) 345 kV Bus a. Apply Fault at the LAC8_STAR7 345.00 (543669) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC8_STAR7 (543669) 345.0 kV to LAC8_Z1 (543672) 4.0 kV Two Winding #z b.2. LAC8_STAR7 (543669) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0787 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 2 (547534) 69.0 kV to ORO110 5 (547467) 161.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 b.2. ORO110 2 (547534) 69.0 kV to WEB436 2 (547527) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0788 | Single Phase Fault with Stuck Breaker on JOP389 2 69.000 (547592) 69 kV Bus a. Apply Fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 b.2. JOP389 2 (547592) 69.0 kV to EXP449T2 (547438) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0789 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 4 (547486) 138.0 kV to VINTAJC4 (510417) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0790 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 2 (547601) 69.0 kV to HOC404 5 (547487) 161.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 b.2. HOC404 2 (547601) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0791 | Single Phase Fault with Stuck Breaker on BEVERLY7 115.00 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 115.00 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 b.2. BEVERLY7 (640082) 115.0 kV to ENDERS 7 (640167) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0792 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 b.2. KEYSTON3 (640252) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0793 | Single Phase Fault with Stuck Breaker on STOCKVL7 115.00 (640365) 115 kV Bus a. Apply Fault at the STOCKVL7 115.00 (640365) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STOCKVL7 (640365) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.2. STOCKVL7 (640365) 115.0 kV to REDWILO7 (640326) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0794 | Single Phase Fault with Stuck Breaker on GILL E 2 (533795) 69 kV Bus a. Apply Fault at the GILL E 2 (533795) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0795 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0796 | Single Phase Fault with Stuck Breaker on GILL W 2 (533796) 69 kV Bus a. Apply Fault at the GILL W 2 (533796) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL W 2 (533796) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0797 | Single Phase Fault with Stuck Breaker on HOOVERS2 (533806) 69 kV Bus a. Apply Fault at the HOOVERS2 (533806) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HOOVERS2 (533806) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0798 | Single Phase Fault with Stuck Breaker on GILL E 4 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 (533044) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0799 | Single Phase Fault with Stuck Breaker on COWSKIN4 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 (533038) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0800 | Single Phase Fault with Stuck Breaker on HOOVERN4 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 (533049) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0801 | Single Phase Fault with Stuck Breaker on ALTOO E2 (533673) 69 kV Bus a. Apply Fault at the ALTOO E2 (533673) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. ALTOO E2 (533673) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0802 | Single Phase Fault with Stuck Breaker on NEOSHON2 (533768) 69 kV Bus a. Apply Fault at the NEOSHON2 (533768) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHON2 (533768) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0803 | Single Phase Fault with Stuck Breaker on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0804 | Single Phase Fault with Stuck Breaker on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0805 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0806 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0807 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0808 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0809 | Single Phase Fault with Stuck Breaker on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0810 | Single Phase Fault with Stuck Breaker on OSAGE J3 (533171) 115 kV Bus a. Apply Fault at the OSAGE J3 (533171) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. OSAGE J3 (533171) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0811 | Single Phase Fault with Stuck Breaker on WEMPORI3 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 (533309) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0812 | Single Phase Fault with Stuck Breaker on MORRIS 7 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 (532770) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MORRIS 7 (532770) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0813 | Single Phase Fault with Stuck Breaker on STILWEL5 (542969) 161 kV Bus a. Apply Fault at the STILWEL5 (542969) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0814 | Single Phase Fault with Stuck Breaker on REDWILO7 (640326) 115 kV Bus a. Apply Fault at the REDWILO7 (640326) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0815 | Single Phase Fault with Stuck Breaker on GENTLMN4 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 (640184) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0816 | Single Phase Fault with Stuck Breaker on SETAB 3 (531464) 115 kV Bus a. Apply Fault at the SETAB 3 (531464) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SETAB 3 (531464) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0817 | Single Phase Fault with Stuck Breaker on MINGO 3 (531429) 115 kV Bus a. Apply Fault at the MINGO 3 (531429) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0818 | Single Phase Fault with Stuck Breaker on SPEARVL3 (539694) 115 kV Bus a. Apply Fault at the SPEARVL3 (539694) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SPEARVL3 (539694) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0819 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0820 | Single Phase Fault with Stuck Breaker on NFTDODG3 (539771) 115 kV Bus a. Apply Fault at the NFTDODG3 (539771) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NFTDODG3 (539771) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0821 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0822 | Single Phase Fault with Stuck Breaker on NASHUA 5 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 (541203) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0823 | Single Phase Fault with Stuck Breaker on PLTCTY 5 (541221) 161 kV Bus a. Apply Fault at the PLTCTY 5 (541221) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. PLTCTY 5 (541221) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0824 | Single Phase Fault with Stuck Breaker on GLADSTN5 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 (543016) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0825 | Single Phase Fault with Stuck Breaker on TWA 5 (541214) 161 kV Bus a. Apply Fault at the TWA 5 (541214) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0826 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0827 | Single Phase Fault with Stuck Breaker on SEDN 2 (541271) 69 kV Bus a. Apply Fault at the SEDN 2 (541271) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SEDN 2 (541271) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0828 | Single Phase Fault with Stuck Breaker on SEDPLT 2 (541275) 69 kV Bus a. Apply Fault at the SEDPLT 2 (541275) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SEDPLT 2 (541275) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0829 | Single Phase Fault with Stuck Breaker on 5GEORGE (300082) 161 kV Bus a. Apply Fault at the 5GEORGE (300082) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. 5GEORGE (300082) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0830 | Single Phase Fault with Stuck Breaker on 5CALIF UE 2 (344234) 161 kV Bus a. Apply Fault at the 5CALIF UE 2 (344234) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. 5CALIF UE 2 (344234) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0831 | Single Phase Fault with Stuck Breaker on 5MCBAIN T (345071) 161 kV Bus a. Apply Fault at the 5MCBAIN T (345071) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. 5MCBAIN T (345071) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0832 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0833 | Single Phase Fault with Stuck Breaker on FRSTCRK5 (543039) 161 kV Bus a. Apply Fault at the FRSTCRK5 (543039) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. FRSTCRK5 (543039) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0834 | Single Phase Fault with Stuck Breaker on SMTHVL 5 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 (541204) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0835 | Single Phase Fault with Stuck Breaker on BLSPE 5 (541205) 161 kV Bus a. Apply Fault at the BLSPE 5 (541205) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BLSPE 5 (541205) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0836 | Single Phase Fault with Stuck Breaker on NEASTS5 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 (542985) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0837 | Single Phase Fault with Stuck Breaker on GRAND W5 (542988) 161 kV Bus a. Apply Fault at the GRAND W5 (542988) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GRAND W5 (542988) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0838 | Single Phase Fault with Stuck Breaker on NAVY 5 (542989) 161 kV Bus a. Apply Fault at the NAVY 5 (542989) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. NAVY 5 (542989) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0839 | Single Phase Fault with Stuck Breaker on AVONDAL5 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 (543015) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0840 | Single Phase Fault with Stuck Breaker on SUB J (548811) 69 kV Bus a. Apply Fault at the SUB J (548811) 69 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SUB J (548811) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0841 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0842 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0843 | Single Phase Fault with Stuck Breaker on LANG 3 (533304) 115 kV Bus a. Apply Fault at the LANG 3 (533304) 115 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. LANG 3 (533304) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0844 | Single Phase Fault with Stuck Breaker on EVANS N4 (533040) 138 kV Bus a. Apply Fault at the EVANS N4 (533040) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0845 | Single Phase Fault with Stuck Breaker on EVANS S4 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 (533041) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0846 | Single Phase Fault with Stuck Breaker on MILAN_GOAB (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB (539008) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0847 | Single Phase Fault with Stuck Breaker on SUMNER 4 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 (532984) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0848 | Single Phase Fault with Stuck Breaker on GILL W 4 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 (533045) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL W 4 (533045) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT_0849 | Single Phase Fault with Stuck Breaker on GILL S 4 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 (533046) 138 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. GILL S 4 (533046) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0012 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0013 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0014 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0015 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0016 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0017 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0018 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0019 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0020 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0021 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0022 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0023 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0024 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0025 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0026 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0027 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0028 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0029 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0030 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0031 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0032 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G22-015-TAP (767280) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0033 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0034 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0035 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0036 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0037 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0038 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0039 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0040 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0041 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0042 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0043 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0044 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0045 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0046 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT_0047 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0001 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0002 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0003 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0004 | Single Phase Fault with Stuck Breaker on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA17-1 (512688) 22.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0005 | Single Phase Fault with Stuck Breaker on GREC TAP7 (512865) 345 kV Bus a. Apply Fault at the GREC TAP7 (512865) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRECSTG_1 (512615) 21.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0006 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0007 | Single Phase Fault with Stuck Breaker on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0008 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_GRDA_FAULT_0009 | Single Phase Fault with Stuck Breaker on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_OKGE_FAULT_0001 | Single Phase Fault with Stuck Breaker on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.3. KAYWNDG1 (515651) 0.7 kV to Generator #1 b.4. KAYWNDG2 (515652) 0.7 kV to Generator #1 b.5. KAYWND11 (515622) 34.5 kV to Load #S1 b.6. KAYWND12 (515623) 34.5 kV to Load #S1 b.7. KAYWIND7 (514825) 345.0 kV to remove bus # b.8. KAYWNDT1 (515619) 12.5 kV to remove bus # b.9. KAYWNDT2 (515620) 12.5 kV to remove bus # b.10. OPENSKY7 (515621) 345.0 kV to remove bus # b.11. KAYWND11 (515622) 34.5 kV to remove bus # b.12. KAYWND12 (515623) 34.5 kV to remove bus # b.13. KAYWNDG1 (515651) 0.7 kV to remove bus # b.14. KAYWNDG2 (515652) 0.7 kV to remove bus # b.15. KAYWNDC1 (515653) 34.5 kV to remove bus # b.16. KAYWNDC2 (515654) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_SPS_FAULT_0001 | Single Phase Fault with Stuck Breaker on FINNEY (523853) 345 kV Bus a. Apply Fault at the FINNEY (523853) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. FINNEY 7 (523853) 345.0 kV to remove bus # b.4. LAMAR7 (599950) 345.0 kV to remove bus # b.5. LAMAR 6 (599951) 345.0 kV to remove bus # b.6. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # b.7. BUFF_DN_TR11 (523114) 13.2 kV to remove bus # b.8. BUFF_DN_TR21 (523115) 13.2 kV to remove bus # b.9. BUFF_DUNES11 (523116) 34.5 kV to remove bus # b.10. BUFF_DUNES21 (523117) 34.5 kV to remove bus # b.11. BUFF_DUNES23 (523061) 0.7 kV to Generator #1 b.12. BUFF_DUNES13 (523062) 0.7 kV to Generator #1 b.13. BUFF_DUNES23 (523061) 0.7 kV to remove bus # b.14. BUFF_DUNES13 (523062) 0.7 kV to remove bus # b.15. BUFF_DUNES22 (523063) 34.5 kV to remove bus # b.16. BUFF_DUNES12 (523064) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_0001 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_0002 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.3. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 b.4. SHAWNEE5 (543041) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.5. SHAWNEE5 (543041) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_KACY_FAULT_0003 | Single Phase Fault with Stuck Breaker on BARBER 5 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 (546651) 161 kV Bus b. Clear Fault after 9 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 b.2. BARBER 5 (546651) 161.0 kV to ROSEDALE 5 (546222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EDE_FAULT_0001 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.2. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.3. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. JOP389 5 (547483) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.7. TIP292 5 (547472) 161.0 kV to Load #1 b.8. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EDE_FAULT_0002 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 7 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Breaker at To Bus #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EDE_FAULT_0003 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 b.3. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EDE_FAULT_0004 | Single Phase Fault with Stuck Breaker on TIP292 5 161.00 (547472) 161 kV Bus a. Apply Fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 b.3. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.4. RNM393 5 (547500) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.5. MON383 5 (547480) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 b.6. TIP292 5 (547472) 161.0 kV to Load #1 b.7. TIP292 5 (547472) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_NPPD_FAULT_0001 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_NPPD_FAULT_0002 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_NPPD_FAULT_0003 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 13.5 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.4. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_NPPD_FAULT_0004 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. G18-125-TAP (763410) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_SUNC_FAULT_0001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_0001 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_0002 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.4. SUB M-161 (548814) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_0003 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_0004 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_0005 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_0006 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_0007 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_0008 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.4. BLUMILS5 (543004) 161.0 kV to Load #1 b.5. BLUMILS_TER1 (543117) 12.5 kV to Load #3 b.6. BLUMILS5 (543004) 161.0 kV to remove bus # b.7. BLUEMLS2 (543116) 69.0 kV to remove bus # b.8. BLUMILS_TER1 (543117) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_0009 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_INDN_FAULT_0010 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Transmission Circuit #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0001 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.4. CLBYT1 1 (530645) 13.8 kV to remove bus # b.5. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Load #99 b.12. COLBY 3 (530555) 115.0 kV to Generator #C8 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0002 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. CLBYT1 1 (530645) 13.8 kV to remove bus # b.6. COLBY 3 (530555) 115.0 kV to Generator #C3 b.7. COLBY 3 (530555) 115.0 kV to Generator #C4 b.8. COLBY 3 (530555) 115.0 kV to Generator #C5 b.9. COLBY 3 (530555) 115.0 kV to Generator #C6 b.10. COLBY 3 (530555) 115.0 kV to Generator #C7 b.11. COLBY 3 (530555) 115.0 kV to Generator #C8 b.12. COLBY 3 (530555) 115.0 kV to Load #99 b.13. COLBY 3 (530555) 115.0 kV to Load #1 b.14. COLBY 3 (530555) 115.0 kV to Load #CC | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0003 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0004 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0005 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. REDLIN 3 (530605) 115.0 kV to Load #71 b.6. REDLIN 3 (530605) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0006 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.4. GMECG1 1 (530674) 13.8 kV to remove bus # b.5. GMECG2 1 (530675) 13.8 kV to remove bus # b.6. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0007 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMECG1 1 (530674) 13.8 kV to remove bus # b.3. GMECG2 1 (530675) 13.8 kV to remove bus # b.5. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.6. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.7. N HAYS3 (530581) 115.0 kV to remove bus # b.8. VINETAP3 (530693) 115.0 kV to remove bus # b.9. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0008 | Single Phase Fault with Stuck Breaker on KNOLL 3 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 (530561) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. N HAYS3 (530581) 115.0 kV to remove bus # b.4. VINETAP3 (530693) 115.0 kV to remove bus # b.5. GMECG1 1 (530674) 13.8 kV to remove bus # b.6. GMECG2 1 (530675) 13.8 kV to remove bus # b.7. GMEC 3 (530676) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0009 | Single Phase Fault with Stuck Breaker on S HAYS 3 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 (530553) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. ANGUS 3 (530714) 115.0 kV to GORHAM 3 (530552) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.5. ANGUS 3 (530714) 115.0 kV to Load #1 b.6. PFEIFER 3 (530725) 115.0 kV to Load #1 b.7. ANGUS 3 (530714) 115.0 kV to remove bus # b.8. PFEIFER 3 (530725) 115.0 kV to remove bus # b.9. GORHAM 3 (530552) 115.0 kV to Load #1 b.10. RUSLPMP3 (530684) 115.0 kV to Load #1 b.11. GORHAM 3 (530552) 115.0 kV to remove bus # b.12. RUSLPMP3 (530684) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0010 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0011 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0012 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0013 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0014 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0015 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.4. BUCKE_WTG (530705) 0.7 kV to remove bus # b.5. BUCKW_WTG (530708) 0.7 kV to remove bus # b.6. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.7. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.8. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.9. BUCKW_TERT (530706) 13.8 kV to remove bus # b.10. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.11. BUCKE_TERT (530709) 13.8 kV to remove bus # b.12. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0016 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0017 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0018 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0019 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0020 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 12 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0021 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0022 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0023 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0024 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. SMOKYHL6 (530592) 230.0 kV to SMKYP2 6 (530599) 230.0 kV Transmission Circuit #1 b.4. SHG2 34 1 (530715) 34.5 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus # b.6. SMKYP2 6 (530599) 230.0 kV to remove bus # b.7. SHP234 1 (530604) 34.5 kV to remove bus # b.8. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0025 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 38 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus # b.3. SMKYP1 6 (530593) 230.0 kV to remove bus # b.4. SMKYP1G1 (530594) 0.7 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus # b.6. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0026 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 14 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 b.3. SMKYT2 1 (530634) 13.9 kV to Generator #1 b.4. SMKYT2 1 (530634) 13.9 kV to remove bus # b.5. SMKYP1G1 (530594) 0.7 kV to remove bus # b.6. SMKYP1 6 (530593) 230.0 kV to remove bus # b.7. SHP134 1 (530595) 34.5 kV to remove bus # b.8. SMKYT1 1 (530633) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0027 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. SMKYP2 6 (530599) 230.0 kV to remove bus # b.3. SMKYP1 6 (530593) 230.0 kV to remove bus # b.4. SMKYP1G1 (530594) 0.7 kV to remove bus # b.5. SMKYP2G1 (530600) 0.6 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.7. SHG2 34 1 (530715) 34.5 kV to remove bus # b.8. SMOKYHL6 (530592) 230.0 kV to remove bus # b.9. SHP134 1 (530595) 34.5 kV to remove bus # b.10. SHP234 1 (530604) 34.5 kV to remove bus # b.11. SMKYT1 1 (530633) 13.2 kV to remove bus # b.12. SMKYT2 1 (530634) 13.9 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0028 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0029 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0030 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0031 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0032 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.3. LACROS 3 (530603) 115.0 kV to remove bus # b.4. NEKOMA 3 (530608) 115.0 kV to remove bus # b.5. ALXNDR 3 (530606) 115.0 kV to remove bus # b.7. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 b.8. HZRNGPL3 (530609) 115.0 kV to remove bus # b.9. ALEXNDR1 (539702) 34.5 kV to Load #1 b.10. LAXTAP 3 (530602) 115.0 kV to remove bus # b.11. NKMA2 1 (530630) 12.5 kV to remove bus # b.12. ALEXNDR1 (539702) 34.5 kV to remove bus # b.13. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0033 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0034 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.4. LACROS 3 (530603) 115.0 kV to remove bus # b.5. NEKOMA 3 (530608) 115.0 kV to remove bus # b.6. ALXNDR 3 (530606) 115.0 kV to remove bus # b.8. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.9. ALEXNDR1 (539702) 34.5 kV to Load #1 b.10. LAXTAP 3 (530602) 115.0 kV to remove bus # b.11. NKMA2 1 (530630) 12.5 kV to remove bus # b.12. ALEXNDR1 (539702) 34.5 kV to remove bus # b.13. ALEXND-T (539902) 12.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0035 | Single Phase Fault with Stuck Breaker on HEIZER 3 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 (530601) 115 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0036 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. RICE 3 (530623) 115.0 kV to RICE 6 (530686) 230.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.2. RICE 6 (530686) 230.0 kV to remove bus # b.3. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. PRWINDG1 (530690) 0.7 kV to Generator #1 b.6. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.7. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.8. PRWINDG1 (530690) 0.7 kV to remove bus # b.9. BUFCRKT11 (530691) 12.5 kV to remove bus # b.10. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0037 | Single Phase Fault with Stuck Breaker on CIRCLE 6 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 (532871) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0038 | Single Phase Fault with Stuck Breaker on RICE 6 (530686) 230 kV Bus a. Apply Fault at the RICE 6 (530686) 230 kV Bus b. Clear Fault after 15 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to RICE 6 (530686) 230.0 kV Transmission Circuit #1 b.2. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.3. PRWINDG1 (530690) 0.7 kV to Generator #1 b.4. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.5. BUFLOCRK6 (530688) 230.0 kV to remove bus # b.6. BUFLOCRK1 (530689) 34.5 kV to remove bus # b.7. PRWINDG1 (530690) 0.7 kV to remove bus # b.8. BUFCRKT11 (530691) 12.5 kV to remove bus # b.9. PRWNDCL1 (530701) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0039 | Single Phase Fault with Stuck Breaker on COLBY 3 (530555) 115 kV Bus a. Apply Fault at the COLBY 3 (530555) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. COLBY 3 (530555) 115.0 kV to MINGO 3 (531429) 115.0 kV Transmission Circuit #1 b.2. COLBY 3 (530555) 115.0 kV to ATWOOD 3 (530554) 115.0 kV Transmission Circuit #1 b.3. COLBY 3 (530555) 115.0 kV to GEM_SW 3 (530713) 115.0 kV Transmission Circuit #1 b.4. COLBY 3 (530555) 115.0 kV to COLBY 2 (530644) 69.0 kV to CLBYT1 1 (530645) 13.8 kV Three Winding #1 b.5. COLBY 3 (530555) 115.0 kV to remove bus # b.6. CLBYT1 1 (530645) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0040 | Single Phase Fault with Stuck Breaker on BEACH 3 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 (530557) 115 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. REDLIN 3 (530605) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HOXIE 3 (530556) 115.0 kV Transmission Circuit #1 b.5. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 b.6. BEACH 3 (530557) 115.0 kV to remove bus # b.7. HILLCTY3 (531387) 34.5 kV to Generator #1 b.8. HILLCTY3 (531387) 34.5 kV to Generator #2 b.9. HILLCTY3 (531387) 34.5 kV to Generator #3 b.10. HILLCTY3 (531387) 34.5 kV to Generator #4 b.11. HILLCTY3 (531387) 34.5 kV to Generator #5 b.12. HILLCTY3 (531387) 34.5 kV to Generator #6 b.13. HILLCTY3 (531387) 34.5 kV to remove bus # b.14. REDLIN 3 (530605) 115.0 kV to remove bus # b.15. HOXIE 3 (530556) 115.0 kV to remove bus # b.16. REDLIN 3 (530605) 115.0 kV to Load #71 b.17. HOXIE 3 (530556) 115.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0041 | Single Phase Fault with Stuck Breaker on ATWOOD 3 (530554) 115 kV Bus a. Apply Fault at the ATWOOD 3 (530554) 115 kV Bus b. Clear Fault after 30 cycles and trip the following elements: b.1. ATWOOD 3 (530554) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. ATWOOD 3 (530554) 115.0 kV to ATWODSW3 (531364) 115.0 kV Transmission Circuit #1 b.3. ATWOOD 3 (530554) 115.0 kV to BVERVLLY (531488) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to remove bus # b.5. ATWOOD 3 (530554) 115.0 kV to Generator #1 b.6. HILLCTY3 (531387) 34.5 kV to Generator #1 b.7. HILLCTY3 (531387) 34.5 kV to Generator #2 b.8. HILLCTY3 (531387) 34.5 kV to Generator #3 b.9. HILLCTY3 (531387) 34.5 kV to Generator #4 b.10. HILLCTY3 (531387) 34.5 kV to Generator #5 b.11. HILLCTY3 (531387) 34.5 kV to Generator #6 b.12. ATWOOD 3 (530554) 115.0 kV to Load #1 b.13. ATWOOD 3 (530554) 115.0 kV to Load #41 b.14. ATWOOD 3 (530554) 115.0 kV to remove bus # b.15. HILLCTY3 (531387) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_MIDW_FAULT_0042 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 4 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0001 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.2. JEC U1 (532651) 26.0 kV to remove bus # b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0002 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.2. JEC U2 (532652) 26.0 kV to remove bus # b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0003 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.2. JEC U3 (532653) 26.0 kV to remove bus # b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0004 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0005 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0006 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0007 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #1 b.4. EMPEC121 (532740) 13.8 kV to Generator #2 b.5. EMPEC121 (532740) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0008 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC121 (532740) 13.8 kV Two Winding #1 b.2. EMPEC121 (532740) 13.8 kV to Generator #1 b.3. EMPEC121 (532740) 13.8 kV to Generator #2 b.4. EMPEC121 (532740) 13.8 kV to remove bus # b.5. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0009 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0010 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.2. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.3. EMPEC7 1 (532744) 18.0 kV to remove bus # b.4. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0011 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0012 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0013 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0014 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 13.25 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0015 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0016 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0017 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0018 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0019 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0020 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0021 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0022 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0023 | Single Phase Fault with Stuck Breaker on Wolf Creek 345 kV (532797) 345 kV Bus a. Apply Fault at the Wolf Creek 345 kV (532797) 345 kV Bus b. Clear Fault after 10.5 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0024 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0025 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0026 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0027 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0028 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to remove bus # b.4. RANDLPH5 (543027) 161.0 kV to Load #1 b.5. RANDLPH5 (543027) 161.0 kV to Load #4 b.6. RANDLPH5 (543027) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0029 | Single Phase Fault with Stuck Breaker on Hawthorn South (542973) 161 kV Bus a. Apply Fault at the Hawthorn South (542973) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0030 | Single Phase Fault with Stuck Breaker on Hawthorn 161 kV (542973) 161 kV Bus a. Apply Fault at the Hawthorn 161 kV (542973) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@1 b.2. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0031 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0032 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0033 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0034 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0035 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0036 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. IAT G1 1 (542957) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0037 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0038 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0039 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LAC G1 1 (542955) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0040 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. LAC G2 1 (542956) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0041 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0042 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 b.4. NEASTN5 (543666) 161.0 kV to Load #78 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0043 | Single Phase Fault with Stuck Breaker on Stilwell 345 kV (542968) 345 kV Bus a. Apply Fault at the Stilwell 345 kV (542968) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0044 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0045 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0046 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 18.25 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to JEC N 7 (532766) 345.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0047 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 16.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0048 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0049 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 14.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0050 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0051 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0052 | Single Phase Fault with Stuck Breaker on Benton 345 kV (532791) 345 kV Bus a. Apply Fault at the Benton 345 kV (532791) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0053 | Single Phase Fault with Stuck Breaker on Emporia EC 345 kV (532768) 345 kV Bus a. Apply Fault at the Emporia EC 345 kV (532768) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to EMPEC7 1 (532744) 18.0 kV Two Winding #1 b.3. EMPEC7 1 (532744) 18.0 kV to Generator #7 b.4. EMPEC7 1 (532744) 18.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0054 | Single Phase Fault with Stuck Breaker on Jeffrey EC 230 kV (532852) 230 kV Bus a. Apply Fault at the Jeffrey EC 230 kV (532852) 230 kV Bus b. Clear Fault after 5.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC 6 (532852) 230.0 kV to JEC U1 (532651) 26.0 kV Two Winding #1 b.3. JEC U1 (532651) 26.0 kV to Generator #1 b.4. JEC U1 (532651) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0055 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0056 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U2 (532652) 26.0 kV Two Winding #1 b.3. JEC U2 (532652) 26.0 kV to Generator #1 b.4. JEC U2 (532652) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0057 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0058 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0059 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC U3 (532653) 26.0 kV Two Winding #1 b.3. JEC U3 (532653) 26.0 kV to Generator #1 b.4. JEC U3 (532653) 26.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0060 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0061 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0062 | Single Phase Fault with Stuck Breaker on Jeffrey EC 345 kV (532766) 345 kV Bus a. Apply Fault at the Jeffrey EC 345 kV (532766) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 b.2. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0063 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0064 | Single Phase Fault with Stuck Breaker on Rose Hill 345 kV (532794) 345 kV Bus a. Apply Fault at the Rose Hill 345 kV (532794) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0065 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0066 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0067 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0068 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0069 | Single Phase Fault with Stuck Breaker on Stranger Creek 345 kV (532772) 345 kV Bus a. Apply Fault at the Stranger Creek 345 kV (532772) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0070 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0071 | Single Phase Fault with Stuck Breaker on Craig 345 kV (542977) 345 kV Bus a. Apply Fault at the Craig 345 kV (542977) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0072 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@1 b.2. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0073 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0074 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0075 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0076 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0077 | Single Phase Fault with Stuck Breaker on Iatan 345 kV (542982) 345 kV Bus a. Apply Fault at the Iatan 345 kV (542982) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. IAT G1 1 (542957) 24.0 kV to remove bus # b.2. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0078 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to remove bus # b.2. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0079 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 b.3. LACYGNE2 (543659) 69.0 kV to remove bus # b.4. LAC_LAKE_2 (541541) 69.0 kV to remove bus # b.5. LAC_LAKE_2 (541541) 69.0 kV to Load #K1 b.6. LAC_LAKE_2 (541541) 69.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0080 | Single Phase Fault with Stuck Breaker on LaCygne 345 kV (542981) 345 kV Bus a. Apply Fault at the LaCygne 345 kV (542981) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0081 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0082 | Single Phase Fault with Stuck Breaker on Northeast North (543666) 161 kV Bus a. Apply Fault at the Northeast North (543666) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NEASTN5 (543666) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to remove bus # b.4. NE CT14 (542971) 13.8 kV to remove bus # b.5. NEASTN5 (543666) 161.0 kV to Load #56 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0083 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NE CT17 (542983) 13.8 kV to remove bus # b.2. NE CT18 (542984) 13.8 kV to remove bus # b.3. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.4. NEASTS5 (542985) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 b.5. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 b.6. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0084 | Single Phase Fault with Stuck Breaker on Stilwell 345 kV (542968) 345 kV Bus a. Apply Fault at the Stilwell 345 kV (542968) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0085 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0086 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Transfer | GROUP3_P4_EVERGY_FAULT_0087 | Single Phase Fault with Stuck Breaker on West Gardner 345 kV (542965) 345 kV Bus a. Apply Fault at the West Gardner 345 kV (542965) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_0779 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 4.75 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 4.75 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT_0911 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | The Grand Prairie Wind Units (645065, 645066, 645067 and 645068) become unstable following the fault clearance and protection trips the units. Reducing the critical clearing time to 2.7 cycles mitigates the issue. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
03 CENTRAL | DISIS-2022-001 CF | 25S | Base | GROUP3_P4_LOCAL_FAULT_0067 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_0779 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 4.75 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 4.75 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2022-001 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT_0911 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | The Grand Prairie Wind Units (645065, 645066, 645067 and 645068) become unstable following the fault clearance and protection trips the units. Reducing the critical clearing time to 3.0 cycles mitigates the issue. This issue is also observed in the base case and no CQ units were found to impact the issue. | No mitigation required.
03 CENTRAL | DISIS-2022-001 CF | 25W | Base | GROUP3_P4_LOCAL_FAULT_0067 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2022-012 | 04 SOUTHEAST | 511409 | TREASILD7 | 345 | 16.2063 | 16.2068 | 0.0005
GEN-2022-012 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.6307 | 10.6309 | 0.0002
GEN-2022-012 | 04 SOUTHEAST | 511458 | ELKCTY-4 | 138 | 11.0368 | 11.037 | 0.0002
GEN-2022-012 | 04 SOUTHEAST | 511490 | ELKCITY6 | 230 | 6.6318 | 6.6319 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 511541 | SWEETWT6 | 230 | 7.3596 | 7.3597 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 511542 | BUFFCK6 | 230 | 5.6376 | 5.6377 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 511544 | DEMPSEY6 | 230 | 4.713 | 4.7131 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 511547 | ROARK6 | 230 | 4.6678 | 4.6678 | 0
GEN-2022-012 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 5.8781 | 5.8782 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 8.5716 | 8.5718 | 0.0002
GEN-2022-012 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 20.2984 | 20.2994 | 0.001
GEN-2022-012 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 19.6736 | 19.6762 | 0.0026
GEN-2022-012 | 04 SOUTHEAST | 514773 | NEWMAN 2 | 69 | 1.6719 | 1.672 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 514775 | TANGRTP2 | 69 | 5.3144 | 5.3152 | 0.0008
GEN-2022-012 | 04 SOUTHEAST | 514776 | NEWGRTP2 | 69 | 6.0374 | 6.0384 | 0.001
GEN-2022-012 | 04 SOUTHEAST | 514778 | CLEOCOR4 | 138 | 6.6424 | 6.6427 | 0.0003
GEN-2022-012 | 04 SOUTHEAST | 514779 | WDNITRO2 | 69 | 5.307 | 5.3078 | 0.0008
GEN-2022-012 | 04 SOUTHEAST | 514781 | CEDARAV2 | 69 | 6.3296 | 6.3307 | 0.0011
GEN-2022-012 | 04 SOUTHEAST | 514782 | WODWRD 2 | 69 | 12.4046 | 12.4089 | 0.0043
GEN-2022-012 | 04 SOUTHEAST | 514785 | WOODWRD4 | 138 | 18.2304 | 18.2588 | 0.0284
GEN-2022-012 | 04 SOUTHEAST | 514787 | DEWEY 4 | 138 | 8.5451 | 8.547 | 0.0019
GEN-2022-012 | 04 SOUTHEAST | 514788 | GLASMTN4 | 138 | 5.4168 | 5.4171 | 0.0003
GEN-2022-012 | 04 SOUTHEAST | 514792 | ALVAOGE2 | 69 | 7.6994 | 7.7004 | 0.001
GEN-2022-012 | 04 SOUTHEAST | 514794 | KNOBHIL2 | 69 | 9.0345 | 9.0359 | 0.0014
GEN-2022-012 | 04 SOUTHEAST | 514795 | KNOBHIL4 | 138 | 10.2285 | 10.2333 | 0.0048
GEN-2022-012 | 04 SOUTHEAST | 514796 | IODINE-4 | 138 | 7.9138 | 7.9183 | 0.0045
GEN-2022-012 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 24.194 | 24.1967 | 0.0027
GEN-2022-012 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.8511 | 17.8519 | 0.0008
GEN-2022-012 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 19.5836 | 19.5845 | 0.0009
GEN-2022-012 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 28.2519 | 28.2532 | 0.0013
GEN-2022-012 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 33.451 | 33.4535 | 0.0025
GEN-2022-012 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 28.0757 | 28.0773 | 0.0016
GEN-2022-012 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.7399 | 23.7412 | 0.0013
GEN-2022-012 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.6763 | 28.6782 | 0.0019
GEN-2022-012 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 47.0235 | 47.0292 | 0.0057
GEN-2022-012 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.115 | 35.126 | 0.011
GEN-2022-012 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.6353 | 24.6397 | 0.0044
GEN-2022-012 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 30.2739 | 30.2753 | 0.0014
GEN-2022-012 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.2466 | 20.2473 | 0.0007
GEN-2022-012 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 47.2595 | 47.2649 | 0.0054
GEN-2022-012 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 37.6904 | 37.7045 | 0.0141
GEN-2022-012 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 43.2789 | 43.2808 | 0.0019
GEN-2022-012 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.2144 | 28.2163 | 0.0019
GEN-2022-012 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.2564 | 27.258 | 0.0016
GEN-2022-012 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.0663 | 27.0684 | 0.0021
GEN-2022-012 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.8887 | 29.8897 | 0.001
GEN-2022-012 | 04 SOUTHEAST | 515363 | CENT 4 | 138 | 3.4022 | 3.4029 | 0.0007
GEN-2022-012 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 20.3258 | 20.5292 | 0.2034
GEN-2022-012 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 26.3708 | 26.4572 | 0.0864
GEN-2022-012 | 04 SOUTHEAST | 515390 | TLGAWND4 | 138 | 4.2846 | 4.285 | 0.0004
GEN-2022-012 | 04 SOUTHEAST | 515394 | KEENAN 4 | 138 | 9.2045 | 9.2142 | 0.0097
GEN-2022-012 | 04 SOUTHEAST | 515398 | OUSPRT 4 | 138 | 10.0796 | 10.0913 | 0.0117
GEN-2022-012 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 17.9631 | 18.0193 | 0.0562
GEN-2022-012 | 04 SOUTHEAST | 515425 | WWDPST 4 | 138 | 19.7857 | 19.8239 | 0.0382
GEN-2022-012 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 24.0975 | 24.1002 | 0.0027
GEN-2022-012 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.5259 | 12.5525 | 0.0266
GEN-2022-012 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 4.5194 | 4.5249 | 0.0055
GEN-2022-012 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 14.0131 | 14.0145 | 0.0014
GEN-2022-012 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 35.0223 | 35.0446 | 0.0223
GEN-2022-012 | 04 SOUTHEAST | 515533 | REDCLFT4 | 138 | 7.2479 | 7.2508 | 0.0029
GEN-2022-012 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 15.0258 | 15.0268 | 0.001
GEN-2022-012 | 04 SOUTHEAST | 515554 | BVRCNTY7 | 345 | 12.042 | 12.0618 | 0.0198
GEN-2022-012 | 04 SOUTHEAST | 515560 | CZYCRVT2 | 69 | 3.4124 | 3.4125 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.7356 | 8.7481 | 0.0125
GEN-2022-012 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.1611 | 14.195 | 0.0339
GEN-2022-012 | 04 SOUTHEAST | 515590 | PALDR2W7 | 345 | 10.8562 | 10.8716 | 0.0154
GEN-2022-012 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 12.5807 | 12.5819 | 0.0012
GEN-2022-012 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 13.7137 | 13.7151 | 0.0014
GEN-2022-012 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.8457 | 18.8486 | 0.0029
GEN-2022-012 | 04 SOUTHEAST | 515618 | BALKOW 7 | 345 | 10.4357 | 10.4503 | 0.0146
GEN-2022-012 | 04 SOUTHEAST | 515634 | PALDR1W7 | 345 | 9.8404 | 9.8525 | 0.0121
GEN-2022-012 | 04 SOUTHEAST | 515677 | BADGER 7 | 345 | 11.7535 | 11.7802 | 0.0267
GEN-2022-012 | 04 SOUTHEAST | 515686 | BLUWND 7 | 345 | 10.701 | 10.7231 | 0.0221
GEN-2022-012 | 04 SOUTHEAST | 515785 | WINDFRM4 | 138 | 22.9898 | 22.9992 | 0.0094
GEN-2022-012 | 04 SOUTHEAST | 515786 | FPLWIND4 | 138 | 7.3083 | 7.3091 | 0.0008
GEN-2022-012 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 18.898 | 18.8989 | 0.0009
GEN-2022-012 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 34.0084 | 34.0089 | 0.0005
GEN-2022-012 | 04 SOUTHEAST | 515825 | GRTWSRN7 | 345 | 9.5942 | 9.635 | 0.0408
GEN-2022-012 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.4165 | 14.4639 | 0.0474
GEN-2022-012 | 04 SOUTHEAST | 515853 | DGRASSE4 | 138 | 15.8812 | 15.8955 | 0.0143
GEN-2022-012 | 04 SOUTHEAST | 515863 | REDCLF 4 | 138 | 7.2318 | 7.2347 | 0.0029
GEN-2022-012 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 17.5618 | 17.5653 | 0.0035
GEN-2022-012 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 17.5573 | 17.5608 | 0.0035
GEN-2022-012 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 11.4539 | 11.514 | 0.0601
GEN-2022-012 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 13.001 | 13.0791 | 0.0781
GEN-2022-012 | 04 SOUTHEAST | 515964 | CANTNLK4 | 138 | 5.1783 | 5.1788 | 0.0005
GEN-2022-012 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 4.6879 | 4.688 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.5437 | 17.5449 | 0.0012
GEN-2022-012 | 04 SOUTHEAST | 516059 | BECKHAM7 | 345 | 5.0915 | 5.0995 | 0.008
GEN-2022-012 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 28.1479 | 28.1509 | 0.003
GEN-2022-012 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 44.436 | 44.4382 | 0.0022
GEN-2022-012 | 04 SOUTHEAST | 516146 | 25MILE 7 | 345 | 10.3321 | 10.3701 | 0.038
GEN-2022-012 | 04 SOUTHEAST | 516159 | 25MILZ 7 | 345 | 10.3207 | 10.3587 | 0.038
GEN-2022-012 | 04 SOUTHEAST | 520425 | PIC4 | 138 | 8.6433 | 8.6444 | 0.0011
GEN-2022-012 | 04 SOUTHEAST | 520430 | NOELSW 4 | 138 | 10.2906 | 10.2955 | 0.0049
GEN-2022-012 | 04 SOUTHEAST | 520436 | ROSEVLY4 | 138 | 11.951 | 11.9587 | 0.0077
GEN-2022-012 | 04 SOUTHEAST | 520437 | SALTPLN4 | 138 | 6.4976 | 6.499 | 0.0014
GEN-2022-012 | 04 SOUTHEAST | 520462 | ASPEN 4 | 138 | 22.5997 | 22.6085 | 0.0088
GEN-2022-012 | 04 SOUTHEAST | 520500 | BEARCAT4 | 138 | 16.1121 | 16.1164 | 0.0043
GEN-2022-012 | 04 SOUTHEAST | 520553 | SEILING4 | 138 | 7.6817 | 7.683 | 0.0013
GEN-2022-012 | 04 SOUTHEAST | 520601 | AVARD 4 | 138 | 6.8705 | 6.8731 | 0.0026
GEN-2022-012 | 04 SOUTHEAST | 520848 | CDRDLTP4 | 138 | 6.079 | 6.0794 | 0.0004
GEN-2022-012 | 04 SOUTHEAST | 520920 | FTSUPLY4 | 138 | 5.8039 | 5.8044 | 0.0005
GEN-2022-012 | 04 SOUTHEAST | 520957 | IODINE 4 | 138 | 8.4783 | 8.4795 | 0.0012
GEN-2022-012 | 04 SOUTHEAST | 520995 | MOORLND2 | 69 | 9.2272 | 9.2284 | 0.0012
GEN-2022-012 | 04 SOUTHEAST | 520999 | MOORLND4 | 138 | 23.5332 | 23.5427 | 0.0095
GEN-2022-012 | 04 SOUTHEAST | 521065 | TALOGA 4 | 138 | 8.4019 | 8.4036 | 0.0017
GEN-2022-012 | 04 SOUTHEAST | 521082 | VICI 2 | 69 | 4.0908 | 4.0911 | 0.0003
GEN-2022-012 | 04 SOUTHEAST | 521096 | WOODWRD2 | 69 | 10.9283 | 10.9308 | 0.0025
GEN-2022-012 | 04 SOUTHEAST | 521196 | FARGOJCT2 | 69 | 8.2191 | 8.2204 | 0.0013
GEN-2022-012 | 04 SOUTHEAST | 521197 | CRTSJCT2 | 69 | 8.8073 | 8.8084 | 0.0011
GEN-2022-012 | 04 SOUTHEAST | 523095 | HITCHLAND 6 | 230 | 12.3327 | 12.3402 | 0.0075
GEN-2022-012 | 04 SOUTHEAST | 523097 | HITCHLAND 7 | 345 | 11.2897 | 11.302 | 0.0123
GEN-2022-012 | 04 SOUTHEAST | 523101 | NOBLE_WND 7 | 345 | 11.2549 | 11.2671 | 0.0122
GEN-2022-012 | 04 SOUTHEAST | 523112 | NOVUS1 7 | 345 | 11.1106 | 11.1224 | 0.0118
GEN-2022-012 | 04 SOUTHEAST | 523777 | WHEELER 6 | 230 | 5.7823 | 5.7824 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 523823 | CARPENTER 7 | 345 | 6.2337 | 6.2357 | 0.002
GEN-2022-012 | 04 SOUTHEAST | 523961 | POTTER_CO 7 | 345 | 9.7747 | 9.7761 | 0.0014
GEN-2022-012 | 04 SOUTHEAST | 525213 | SWISHER 6 | 230 | 10.6376 | 10.6378 | 0.0002
GEN-2022-012 | 04 SOUTHEAST | 525531 | TOLK 6 | 230 | 26.543 | 26.5433 | 0.0003
GEN-2022-012 | 04 SOUTHEAST | 525828 | TUCO_INT 3 | 115 | 18.8262 | 18.8265 | 0.0003
GEN-2022-012 | 04 SOUTHEAST | 525830 | TUCO_INT 6 | 230 | 22.5286 | 22.5297 | 0.0011
GEN-2022-012 | 04 SOUTHEAST | 525832 | TUCO_INT 7 | 345 | 11.215 | 11.2159 | 0.0009
GEN-2022-012 | 04 SOUTHEAST | 525840 | ANTELOPE_1 6 | 230 | 22.3422 | 22.3433 | 0.0011
GEN-2022-012 | 04 SOUTHEAST | 525850 | ELK_CT1 | 345 | 11.1411 | 11.1421 | 0.001
GEN-2022-012 | 04 SOUTHEAST | 525957 | HALE_WNDCL16 | 230 | 12.2241 | 12.2244 | 0.0003
GEN-2022-012 | 04 SOUTHEAST | 526161 | CARLISLE 6 | 230 | 10.7149 | 10.715 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 526337 | JONES 6 | 230 | 17.7995 | 17.7997 | 0.0002
GEN-2022-012 | 04 SOUTHEAST | 526936 | YOAKUM_345 | 345 | 10.397 | 10.3971 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 531469 | SPERVIL7 | 345 | 11.0807 | 11.0836 | 0.0029
GEN-2022-012 | 04 SOUTHEAST | 532771 | RENO 7 | 345 | 11.0252 | 11.026 | 0.0008
GEN-2022-012 | 04 SOUTHEAST | 532782 | BUFFALO7 | 345 | 19.2154 | 19.2221 | 0.0067
GEN-2022-012 | 04 SOUTHEAST | 532783 | KINGMAN7 | 345 | 7.2091 | 7.2098 | 0.0007
GEN-2022-012 | 04 SOUTHEAST | 532784 | NINN1WF7 | 345 | 6.0164 | 6.0168 | 0.0004
GEN-2022-012 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 18.4668 | 18.469 | 0.0022
GEN-2022-012 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 22.0351 | 22.0413 | 0.0062
GEN-2022-012 | 04 SOUTHEAST | 532798 | VIOLA 7 | 345 | 13.4745 | 13.4763 | 0.0018
GEN-2022-012 | 04 SOUTHEAST | 532803 | BURNS 7 | 345 | 10.4599 | 10.4604 | 0.0005
GEN-2022-012 | 04 SOUTHEAST | 533040 | EVANS N4 | 138 | 27.9631 | 27.9662 | 0.0031
GEN-2022-012 | 04 SOUTHEAST | 539631 | FLATRWD4 | 138 | 10.3907 | 10.3932 | 0.0025
GEN-2022-012 | 04 SOUTHEAST | 539638 | FLATRDG4 | 138 | 15.4338 | 15.4393 | 0.0055
GEN-2022-012 | 04 SOUTHEAST | 539668 | HARPER 4 | 138 | 7.4348 | 7.4355 | 0.0007
GEN-2022-012 | 04 SOUTHEAST | 539674 | BARBER 4 | 138 | 8.3536 | 8.355 | 0.0014
GEN-2022-012 | 04 SOUTHEAST | 539800 | CLARKCOUNTY7 | 345 | 10.1971 | 10.2008 | 0.0037
GEN-2022-012 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 15.3229 | 15.3415 | 0.0186
GEN-2022-012 | 04 SOUTHEAST | 539803 | IRONWOOD7 | 345 | 10.623 | 10.6258 | 0.0028
GEN-2022-012 | 04 SOUTHEAST | 539804 | THISTLE4 | 138 | 17.339 | 17.3465 | 0.0075
GEN-2022-012 | 04 SOUTHEAST | 539813 | TRANSFORMER | 345 | 8.8882 | 8.8911 | 0.0029
GEN-2022-012 | 04 SOUTHEAST | 539840 | GEN-2011-008 | 345 | 8.5086 | 8.5112 | 0.0026
GEN-2022-012 | 04 SOUTHEAST | 539841 | G-2011-008-1 | 345 | 7.329 | 7.331 | 0.002
GEN-2022-012 | 04 SOUTHEAST | 539855 | G-2011-008-2 | 345 | 7.3272 | 7.3292 | 0.002
GEN-2022-012 | 04 SOUTHEAST | 539857 | G-2011-008-3 | 345 | 6.8796 | 6.8814 | 0.0018
GEN-2022-012 | 04 SOUTHEAST | 560071 | G16-003-TAP | 345 | 14.7144 | 14.7941 | 0.0797
GEN-2022-012 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 7.595 | 7.5951 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 560080 | G16-046-TAP | 345 | 9.2075 | 9.2102 | 0.0027
GEN-2022-012 | 04 SOUTHEAST | 576397 | G10014G11022 | 345 | 8.051 | 8.0573 | 0.0063
GEN-2022-012 | 04 SOUTHEAST | 585190 | GEN-2015-082 | 345 | 6.3754 | 6.3833 | 0.0079
GEN-2022-012 | 04 SOUTHEAST | 585440 | PRSIMN_CRK2 | 345 | 10.5168 | 10.5672 | 0.0504
GEN-2022-012 | 04 SOUTHEAST | 587140 | GEN-2016-020 | 138 | 8.077 | 8.078 | 0.001
GEN-2022-012 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 7.3368 | 7.337 | 0.0002
GEN-2022-012 | 04 SOUTHEAST | 587310 | GEN-2016-046 | 345 | 8.1844 | 8.1865 | 0.0021
GEN-2022-012 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.9485 | 15.9494 | 0.0009
GEN-2022-012 | 04 SOUTHEAST | 588560 | GEN-2017-011 | 345 | 12.0263 | 12.0795 | 0.0532
GEN-2022-012 | 04 SOUTHEAST | 588630 | GEN-2017-018 | 345 | 15.3229 | 15.3415 | 0.0186
GEN-2022-012 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 4.9611 | 4.9611 | 0
GEN-2022-012 | 04 SOUTHEAST | 760284 | GEN-2017-220 | 345 | 19.1166 | 19.1232 | 0.0066
GEN-2022-012 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 23.4017 | 23.4043 | 0.0026
GEN-2022-012 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 7.0943 | 7.0946 | 0.0003
GEN-2022-012 | 04 SOUTHEAST | 762217 | GEN-2017-151 | 345 | 5.2668 | 5.267 | 0.0002
GEN-2022-012 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.7156 | 11.7165 | 0.0009
GEN-2022-012 | 04 SOUTHEAST | 762467 | G18-015-TAP | 345 | 4.4184 | 4.4185 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 762834 | GEN-2018-049 | 345 | 6.695 | 6.6985 | 0.0035
GEN-2022-012 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 17.9362 | 18.0937 | 0.1575
GEN-2022-012 | 04 SOUTHEAST | 763670 | GEN-2019-030 | 345 | 7.7823 | 7.7841 | 0.0018
GEN-2022-012 | 04 SOUTHEAST | 763677 | G19-030-TAP | 345 | 9.2504 | 9.2529 | 0.0025
GEN-2022-012 | 04 SOUTHEAST | 763769 | GEN-2019-045 | 138 | 15.8812 | 15.8955 | 0.0143
GEN-2022-012 | 04 SOUTHEAST | 763890 | GEN-2019-058 | 345 | 10.03 | 10.0337 | 0.0037
GEN-2022-012 | 04 SOUTHEAST | 764935 | GEN-2020-067 | 345 | 5.769 | 5.7691 | 0.0001
GEN-2022-012 | 04 SOUTHEAST | 764945 | G20-067-TAP | 345 | 6.9922 | 6.9924 | 0.0002
GEN-2022-012 | 04 SOUTHEAST | 765215 | G20-010-TAP | 138 | 8.0714 | 8.0729 | 0.0015
GEN-2022-012 | 04 SOUTHEAST | 765530 | GEN-2021-025 | 138 | 18.4466 | 18.4523 | 0.0057
GEN-2022-012 | 04 SOUTHEAST | 767221 | GEN-2022-012 | 345 | 20.042 | 20.2455 | 0.2035
GEN-2022-012 | 04 SOUTHEAST | 767301 | GEN-2022-016 | 345 | 20.0667 | 20.2647 | 0.198
GEN-2022-012 | 04 SOUTHEAST | 767321 | GEN-2022-017 | 345 | 19.7985 | 19.9912 | 0.1927
GEN-2022-012 | 04 SOUTHEAST | 769921 | GEN-2022-147 | 345 | 11.1166 | 11.1175 | 0.0009
GEN-2022-012 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.1207 | 7.1213 | 0.0006
GEN-2022-012 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.6925 | 5.6929 | 0.0004
GEN-2022-012 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.36 | 6.3605 | 0.0005
GEN-2022-016 | 04 SOUTHEAST | 511409 | TREASILD7 | 345 | 16.2053 | 16.2068 | 0.0015
GEN-2022-016 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.6304 | 10.6309 | 0.0005
GEN-2022-016 | 04 SOUTHEAST | 511458 | ELKCTY-4 | 138 | 11.0367 | 11.037 | 0.0003
GEN-2022-016 | 04 SOUTHEAST | 511490 | ELKCITY6 | 230 | 6.6319 | 6.6319 | 0
GEN-2022-016 | 04 SOUTHEAST | 511541 | SWEETWT6 | 230 | 7.3606 | 7.3597 | -0.0009
GEN-2022-016 | 04 SOUTHEAST | 511542 | BUFFCK6 | 230 | 5.6382 | 5.6377 | -0.0005
GEN-2022-016 | 04 SOUTHEAST | 511544 | DEMPSEY6 | 230 | 4.7134 | 4.7131 | -0.0003
GEN-2022-016 | 04 SOUTHEAST | 511547 | ROARK6 | 230 | 4.6681 | 4.6678 | -0.0003
GEN-2022-016 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 5.8783 | 5.8782 | -0.0001
GEN-2022-016 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 8.5722 | 8.5718 | -0.0004
GEN-2022-016 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 20.2967 | 20.2994 | 0.0027
GEN-2022-016 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 19.6687 | 19.6762 | 0.0075
GEN-2022-016 | 04 SOUTHEAST | 514773 | NEWMAN 2 | 69 | 1.6717 | 1.672 | 0.0003
GEN-2022-016 | 04 SOUTHEAST | 514775 | TANGRTP2 | 69 | 5.3129 | 5.3152 | 0.0023
GEN-2022-016 | 04 SOUTHEAST | 514776 | NEWGRTP2 | 69 | 6.0355 | 6.0384 | 0.0029
GEN-2022-016 | 04 SOUTHEAST | 514778 | CLEOCOR4 | 138 | 6.6419 | 6.6427 | 0.0008
GEN-2022-016 | 04 SOUTHEAST | 514779 | WDNITRO2 | 69 | 5.3056 | 5.3078 | 0.0022
GEN-2022-016 | 04 SOUTHEAST | 514781 | CEDARAV2 | 69 | 6.3275 | 6.3307 | 0.0032
GEN-2022-016 | 04 SOUTHEAST | 514782 | WODWRD 2 | 69 | 12.3963 | 12.4089 | 0.0126
GEN-2022-016 | 04 SOUTHEAST | 514785 | WOODWRD4 | 138 | 18.1763 | 18.2588 | 0.0825
GEN-2022-016 | 04 SOUTHEAST | 514787 | DEWEY 4 | 138 | 8.5413 | 8.547 | 0.0057
GEN-2022-016 | 04 SOUTHEAST | 514788 | GLASMTN4 | 138 | 5.4162 | 5.4171 | 0.0009
GEN-2022-016 | 04 SOUTHEAST | 514792 | ALVAOGE2 | 69 | 7.6976 | 7.7004 | 0.0028
GEN-2022-016 | 04 SOUTHEAST | 514794 | KNOBHIL2 | 69 | 9.0317 | 9.0359 | 0.0042
GEN-2022-016 | 04 SOUTHEAST | 514795 | KNOBHIL4 | 138 | 10.2194 | 10.2333 | 0.0139
GEN-2022-016 | 04 SOUTHEAST | 514796 | IODINE-4 | 138 | 7.9052 | 7.9183 | 0.0131
GEN-2022-016 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 24.1888 | 24.1967 | 0.0079
GEN-2022-016 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.8495 | 17.8519 | 0.0024
GEN-2022-016 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 19.582 | 19.5845 | 0.0025
GEN-2022-016 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 28.2495 | 28.2532 | 0.0037
GEN-2022-016 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 33.4461 | 33.4535 | 0.0074
GEN-2022-016 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 28.0725 | 28.0773 | 0.0048
GEN-2022-016 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.7374 | 23.7412 | 0.0038
GEN-2022-016 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.6728 | 28.6782 | 0.0054
GEN-2022-016 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 47.0127 | 47.0292 | 0.0165
GEN-2022-016 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.094 | 35.126 | 0.032
GEN-2022-016 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.627 | 24.6397 | 0.0127
GEN-2022-016 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 30.2711 | 30.2753 | 0.0042
GEN-2022-016 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.2454 | 20.2473 | 0.0019
GEN-2022-016 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 47.2492 | 47.2649 | 0.0157
GEN-2022-016 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 37.6634 | 37.7045 | 0.0411
GEN-2022-016 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 43.2754 | 43.2808 | 0.0054
GEN-2022-016 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.2108 | 28.2163 | 0.0055
GEN-2022-016 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.2534 | 27.258 | 0.0046
GEN-2022-016 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.0622 | 27.0684 | 0.0062
GEN-2022-016 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.8867 | 29.8897 | 0.003
GEN-2022-016 | 04 SOUTHEAST | 515363 | CENT 4 | 138 | 3.4008 | 3.4029 | 0.0021
GEN-2022-016 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 19.9472 | 20.5292 | 0.582
GEN-2022-016 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 26.207 | 26.4572 | 0.2502
GEN-2022-016 | 04 SOUTHEAST | 515390 | TLGAWND4 | 138 | 4.2839 | 4.285 | 0.0011
GEN-2022-016 | 04 SOUTHEAST | 515394 | KEENAN 4 | 138 | 9.1862 | 9.2142 | 0.028
GEN-2022-016 | 04 SOUTHEAST | 515398 | OUSPRT 4 | 138 | 10.0572 | 10.0913 | 0.0341
GEN-2022-016 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 17.8564 | 18.0193 | 0.1629
GEN-2022-016 | 04 SOUTHEAST | 515425 | WWDPST 4 | 138 | 19.7131 | 19.8239 | 0.1108
GEN-2022-016 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 24.0924 | 24.1002 | 0.0078
GEN-2022-016 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.4752 | 12.5525 | 0.0773
GEN-2022-016 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 4.5089 | 4.5249 | 0.016
GEN-2022-016 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 14.0106 | 14.0145 | 0.0039
GEN-2022-016 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 34.9798 | 35.0446 | 0.0648
GEN-2022-016 | 04 SOUTHEAST | 515533 | REDCLFT4 | 138 | 7.2423 | 7.2508 | 0.0085
GEN-2022-016 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 15.024 | 15.0268 | 0.0028
GEN-2022-016 | 04 SOUTHEAST | 515554 | BVRCNTY7 | 345 | 12.0042 | 12.0618 | 0.0576
GEN-2022-016 | 04 SOUTHEAST | 515560 | CZYCRVT2 | 69 | 3.4122 | 3.4125 | 0.0003
GEN-2022-016 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.7118 | 8.7481 | 0.0363
GEN-2022-016 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.0966 | 14.195 | 0.0984
GEN-2022-016 | 04 SOUTHEAST | 515590 | PALDR2W7 | 345 | 10.8267 | 10.8716 | 0.0449
GEN-2022-016 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 12.5785 | 12.5819 | 0.0034
GEN-2022-016 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 13.711 | 13.7151 | 0.0041
GEN-2022-016 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.8401 | 18.8486 | 0.0085
GEN-2022-016 | 04 SOUTHEAST | 515618 | BALKOW 7 | 345 | 10.4079 | 10.4503 | 0.0424
GEN-2022-016 | 04 SOUTHEAST | 515634 | PALDR1W7 | 345 | 9.8173 | 9.8525 | 0.0352
GEN-2022-016 | 04 SOUTHEAST | 515677 | BADGER 7 | 345 | 11.7026 | 11.7802 | 0.0776
GEN-2022-016 | 04 SOUTHEAST | 515686 | BLUWND 7 | 345 | 10.6587 | 10.7231 | 0.0644
GEN-2022-016 | 04 SOUTHEAST | 515785 | WINDFRM4 | 138 | 22.9718 | 22.9992 | 0.0274
GEN-2022-016 | 04 SOUTHEAST | 515786 | FPLWIND4 | 138 | 7.3069 | 7.3091 | 0.0022
GEN-2022-016 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 18.8963 | 18.8989 | 0.0026
GEN-2022-016 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 34.0075 | 34.0089 | 0.0014
GEN-2022-016 | 04 SOUTHEAST | 515825 | GRTWSRN7 | 345 | 9.5172 | 9.635 | 0.1178
GEN-2022-016 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.3266 | 14.4639 | 0.1373
GEN-2022-016 | 04 SOUTHEAST | 515853 | DGRASSE4 | 138 | 15.854 | 15.8955 | 0.0415
GEN-2022-016 | 04 SOUTHEAST | 515863 | REDCLF 4 | 138 | 7.2263 | 7.2347 | 0.0084
GEN-2022-016 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 17.5551 | 17.5653 | 0.0102
GEN-2022-016 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 17.5506 | 17.5608 | 0.0102
GEN-2022-016 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 11.3404 | 11.514 | 0.1736
GEN-2022-016 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 12.854 | 13.0791 | 0.2251
GEN-2022-016 | 04 SOUTHEAST | 515964 | CANTNLK4 | 138 | 5.1774 | 5.1788 | 0.0014
GEN-2022-016 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 4.6876 | 4.688 | 0.0004
GEN-2022-016 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.5415 | 17.5449 | 0.0034
GEN-2022-016 | 04 SOUTHEAST | 516059 | BECKHAM7 | 345 | 5.0762 | 5.0995 | 0.0233
GEN-2022-016 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 28.142 | 28.1509 | 0.0089
GEN-2022-016 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 44.4318 | 44.4382 | 0.0064
GEN-2022-016 | 04 SOUTHEAST | 516146 | 25MILE 7 | 345 | 10.2601 | 10.3701 | 0.11
GEN-2022-016 | 04 SOUTHEAST | 516159 | 25MILZ 7 | 345 | 10.2489 | 10.3587 | 0.1098
GEN-2022-016 | 04 SOUTHEAST | 520425 | PIC4 | 138 | 8.6412 | 8.6444 | 0.0032
GEN-2022-016 | 04 SOUTHEAST | 520430 | NOELSW 4 | 138 | 10.2814 | 10.2955 | 0.0141
GEN-2022-016 | 04 SOUTHEAST | 520436 | ROSEVLY4 | 138 | 11.9364 | 11.9587 | 0.0223
GEN-2022-016 | 04 SOUTHEAST | 520437 | SALTPLN4 | 138 | 6.495 | 6.499 | 0.004
GEN-2022-016 | 04 SOUTHEAST | 520462 | ASPEN 4 | 138 | 22.5829 | 22.6085 | 0.0256
GEN-2022-016 | 04 SOUTHEAST | 520500 | BEARCAT4 | 138 | 16.104 | 16.1164 | 0.0124
GEN-2022-016 | 04 SOUTHEAST | 520553 | SEILING4 | 138 | 7.6793 | 7.683 | 0.0037
GEN-2022-016 | 04 SOUTHEAST | 520601 | AVARD 4 | 138 | 6.8656 | 6.8731 | 0.0075
GEN-2022-016 | 04 SOUTHEAST | 520848 | CDRDLTP4 | 138 | 6.0782 | 6.0794 | 0.0012
GEN-2022-016 | 04 SOUTHEAST | 520920 | FTSUPLY4 | 138 | 5.8029 | 5.8044 | 0.0015
GEN-2022-016 | 04 SOUTHEAST | 520957 | IODINE 4 | 138 | 8.4761 | 8.4795 | 0.0034
GEN-2022-016 | 04 SOUTHEAST | 520995 | MOORLND2 | 69 | 9.225 | 9.2284 | 0.0034
GEN-2022-016 | 04 SOUTHEAST | 520999 | MOORLND4 | 138 | 23.5149 | 23.5427 | 0.0278
GEN-2022-016 | 04 SOUTHEAST | 521065 | TALOGA 4 | 138 | 8.3987 | 8.4036 | 0.0049
GEN-2022-016 | 04 SOUTHEAST | 521082 | VICI 2 | 69 | 4.0904 | 4.0911 | 0.0007
GEN-2022-016 | 04 SOUTHEAST | 521096 | WOODWRD2 | 69 | 10.9235 | 10.9308 | 0.0073
GEN-2022-016 | 04 SOUTHEAST | 521196 | FARGOJCT2 | 69 | 8.2166 | 8.2204 | 0.0038
GEN-2022-016 | 04 SOUTHEAST | 521197 | CRTSJCT2 | 69 | 8.8052 | 8.8084 | 0.0032
GEN-2022-016 | 04 SOUTHEAST | 523095 | HITCHLAND 6 | 230 | 12.3179 | 12.3402 | 0.0223
GEN-2022-016 | 04 SOUTHEAST | 523097 | HITCHLAND 7 | 345 | 11.2662 | 11.302 | 0.0358
GEN-2022-016 | 04 SOUTHEAST | 523101 | NOBLE_WND 7 | 345 | 11.2316 | 11.2671 | 0.0355
GEN-2022-016 | 04 SOUTHEAST | 523112 | NOVUS1 7 | 345 | 11.0879 | 11.1224 | 0.0345
GEN-2022-016 | 04 SOUTHEAST | 523777 | WHEELER 6 | 230 | 5.784 | 5.7824 | -0.0016
GEN-2022-016 | 04 SOUTHEAST | 523823 | CARPENTER 7 | 345 | 6.23 | 6.2357 | 0.0057
GEN-2022-016 | 04 SOUTHEAST | 523961 | POTTER_CO 7 | 345 | 9.772 | 9.7761 | 0.0041
GEN-2022-016 | 04 SOUTHEAST | 525213 | SWISHER 6 | 230 | 10.6372 | 10.6378 | 0.0006
GEN-2022-016 | 04 SOUTHEAST | 525531 | TOLK 6 | 230 | 26.5423 | 26.5433 | 0.001
GEN-2022-016 | 04 SOUTHEAST | 525828 | TUCO_INT 3 | 115 | 18.8256 | 18.8265 | 0.0009
GEN-2022-016 | 04 SOUTHEAST | 525830 | TUCO_INT 6 | 230 | 22.5265 | 22.5297 | 0.0032
GEN-2022-016 | 04 SOUTHEAST | 525832 | TUCO_INT 7 | 345 | 11.2131 | 11.2159 | 0.0028
GEN-2022-016 | 04 SOUTHEAST | 525840 | ANTELOPE_1 6 | 230 | 22.3401 | 22.3433 | 0.0032
GEN-2022-016 | 04 SOUTHEAST | 525850 | ELK_CT1 | 345 | 11.1393 | 11.1421 | 0.0028
GEN-2022-016 | 04 SOUTHEAST | 525957 | HALE_WNDCL16 | 230 | 12.2236 | 12.2244 | 0.0008
GEN-2022-016 | 04 SOUTHEAST | 526161 | CARLISLE 6 | 230 | 10.7147 | 10.715 | 0.0003
GEN-2022-016 | 04 SOUTHEAST | 526337 | JONES 6 | 230 | 17.7992 | 17.7997 | 0.0005
GEN-2022-016 | 04 SOUTHEAST | 526936 | YOAKUM_345 | 345 | 10.3967 | 10.3971 | 0.0004
GEN-2022-016 | 04 SOUTHEAST | 531469 | SPERVIL7 | 345 | 11.075 | 11.0836 | 0.0086
GEN-2022-016 | 04 SOUTHEAST | 532771 | RENO 7 | 345 | 11.0237 | 11.026 | 0.0023
GEN-2022-016 | 04 SOUTHEAST | 532782 | BUFFALO7 | 345 | 19.2026 | 19.2221 | 0.0195
GEN-2022-016 | 04 SOUTHEAST | 532783 | KINGMAN7 | 345 | 7.2079 | 7.2098 | 0.0019
GEN-2022-016 | 04 SOUTHEAST | 532784 | NINN1WF7 | 345 | 6.0156 | 6.0168 | 0.0012
GEN-2022-016 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 18.4626 | 18.469 | 0.0064
GEN-2022-016 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 22.0234 | 22.0413 | 0.0179
GEN-2022-016 | 04 SOUTHEAST | 532798 | VIOLA 7 | 345 | 13.4712 | 13.4763 | 0.0051
GEN-2022-016 | 04 SOUTHEAST | 532803 | BURNS 7 | 345 | 10.4589 | 10.4604 | 0.0015
GEN-2022-016 | 04 SOUTHEAST | 533040 | EVANS N4 | 138 | 27.9572 | 27.9662 | 0.009
GEN-2022-016 | 04 SOUTHEAST | 539631 | FLATRWD4 | 138 | 10.3859 | 10.3932 | 0.0073
GEN-2022-016 | 04 SOUTHEAST | 539638 | FLATRDG4 | 138 | 15.4231 | 15.4393 | 0.0162
GEN-2022-016 | 04 SOUTHEAST | 539668 | HARPER 4 | 138 | 7.4335 | 7.4355 | 0.002
GEN-2022-016 | 04 SOUTHEAST | 539674 | BARBER 4 | 138 | 8.351 | 8.355 | 0.004
GEN-2022-016 | 04 SOUTHEAST | 539800 | CLARKCOUNTY7 | 345 | 10.1898 | 10.2008 | 0.011
GEN-2022-016 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 15.2874 | 15.3415 | 0.0541
GEN-2022-016 | 04 SOUTHEAST | 539803 | IRONWOOD7 | 345 | 10.6176 | 10.6258 | 0.0082
GEN-2022-016 | 04 SOUTHEAST | 539804 | THISTLE4 | 138 | 17.3245 | 17.3465 | 0.022
GEN-2022-016 | 04 SOUTHEAST | 539813 | TRANSFORMER | 345 | 8.8828 | 8.8911 | 0.0083
GEN-2022-016 | 04 SOUTHEAST | 539840 | GEN-2011-008 | 345 | 8.5035 | 8.5112 | 0.0077
GEN-2022-016 | 04 SOUTHEAST | 539841 | G-2011-008-1 | 345 | 7.3253 | 7.331 | 0.0057
GEN-2022-016 | 04 SOUTHEAST | 539855 | G-2011-008-2 | 345 | 7.3235 | 7.3292 | 0.0057
GEN-2022-016 | 04 SOUTHEAST | 539857 | G-2011-008-3 | 345 | 6.8763 | 6.8814 | 0.0051
GEN-2022-016 | 04 SOUTHEAST | 560071 | G16-003-TAP | 345 | 14.5642 | 14.7941 | 0.2299
GEN-2022-016 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 7.5949 | 7.5951 | 0.0002
GEN-2022-016 | 04 SOUTHEAST | 560080 | G16-046-TAP | 345 | 9.2024 | 9.2102 | 0.0078
GEN-2022-016 | 04 SOUTHEAST | 576397 | G10014G11022 | 345 | 8.039 | 8.0573 | 0.0183
GEN-2022-016 | 04 SOUTHEAST | 585190 | GEN-2015-082 | 345 | 6.3604 | 6.3833 | 0.0229
GEN-2022-016 | 04 SOUTHEAST | 585440 | PRSIMN_CRK2 | 345 | 10.4215 | 10.5672 | 0.1457
GEN-2022-016 | 04 SOUTHEAST | 587140 | GEN-2016-020 | 138 | 8.0751 | 8.078 | 0.0029
GEN-2022-016 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 7.3368 | 7.337 | 0.0002
GEN-2022-016 | 04 SOUTHEAST | 587310 | GEN-2016-046 | 345 | 8.1803 | 8.1865 | 0.0062
GEN-2022-016 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.947 | 15.9494 | 0.0024
GEN-2022-016 | 04 SOUTHEAST | 588560 | GEN-2017-011 | 345 | 11.9257 | 12.0795 | 0.1538
GEN-2022-016 | 04 SOUTHEAST | 588630 | GEN-2017-018 | 345 | 15.2874 | 15.3415 | 0.0541
GEN-2022-016 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 4.961 | 4.9611 | 0.0001
GEN-2022-016 | 04 SOUTHEAST | 760284 | GEN-2017-220 | 345 | 19.104 | 19.1232 | 0.0192
GEN-2022-016 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 23.3969 | 23.4043 | 0.0074
GEN-2022-016 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 7.0936 | 7.0946 | 0.001
GEN-2022-016 | 04 SOUTHEAST | 762217 | GEN-2017-151 | 345 | 5.2664 | 5.267 | 0.0006
GEN-2022-016 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.7139 | 11.7165 | 0.0026
GEN-2022-016 | 04 SOUTHEAST | 762467 | G18-015-TAP | 345 | 4.4182 | 4.4185 | 0.0003
GEN-2022-016 | 04 SOUTHEAST | 762834 | GEN-2018-049 | 345 | 6.6882 | 6.6985 | 0.0103
GEN-2022-016 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 17.6421 | 18.0937 | 0.4516
GEN-2022-016 | 04 SOUTHEAST | 763670 | GEN-2019-030 | 345 | 7.7789 | 7.7841 | 0.0052
GEN-2022-016 | 04 SOUTHEAST | 763677 | G19-030-TAP | 345 | 9.2456 | 9.2529 | 0.0073
GEN-2022-016 | 04 SOUTHEAST | 763769 | GEN-2019-045 | 138 | 15.854 | 15.8955 | 0.0415
GEN-2022-016 | 04 SOUTHEAST | 763890 | GEN-2019-058 | 345 | 10.0231 | 10.0337 | 0.0106
GEN-2022-016 | 04 SOUTHEAST | 764935 | GEN-2020-067 | 345 | 5.7688 | 5.7691 | 0.0003
GEN-2022-016 | 04 SOUTHEAST | 764945 | G20-067-TAP | 345 | 6.9919 | 6.9924 | 0.0005
GEN-2022-016 | 04 SOUTHEAST | 765215 | G20-010-TAP | 138 | 8.0686 | 8.0729 | 0.0043
GEN-2022-016 | 04 SOUTHEAST | 765530 | GEN-2021-025 | 138 | 18.4357 | 18.4523 | 0.0166
GEN-2022-016 | 04 SOUTHEAST | 767221 | GEN-2022-012 | 345 | 19.6794 | 20.2455 | 0.5661
GEN-2022-016 | 04 SOUTHEAST | 767301 | GEN-2022-016 | 345 | 19.6821 | 20.2647 | 0.5826
GEN-2022-016 | 04 SOUTHEAST | 767321 | GEN-2022-017 | 345 | 19.4243 | 19.9912 | 0.5669
GEN-2022-016 | 04 SOUTHEAST | 769921 | GEN-2022-147 | 345 | 11.1147 | 11.1175 | 0.0028
GEN-2022-016 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.1196 | 7.1213 | 0.0017
GEN-2022-016 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.6919 | 5.6929 | 0.001
GEN-2022-016 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.3592 | 6.3605 | 0.0013
GEN-2022-017 | 04 SOUTHEAST | 511409 | TREASILD7 | 345 | 16.206 | 16.2068 | 0.0008
GEN-2022-017 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.6306 | 10.6309 | 0.0003
GEN-2022-017 | 04 SOUTHEAST | 511458 | ELKCTY-4 | 138 | 11.0367 | 11.037 | 0.0003
GEN-2022-017 | 04 SOUTHEAST | 511490 | ELKCITY6 | 230 | 6.6318 | 6.6319 | 0.0001
GEN-2022-017 | 04 SOUTHEAST | 511541 | SWEETWT6 | 230 | 7.3595 | 7.3597 | 0.0002
GEN-2022-017 | 04 SOUTHEAST | 511542 | BUFFCK6 | 230 | 5.6376 | 5.6377 | 0.0001
GEN-2022-017 | 04 SOUTHEAST | 511544 | DEMPSEY6 | 230 | 4.713 | 4.7131 | 0.0001
GEN-2022-017 | 04 SOUTHEAST | 511547 | ROARK6 | 230 | 4.6678 | 4.6678 | 0
GEN-2022-017 | 04 SOUTHEAST | 511553 | CHISHOLM7 | 345 | 5.8781 | 5.8782 | 0.0001
GEN-2022-017 | 04 SOUTHEAST | 511557 | CHISHOLM6 | 230 | 8.5716 | 8.5718 | 0.0002
GEN-2022-017 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 20.2979 | 20.2994 | 0.0015
GEN-2022-017 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 19.6722 | 19.6762 | 0.004
GEN-2022-017 | 04 SOUTHEAST | 514773 | NEWMAN 2 | 69 | 1.6718 | 1.672 | 0.0002
GEN-2022-017 | 04 SOUTHEAST | 514775 | TANGRTP2 | 69 | 5.314 | 5.3152 | 0.0012
GEN-2022-017 | 04 SOUTHEAST | 514776 | NEWGRTP2 | 69 | 6.0369 | 6.0384 | 0.0015
GEN-2022-017 | 04 SOUTHEAST | 514778 | CLEOCOR4 | 138 | 6.6423 | 6.6427 | 0.0004
GEN-2022-017 | 04 SOUTHEAST | 514779 | WDNITRO2 | 69 | 5.3066 | 5.3078 | 0.0012
GEN-2022-017 | 04 SOUTHEAST | 514781 | CEDARAV2 | 69 | 6.329 | 6.3307 | 0.0017
GEN-2022-017 | 04 SOUTHEAST | 514782 | WODWRD 2 | 69 | 12.4023 | 12.4089 | 0.0066
GEN-2022-017 | 04 SOUTHEAST | 514785 | WOODWRD4 | 138 | 18.2155 | 18.2588 | 0.0433
GEN-2022-017 | 04 SOUTHEAST | 514787 | DEWEY 4 | 138 | 8.544 | 8.547 | 0.003
GEN-2022-017 | 04 SOUTHEAST | 514788 | GLASMTN4 | 138 | 5.4166 | 5.4171 | 0.0005
GEN-2022-017 | 04 SOUTHEAST | 514792 | ALVAOGE2 | 69 | 7.6989 | 7.7004 | 0.0015
GEN-2022-017 | 04 SOUTHEAST | 514794 | KNOBHIL2 | 69 | 9.0337 | 9.0359 | 0.0022
GEN-2022-017 | 04 SOUTHEAST | 514795 | KNOBHIL4 | 138 | 10.226 | 10.2333 | 0.0073
GEN-2022-017 | 04 SOUTHEAST | 514796 | IODINE-4 | 138 | 7.9114 | 7.9183 | 0.0069
GEN-2022-017 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 24.1925 | 24.1967 | 0.0042
GEN-2022-017 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.8506 | 17.8519 | 0.0013
GEN-2022-017 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 19.5832 | 19.5845 | 0.0013
GEN-2022-017 | 04 SOUTHEAST | 514828 | KETCHTP4 | 138 | 28.2512 | 28.2532 | 0.002
GEN-2022-017 | 04 SOUTHEAST | 514854 | BRADEN 4 | 138 | 33.4496 | 33.4535 | 0.0039
GEN-2022-017 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 28.0748 | 28.0773 | 0.0025
GEN-2022-017 | 04 SOUTHEAST | 514864 | PIEDMNT4 | 138 | 23.7392 | 23.7412 | 0.002
GEN-2022-017 | 04 SOUTHEAST | 514873 | LNEOAK 4 | 138 | 28.6753 | 28.6782 | 0.0029
GEN-2022-017 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 47.0206 | 47.0292 | 0.0086
GEN-2022-017 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.1092 | 35.126 | 0.0168
GEN-2022-017 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.633 | 24.6397 | 0.0067
GEN-2022-017 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 30.2731 | 30.2753 | 0.0022
GEN-2022-017 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.2463 | 20.2473 | 0.001
GEN-2022-017 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 47.2567 | 47.2649 | 0.0082
GEN-2022-017 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 37.6829 | 37.7045 | 0.0216
GEN-2022-017 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 43.2779 | 43.2808 | 0.0029
GEN-2022-017 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.2134 | 28.2163 | 0.0029
GEN-2022-017 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.2556 | 27.258 | 0.0024
GEN-2022-017 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.0651 | 27.0684 | 0.0033
GEN-2022-017 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.8882 | 29.8897 | 0.0015
GEN-2022-017 | 04 SOUTHEAST | 515363 | CENT 4 | 138 | 3.4018 | 3.4029 | 0.0011
GEN-2022-017 | 04 SOUTHEAST | 515375 | WWRDEHV7 | 345 | 20.2199 | 20.5292 | 0.3093
GEN-2022-017 | 04 SOUTHEAST | 515376 | WWRDEHV4 | 138 | 26.3254 | 26.4572 | 0.1318
GEN-2022-017 | 04 SOUTHEAST | 515390 | TLGAWND4 | 138 | 4.2844 | 4.285 | 0.0006
GEN-2022-017 | 04 SOUTHEAST | 515394 | KEENAN 4 | 138 | 9.1995 | 9.2142 | 0.0147
GEN-2022-017 | 04 SOUTHEAST | 515398 | OUSPRT 4 | 138 | 10.0734 | 10.0913 | 0.0179
GEN-2022-017 | 04 SOUTHEAST | 515407 | TATONGA7 | 345 | 17.9335 | 18.0193 | 0.0858
GEN-2022-017 | 04 SOUTHEAST | 515425 | WWDPST 4 | 138 | 19.7656 | 19.8239 | 0.0583
GEN-2022-017 | 04 SOUTHEAST | 515444 | MCNOWND7 | 345 | 24.0961 | 24.1002 | 0.0041
GEN-2022-017 | 04 SOUTHEAST | 515448 | CRSRDSW7 | 345 | 12.5118 | 12.5525 | 0.0407
GEN-2022-017 | 04 SOUTHEAST | 515458 | BORDER 7 | 345 | 4.5165 | 4.5249 | 0.0084
GEN-2022-017 | 04 SOUTHEAST | 515476 | HUNTERS7 | 345 | 14.0124 | 14.0145 | 0.0021
GEN-2022-017 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 35.0106 | 35.0446 | 0.034
GEN-2022-017 | 04 SOUTHEAST | 515533 | REDCLFT4 | 138 | 7.2464 | 7.2508 | 0.0044
GEN-2022-017 | 04 SOUTHEAST | 515549 | MNCWND37 | 345 | 15.0253 | 15.0268 | 0.0015
GEN-2022-017 | 04 SOUTHEAST | 515554 | BVRCNTY7 | 345 | 12.0315 | 12.0618 | 0.0303
GEN-2022-017 | 04 SOUTHEAST | 515560 | CZYCRVT2 | 69 | 3.4124 | 3.4125 | 0.0001
GEN-2022-017 | 04 SOUTHEAST | 515582 | SLNGWND7 | 345 | 8.7291 | 8.7481 | 0.019
GEN-2022-017 | 04 SOUTHEAST | 515585 | MAMTHPW7 | 345 | 14.1433 | 14.195 | 0.0517
GEN-2022-017 | 04 SOUTHEAST | 515590 | PALDR2W7 | 345 | 10.848 | 10.8716 | 0.0236
GEN-2022-017 | 04 SOUTHEAST | 515600 | KNGFSHR7 | 345 | 12.5801 | 12.5819 | 0.0018
GEN-2022-017 | 04 SOUTHEAST | 515605 | CANADN7 | 345 | 13.7129 | 13.7151 | 0.0022
GEN-2022-017 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.8441 | 18.8486 | 0.0045
GEN-2022-017 | 04 SOUTHEAST | 515618 | BALKOW 7 | 345 | 10.428 | 10.4503 | 0.0223
GEN-2022-017 | 04 SOUTHEAST | 515634 | PALDR1W7 | 345 | 9.834 | 9.8525 | 0.0185
GEN-2022-017 | 04 SOUTHEAST | 515677 | BADGER 7 | 345 | 11.7394 | 11.7802 | 0.0408
GEN-2022-017 | 04 SOUTHEAST | 515686 | BLUWND 7 | 345 | 10.6892 | 10.7231 | 0.0339
GEN-2022-017 | 04 SOUTHEAST | 515785 | WINDFRM4 | 138 | 22.9848 | 22.9992 | 0.0144
GEN-2022-017 | 04 SOUTHEAST | 515786 | FPLWIND4 | 138 | 7.3079 | 7.3091 | 0.0012
GEN-2022-017 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 18.8975 | 18.8989 | 0.0014
GEN-2022-017 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 34.0082 | 34.0089 | 0.0007
GEN-2022-017 | 04 SOUTHEAST | 515825 | GRTWSRN7 | 345 | 9.5728 | 9.635 | 0.0622
GEN-2022-017 | 04 SOUTHEAST | 515852 | DGRASSE7 | 345 | 14.3916 | 14.4639 | 0.0723
GEN-2022-017 | 04 SOUTHEAST | 515853 | DGRASSE4 | 138 | 15.8737 | 15.8955 | 0.0218
GEN-2022-017 | 04 SOUTHEAST | 515863 | REDCLF 4 | 138 | 7.2303 | 7.2347 | 0.0044
GEN-2022-017 | 04 SOUTHEAST | 515875 | REDNGTN7 | 345 | 17.56 | 17.5653 | 0.0053
GEN-2022-017 | 04 SOUTHEAST | 515877 | REDDIRT7 | 345 | 17.5555 | 17.5608 | 0.0053
GEN-2022-017 | 04 SOUTHEAST | 515951 | PERSIMN7 | 345 | 11.4223 | 11.514 | 0.0917
GEN-2022-017 | 04 SOUTHEAST | 515961 | GUTHRIE7 | 345 | 12.9601 | 13.0791 | 0.119
GEN-2022-017 | 04 SOUTHEAST | 515964 | CANTNLK4 | 138 | 5.1781 | 5.1788 | 0.0007
GEN-2022-017 | 04 SOUTHEAST | 515990 | SKELTON7 | 345 | 4.6878 | 4.688 | 0.0002
GEN-2022-017 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.5431 | 17.5449 | 0.0018
GEN-2022-017 | 04 SOUTHEAST | 516059 | BECKHAM7 | 345 | 5.0873 | 5.0995 | 0.0122
GEN-2022-017 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 28.1463 | 28.1509 | 0.0046
GEN-2022-017 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 44.4348 | 44.4382 | 0.0034
GEN-2022-017 | 04 SOUTHEAST | 516146 | 25MILE 7 | 345 | 10.3121 | 10.3701 | 0.058
GEN-2022-017 | 04 SOUTHEAST | 516159 | 25MILZ 7 | 345 | 10.3008 | 10.3587 | 0.0579
GEN-2022-017 | 04 SOUTHEAST | 520425 | PIC4 | 138 | 8.6427 | 8.6444 | 0.0017
GEN-2022-017 | 04 SOUTHEAST | 520430 | NOELSW 4 | 138 | 10.2881 | 10.2955 | 0.0074
GEN-2022-017 | 04 SOUTHEAST | 520436 | ROSEVLY4 | 138 | 11.947 | 11.9587 | 0.0117
GEN-2022-017 | 04 SOUTHEAST | 520437 | SALTPLN4 | 138 | 6.4969 | 6.499 | 0.0021
GEN-2022-017 | 04 SOUTHEAST | 520462 | ASPEN 4 | 138 | 22.595 | 22.6085 | 0.0135
GEN-2022-017 | 04 SOUTHEAST | 520500 | BEARCAT4 | 138 | 16.1099 | 16.1164 | 0.0065
GEN-2022-017 | 04 SOUTHEAST | 520553 | SEILING4 | 138 | 7.6811 | 7.683 | 0.0019
GEN-2022-017 | 04 SOUTHEAST | 520601 | AVARD 4 | 138 | 6.8692 | 6.8731 | 0.0039
GEN-2022-017 | 04 SOUTHEAST | 520848 | CDRDLTP4 | 138 | 6.0788 | 6.0794 | 0.0006
GEN-2022-017 | 04 SOUTHEAST | 520920 | FTSUPLY4 | 138 | 5.8036 | 5.8044 | 0.0008
GEN-2022-017 | 04 SOUTHEAST | 520957 | IODINE 4 | 138 | 8.4777 | 8.4795 | 0.0018
GEN-2022-017 | 04 SOUTHEAST | 520995 | MOORLND2 | 69 | 9.2266 | 9.2284 | 0.0018
GEN-2022-017 | 04 SOUTHEAST | 520999 | MOORLND4 | 138 | 23.5281 | 23.5427 | 0.0146
GEN-2022-017 | 04 SOUTHEAST | 521065 | TALOGA 4 | 138 | 8.401 | 8.4036 | 0.0026
GEN-2022-017 | 04 SOUTHEAST | 521082 | VICI 2 | 69 | 4.0907 | 4.0911 | 0.0004
GEN-2022-017 | 04 SOUTHEAST | 521096 | WOODWRD2 | 69 | 10.927 | 10.9308 | 0.0038
GEN-2022-017 | 04 SOUTHEAST | 521196 | FARGOJCT2 | 69 | 8.2184 | 8.2204 | 0.002
GEN-2022-017 | 04 SOUTHEAST | 521197 | CRTSJCT2 | 69 | 8.8067 | 8.8084 | 0.0017
GEN-2022-017 | 04 SOUTHEAST | 523095 | HITCHLAND 6 | 230 | 12.3284 | 12.3402 | 0.0118
GEN-2022-017 | 04 SOUTHEAST | 523097 | HITCHLAND 7 | 345 | 11.2831 | 11.302 | 0.0189
GEN-2022-017 | 04 SOUTHEAST | 523101 | NOBLE_WND 7 | 345 | 11.2484 | 11.2671 | 0.0187
GEN-2022-017 | 04 SOUTHEAST | 523112 | NOVUS1 7 | 345 | 11.1042 | 11.1224 | 0.0182
GEN-2022-017 | 04 SOUTHEAST | 523777 | WHEELER 6 | 230 | 5.7823 | 5.7824 | 0.0001
GEN-2022-017 | 04 SOUTHEAST | 523823 | CARPENTER 7 | 345 | 6.2327 | 6.2357 | 0.003
GEN-2022-017 | 04 SOUTHEAST | 523961 | POTTER_CO 7 | 345 | 9.7739 | 9.7761 | 0.0022
GEN-2022-017 | 04 SOUTHEAST | 525213 | SWISHER 6 | 230 | 10.6375 | 10.6378 | 0.0003
GEN-2022-017 | 04 SOUTHEAST | 525531 | TOLK 6 | 230 | 26.5429 | 26.5433 | 0.0004
GEN-2022-017 | 04 SOUTHEAST | 525828 | TUCO_INT 3 | 115 | 18.8261 | 18.8265 | 0.0004
GEN-2022-017 | 04 SOUTHEAST | 525830 | TUCO_INT 6 | 230 | 22.528 | 22.5297 | 0.0017
GEN-2022-017 | 04 SOUTHEAST | 525832 | TUCO_INT 7 | 345 | 11.2144 | 11.2159 | 0.0015
GEN-2022-017 | 04 SOUTHEAST | 525840 | ANTELOPE_1 6 | 230 | 22.3417 | 22.3433 | 0.0016
GEN-2022-017 | 04 SOUTHEAST | 525850 | ELK_CT1 | 345 | 11.1406 | 11.1421 | 0.0015
GEN-2022-017 | 04 SOUTHEAST | 525957 | HALE_WNDCL16 | 230 | 12.224 | 12.2244 | 0.0004
GEN-2022-017 | 04 SOUTHEAST | 526161 | CARLISLE 6 | 230 | 10.7148 | 10.715 | 0.0002
GEN-2022-017 | 04 SOUTHEAST | 526337 | JONES 6 | 230 | 17.7994 | 17.7997 | 0.0003
GEN-2022-017 | 04 SOUTHEAST | 526936 | YOAKUM_345 | 345 | 10.397 | 10.3971 | 0.0001
GEN-2022-017 | 04 SOUTHEAST | 531469 | SPERVIL7 | 345 | 11.0791 | 11.0836 | 0.0045
GEN-2022-017 | 04 SOUTHEAST | 532771 | RENO 7 | 345 | 11.0248 | 11.026 | 0.0012
GEN-2022-017 | 04 SOUTHEAST | 532782 | BUFFALO7 | 345 | 19.2119 | 19.2221 | 0.0102
GEN-2022-017 | 04 SOUTHEAST | 532783 | KINGMAN7 | 345 | 7.2088 | 7.2098 | 0.001
GEN-2022-017 | 04 SOUTHEAST | 532784 | NINN1WF7 | 345 | 6.0162 | 6.0168 | 0.0006
GEN-2022-017 | 04 SOUTHEAST | 532791 | BENTON 7 | 345 | 18.4656 | 18.469 | 0.0034
GEN-2022-017 | 04 SOUTHEAST | 532796 | WICHITA7 | 345 | 22.0319 | 22.0413 | 0.0094
GEN-2022-017 | 04 SOUTHEAST | 532798 | VIOLA 7 | 345 | 13.4736 | 13.4763 | 0.0027
GEN-2022-017 | 04 SOUTHEAST | 532803 | BURNS 7 | 345 | 10.4596 | 10.4604 | 0.0008
GEN-2022-017 | 04 SOUTHEAST | 533040 | EVANS N4 | 138 | 27.9615 | 27.9662 | 0.0047
GEN-2022-017 | 04 SOUTHEAST | 539631 | FLATRWD4 | 138 | 10.3894 | 10.3932 | 0.0038
GEN-2022-017 | 04 SOUTHEAST | 539638 | FLATRDG4 | 138 | 15.4308 | 15.4393 | 0.0085
GEN-2022-017 | 04 SOUTHEAST | 539668 | HARPER 4 | 138 | 7.4345 | 7.4355 | 0.001
GEN-2022-017 | 04 SOUTHEAST | 539674 | BARBER 4 | 138 | 8.3529 | 8.355 | 0.0021
GEN-2022-017 | 04 SOUTHEAST | 539800 | CLARKCOUNTY7 | 345 | 10.1951 | 10.2008 | 0.0057
GEN-2022-017 | 04 SOUTHEAST | 539801 | THISTLE7 | 345 | 15.3131 | 15.3415 | 0.0284
GEN-2022-017 | 04 SOUTHEAST | 539803 | IRONWOOD7 | 345 | 10.6215 | 10.6258 | 0.0043
GEN-2022-017 | 04 SOUTHEAST | 539804 | THISTLE4 | 138 | 17.335 | 17.3465 | 0.0115
GEN-2022-017 | 04 SOUTHEAST | 539813 | TRANSFORMER | 345 | 8.8867 | 8.8911 | 0.0044
GEN-2022-017 | 04 SOUTHEAST | 539840 | GEN-2011-008 | 345 | 8.5072 | 8.5112 | 0.004
GEN-2022-017 | 04 SOUTHEAST | 539841 | G-2011-008-1 | 345 | 7.328 | 7.331 | 0.003
GEN-2022-017 | 04 SOUTHEAST | 539855 | G-2011-008-2 | 345 | 7.3262 | 7.3292 | 0.003
GEN-2022-017 | 04 SOUTHEAST | 539857 | G-2011-008-3 | 345 | 6.8787 | 6.8814 | 0.0027
GEN-2022-017 | 04 SOUTHEAST | 560071 | G16-003-TAP | 345 | 14.6726 | 14.7941 | 0.1215
GEN-2022-017 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 7.5949 | 7.5951 | 0.0002
GEN-2022-017 | 04 SOUTHEAST | 560080 | G16-046-TAP | 345 | 9.2061 | 9.2102 | 0.0041
GEN-2022-017 | 04 SOUTHEAST | 576397 | G10014G11022 | 345 | 8.0476 | 8.0573 | 0.0097
GEN-2022-017 | 04 SOUTHEAST | 585190 | GEN-2015-082 | 345 | 6.3713 | 6.3833 | 0.012
GEN-2022-017 | 04 SOUTHEAST | 585440 | PRSIMN_CRK2 | 345 | 10.4903 | 10.5672 | 0.0769
GEN-2022-017 | 04 SOUTHEAST | 587140 | GEN-2016-020 | 138 | 8.0764 | 8.078 | 0.0016
GEN-2022-017 | 04 SOUTHEAST | 587230 | GEN-2016-037 | 345 | 7.3368 | 7.337 | 0.0002
GEN-2022-017 | 04 SOUTHEAST | 587310 | GEN-2016-046 | 345 | 8.1832 | 8.1865 | 0.0033
GEN-2022-017 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.9481 | 15.9494 | 0.0013
GEN-2022-017 | 04 SOUTHEAST | 588560 | GEN-2017-011 | 345 | 11.9984 | 12.0795 | 0.0811
GEN-2022-017 | 04 SOUTHEAST | 588630 | GEN-2017-018 | 345 | 15.3131 | 15.3415 | 0.0284
GEN-2022-017 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 4.9611 | 4.9611 | 0
GEN-2022-017 | 04 SOUTHEAST | 760284 | GEN-2017-220 | 345 | 19.1131 | 19.1232 | 0.0101
GEN-2022-017 | 04 SOUTHEAST | 761250 | GEN-2017-233 | 345 | 23.4004 | 23.4043 | 0.0039
GEN-2022-017 | 04 SOUTHEAST | 762216 | G17-151TAP | 345 | 7.0941 | 7.0946 | 0.0005
GEN-2022-017 | 04 SOUTHEAST | 762217 | GEN-2017-151 | 345 | 5.2667 | 5.267 | 0.0003
GEN-2022-017 | 04 SOUTHEAST | 762321 | GEN-2017-164 | 345 | 11.7151 | 11.7165 | 0.0014
GEN-2022-017 | 04 SOUTHEAST | 762467 | G18-015-TAP | 345 | 4.4183 | 4.4185 | 0.0002
GEN-2022-017 | 04 SOUTHEAST | 762834 | GEN-2018-049 | 345 | 6.6931 | 6.6985 | 0.0054
GEN-2022-017 | 04 SOUTHEAST | 763527 | GEN-2019-012 | 345 | 17.8541 | 18.0937 | 0.2396
GEN-2022-017 | 04 SOUTHEAST | 763670 | GEN-2019-030 | 345 | 7.7814 | 7.7841 | 0.0027
GEN-2022-017 | 04 SOUTHEAST | 763677 | G19-030-TAP | 345 | 9.2491 | 9.2529 | 0.0038
GEN-2022-017 | 04 SOUTHEAST | 763769 | GEN-2019-045 | 138 | 15.8737 | 15.8955 | 0.0218
GEN-2022-017 | 04 SOUTHEAST | 763890 | GEN-2019-058 | 345 | 10.0281 | 10.0337 | 0.0056
GEN-2022-017 | 04 SOUTHEAST | 764935 | GEN-2020-067 | 345 | 5.769 | 5.7691 | 0.0001
GEN-2022-017 | 04 SOUTHEAST | 764945 | G20-067-TAP | 345 | 6.9921 | 6.9924 | 0.0003
GEN-2022-017 | 04 SOUTHEAST | 765215 | G20-010-TAP | 138 | 8.0707 | 8.0729 | 0.0022
GEN-2022-017 | 04 SOUTHEAST | 765530 | GEN-2021-025 | 138 | 18.4436 | 18.4523 | 0.0087
GEN-2022-017 | 04 SOUTHEAST | 767221 | GEN-2022-012 | 345 | 19.9447 | 20.2455 | 0.3008
GEN-2022-017 | 04 SOUTHEAST | 767301 | GEN-2022-016 | 345 | 19.955 | 20.2647 | 0.3097
GEN-2022-017 | 04 SOUTHEAST | 767321 | GEN-2022-017 | 345 | 19.6814 | 19.9912 | 0.3098
GEN-2022-017 | 04 SOUTHEAST | 769921 | GEN-2022-147 | 345 | 11.1161 | 11.1175 | 0.0014
GEN-2022-017 | 04 SOUTHEAST | 900001 | TRAVERSE3 | 345 | 7.1204 | 7.1213 | 0.0009
GEN-2022-017 | 04 SOUTHEAST | 900002 | TRAVERSE-2 | 345 | 5.6924 | 5.6929 | 0.0005
GEN-2022-017 | 04 SOUTHEAST | 900004 | TRW2-TRW3 | 345 | 6.3598 | 6.3605 | 0.0007
GEN-2022-038 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 22.1167 | 22.1506 | 0.0339
GEN-2022-038 | 04 SOUTHEAST | 337361 | 3MINDEN_LA! | 115 | 7.013 | 7.0141 | 0.0011
GEN-2022-038 | 04 SOUTHEAST | 337363 | 3SAREPTA! | 115 | 20.3589 | 20.3788 | 0.0199
GEN-2022-038 | 04 SOUTHEAST | 337364 | 3CULLEN | 115 | 8.6629 | 8.6668 | 0.0039
GEN-2022-038 | 04 SOUTHEAST | 337365 | 3SPRINGHILL | 115 | 10.002 | 10.0059 | 0.0039
GEN-2022-038 | 04 SOUTHEAST | 337366 | 3HAYNESVILLE | 115 | 6.0652 | 6.0661 | 0.0009
GEN-2022-038 | 04 SOUTHEAST | 337376 | 7SAREPTA% | 345 | 10.1635 | 10.1821 | 0.0186
GEN-2022-038 | 04 SOUTHEAST | 337561 | 8EL DORADO% | 500 | 27.8035 | 27.8077 | 0.0042
GEN-2022-038 | 04 SOUTHEAST | 337562 | 7EL DORADO | 345 | 14.2155 | 14.2205 | 0.005
GEN-2022-038 | 04 SOUTHEAST | 500250 | DOLHILL7 | 345 | 12.6966 | 12.7126 | 0.016
GEN-2022-038 | 04 SOUTHEAST | 500260 | DOLHILL6 | 230 | 15.4981 | 15.5097 | 0.0116
GEN-2022-038 | 04 SOUTHEAST | 507710 | ARSHILL2 | 69 | 28.7358 | 28.8469 | 0.1111
GEN-2022-038 | 04 SOUTHEAST | 507711 | ARSHILL4 | 138 | 26.185 | 26.3645 | 0.1795
GEN-2022-038 | 04 SOUTHEAST | 507717 | BROOKS 2 | 69 | 20.8897 | 20.948 | 0.0583
GEN-2022-038 | 04 SOUTHEAST | 507726 | FLOURNY2 | 69 | 14.3682 | 14.3989 | 0.0307
GEN-2022-038 | 04 SOUTHEAST | 507727 | FLOURNY4 | 138 | 17.4202 | 17.5307 | 0.1105
GEN-2022-038 | 04 SOUTHEAST | 507730 | FTHUMBG2 | 69 | 18.4086 | 18.4531 | 0.0445
GEN-2022-038 | 04 SOUTHEAST | 507731 | FTHUMBG4 | 138 | 20.2578 | 20.3631 | 0.1053
GEN-2022-038 | 04 SOUTHEAST | 507732 | GENMOTR4 | 138 | 18.6789 | 18.7887 | 0.1098
GEN-2022-038 | 04 SOUTHEAST | 507738 | LINWOOD4 | 138 | 23.5093 | 23.6337 | 0.1244
GEN-2022-038 | 04 SOUTHEAST | 507742 | MCWILLI4 | 138 | 22.2197 | 22.3373 | 0.1176
GEN-2022-038 | 04 SOUTHEAST | 507745 | NMARKET2 | 69 | 16.4983 | 16.5352 | 0.0369
GEN-2022-038 | 04 SOUTHEAST | 507746 | PIERMNT4 | 138 | 17.1112 | 17.1819 | 0.0707
GEN-2022-038 | 04 SOUTHEAST | 507747 | PINESRD2 | 69 | 10.9707 | 10.9877 | 0.017
GEN-2022-038 | 04 SOUTHEAST | 507748 | POWELL 4 | 138 | 20.4116 | 20.5013 | 0.0897
GEN-2022-038 | 04 SOUTHEAST | 507749 | RAINES 4 | 138 | 16.9903 | 17.1326 | 0.1423
GEN-2022-038 | 04 SOUTHEAST | 507755 | S SHV 4 | 138 | 24.3562 | 24.4859 | 0.1297
GEN-2022-038 | 04 SOUTHEAST | 507756 | SHEDRD 2 | 69 | 17.7123 | 17.7548 | 0.0425
GEN-2022-038 | 04 SOUTHEAST | 507757 | SPRIDGE4 | 138 | 11.8009 | 11.8223 | 0.0214
GEN-2022-038 | 04 SOUTHEAST | 507759 | SW SHV 4 | 138 | 32.7434 | 32.9515 | 0.2081
GEN-2022-038 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.4791 | 16.5784 | 0.0993
GEN-2022-038 | 04 SOUTHEAST | 507763 | TRICHEL4 | 138 | 16.9666 | 17.0419 | 0.0753
GEN-2022-038 | 04 SOUTHEAST | 507766 | WATERWK2 | 69 | 17.2643 | 17.3035 | 0.0392
GEN-2022-038 | 04 SOUTHEAST | 507770 | WOOLWTP2 | 69 | 11.9953 | 12.0159 | 0.0206
GEN-2022-038 | 04 SOUTHEAST | 507774 | NORAM 4 | 138 | 17.7719 | 18.0115 | 0.2396
GEN-2022-038 | 04 SOUTHEAST | 507789 | STLGENS4 | 138 | 25.7744 | 25.9424 | 0.168
GEN-2022-038 | 04 SOUTHEAST | 507793 | LEASIDE 4 | 138 | 23.478 | 23.5869 | 0.1089
GEN-2022-038 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.6797 | 7.681 | 0.0013
GEN-2022-038 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 14.5397 | 14.5454 | 0.0057
GEN-2022-038 | 04 SOUTHEAST | 508090 | WATLANT4 | 138 | 7.8599 | 7.8614 | 0.0015
GEN-2022-038 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 18.2501 | 18.2629 | 0.0128
GEN-2022-038 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.9986 | 14.005 | 0.0064
GEN-2022-038 | 04 SOUTHEAST | 508355 | WELSHRE4 | 138 | 7.8578 | 7.86 | 0.0022
GEN-2022-038 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 22.1167 | 22.1506 | 0.0339
GEN-2022-038 | 04 SOUTHEAST | 508557 | MARSHL-4 | 138 | 17.4526 | 17.478 | 0.0254
GEN-2022-038 | 04 SOUTHEAST | 508562 | PIRKEY 4 | 138 | 43.6375 | 43.7802 | 0.1427
GEN-2022-038 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 18.4859 | 18.5242 | 0.0383
GEN-2022-038 | 04 SOUTHEAST | 508566 | SABMINT4 | 138 | 35.5285 | 35.6569 | 0.1284
GEN-2022-038 | 04 SOUTHEAST | 508567 | SCOTTSV4 | 138 | 12.6261 | 12.8523 | 0.2262
GEN-2022-038 | 04 SOUTHEAST | 508569 | SEMRSHL4 | 138 | 14.0137 | 14.1617 | 0.148
GEN-2022-038 | 04 SOUTHEAST | 508577 | SABINEM4 | 138 | 23.3654 | 23.4213 | 0.0559
GEN-2022-038 | 04 SOUTHEAST | 508595 | HALLSVLS4 | 138 | 19.4882 | 19.5071 | 0.0189
GEN-2022-038 | 04 SOUTHEAST | 508801 | BLANCH-2 | 69 | 7.0765 | 7.0848 | 0.0083
GEN-2022-038 | 04 SOUTHEAST | 508802 | BLANCHR2 | 69 | 7.9291 | 7.9386 | 0.0095
GEN-2022-038 | 04 SOUTHEAST | 508805 | LIEBERM2 | 69 | 9.3935 | 9.4098 | 0.0163
GEN-2022-038 | 04 SOUTHEAST | 508806 | LIEBERM4 | 138 | 17.4964 | 17.675 | 0.1786
GEN-2022-038 | 04 SOUTHEAST | 508807 | LINTNRD4 | 138 | 9.3112 | 9.3466 | 0.0354
GEN-2022-038 | 04 SOUTHEAST | 508808 | LONGWD 4 | 138 | 25.543 | 26.2132 | 0.6702
GEN-2022-038 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 16.4582 | 16.5842 | 0.126
GEN-2022-038 | 04 SOUTHEAST | 508810 | NBENTON2 | 69 | 4.2147 | 4.2178 | 0.0031
GEN-2022-038 | 04 SOUTHEAST | 508811 | NBENTON4 | 138 | 9.638 | 9.6778 | 0.0398
GEN-2022-038 | 04 SOUTHEAST | 508812 | OILCITY2 | 69 | 7.5468 | 7.5559 | 0.0091
GEN-2022-038 | 04 SOUTHEAST | 508815 | SUPEROR2 | 69 | 7.0223 | 7.0285 | 0.0062
GEN-2022-038 | 04 SOUTHEAST | 508816 | OAKPH 4 | 138 | 20.0748 | 20.4388 | 0.364
GEN-2022-038 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.9713 | 30.0091 | 0.0378
GEN-2022-038 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 20.1172 | 20.1598 | 0.0426
GEN-2022-038 | 04 SOUTHEAST | 508833 | IPCJEFF4 | 138 | 12.7486 | 12.7679 | 0.0193
GEN-2022-038 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 14.0816 | 14.1027 | 0.0211
GEN-2022-038 | 04 SOUTHEAST | 508839 | WASKOM 2 | 69 | 4.6564 | 4.6592 | 0.0028
GEN-2022-038 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 31.7418 | 31.7808 | 0.039
GEN-2022-038 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 16.3915 | 16.4302 | 0.0387
GEN-2022-038 | 04 SOUTHEAST | 509092 | EASTON 4 | 138 | 25.3568 | 25.3829 | 0.0261
GEN-2022-038 | 04 SOUTHEAST | 509624 | LAKEPIN4 | 138 | 7.7527 | 7.759 | 0.0063
GEN-2022-038 | 04 SOUTHEAST | 588400 | GEN-2016-167 | 138 | 10.2272 | 10.2764 | 0.0492
GEN-2022-038 | 04 SOUTHEAST | 588404 | G16-167-TAP | 138 | 10.3326 | 10.3828 | 0.0502
GEN-2022-038 | 04 SOUTHEAST | 762845 | GEN-2018-050 | 345 | 16.1086 | 16.2291 | 0.1205
GEN-2022-038 | 04 SOUTHEAST | 765660 | GEN-2021-038 | 345 | 20.5978 | 20.6272 | 0.0294
GEN-2022-038 | 04 SOUTHEAST | 767740 | G22-038-TAP | 138 | 16.4561 | 17.3412 | 0.8851
GEN-2022-038 | 04 SOUTHEAST | 767741 | GEN-2022-038 | 138 | 15.3018 | 16.1918 | 0.89
GEN-2022-038 | 04 SOUTHEAST | 769201 | GEN-2022-111 | 345 | 16.0379 | 16.0749 | 0.037
GEN-2022-055 | 04 SOUTHEAST | 511409 | TREASILD7 | 345 | 16.1935 | 16.2068 | 0.0133
GEN-2022-055 | 04 SOUTHEAST | 511421 | VERDEN 4 | 138 | 10.3269 | 10.335 | 0.0081
GEN-2022-055 | 04 SOUTHEAST | 511423 | FLE TAP4 | 138 | 9.1793 | 9.183 | 0.0037
GEN-2022-055 | 04 SOUTHEAST | 511443 | BING-TP2 | 69 | 2.7894 | 2.7897 | 0.0003
GEN-2022-055 | 04 SOUTHEAST | 511445 | CARNEG-4 | 138 | 8.1877 | 8.1918 | 0.0041
GEN-2022-055 | 04 SOUTHEAST | 511449 | CORNVIL4 | 138 | 16.8897 | 16.9096 | 0.0199
GEN-2022-055 | 04 SOUTHEAST | 511463 | HOB-JCT4 | 138 | 7.1112 | 7.1127 | 0.0015
GEN-2022-055 | 04 SOUTHEAST | 511476 | S.W.S.-2 | 69 | 4.4126 | 4.4134 | 0.0008
GEN-2022-055 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 35.3389 | 35.4415 | 0.1026
GEN-2022-055 | 04 SOUTHEAST | 511483 | NORGE--4 | 138 | 11.8223 | 11.8323 | 0.01
GEN-2022-055 | 04 SOUTHEAST | 511486 | ELGINJT4 | 138 | 10.5889 | 10.5936 | 0.0047
GEN-2022-055 | 04 SOUTHEAST | 511502 | N29CHIK4 | 138 | 10.842 | 10.8504 | 0.0084
GEN-2022-055 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 10.5077 | 10.5123 | 0.0046
GEN-2022-055 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 24.1758 | 24.1967 | 0.0209
GEN-2022-055 | 04 SOUTHEAST | 515800 | GRACMNT7 | 345 | 18.8774 | 18.8989 | 0.0215
GEN-2022-055 | 04 SOUTHEAST | 515802 | GRACMNT4 | 138 | 33.8615 | 34.0089 | 0.1474
GEN-2022-055 | 04 SOUTHEAST | 520401 | BAILEY4 | 138 | 10.5712 | 10.7974 | 0.2262
GEN-2022-055 | 04 SOUTHEAST | 520404 | MDCPRK4 | 138 | 5.8775 | 5.8804 | 0.0029
GEN-2022-055 | 04 SOUTHEAST | 520412 | MUSTANG4 | 138 | 7.5082 | 7.6025 | 0.0943
GEN-2022-055 | 04 SOUTHEAST | 520422 | SEQUOYAHJ4 | 138 | 26.6135 | 26.7703 | 0.1568
GEN-2022-055 | 04 SOUTHEAST | 520440 | HARPER2 | 69 | 14.2969 | 14.3158 | 0.0189
GEN-2022-055 | 04 SOUTHEAST | 520472 | CHCKSHA4 | 138 | 8.8297 | 8.8399 | 0.0102
GEN-2022-055 | 04 SOUTHEAST | 520473 | CKSHATP4 | 138 | 11.4976 | 11.5149 | 0.0173
GEN-2022-055 | 04 SOUTHEAST | 520496 | TUTTLE 4 | 138 | 6.5455 | 7.056 | 0.5105
GEN-2022-055 | 04 SOUTHEAST | 520501 | BRIDGCR4 | 138 | 8.6828 | 9.1141 | 0.4313
GEN-2022-055 | 04 SOUTHEAST | 520508 | CLVLDSW4 | 138 | 13.2754 | 13.3069 | 0.0315
GEN-2022-055 | 04 SOUTHEAST | 520513 | BCV SW 4 | 138 | 6.107 | 6.1104 | 0.0034
GEN-2022-055 | 04 SOUTHEAST | 520530 | AMBERTP4 | 138 | 8.6397 | 8.6501 | 0.0104
GEN-2022-055 | 04 SOUTHEAST | 520531 | AMBER 4 | 138 | 7.6909 | 7.6991 | 0.0082
GEN-2022-055 | 04 SOUTHEAST | 520547 | SEQOYAH4 | 138 | 20.9519 | 21.0495 | 0.0976
GEN-2022-055 | 04 SOUTHEAST | 520552 | REDCNTP4 | 138 | 9.6319 | 9.6469 | 0.015
GEN-2022-055 | 04 SOUTHEAST | 520810 | ANADARK2 | 69 | 15.0829 | 15.104 | 0.0211
GEN-2022-055 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 37.1543 | 37.4742 | 0.3199
GEN-2022-055 | 04 SOUTHEAST | 520828 | BLANCHD4 | 138 | 13.01 | 13.0272 | 0.0172
GEN-2022-055 | 04 SOUTHEAST | 520838 | CADDO 2 | 69 | 11.8066 | 11.8188 | 0.0122
GEN-2022-055 | 04 SOUTHEAST | 520859 | COGAR 4 | 138 | 9.6002 | 9.6151 | 0.0149
GEN-2022-055 | 04 SOUTHEAST | 520867 | CORN TP4 | 138 | 14.6034 | 14.6216 | 0.0182
GEN-2022-055 | 04 SOUTHEAST | 520870 | CYRIL 2 | 69 | 6.6977 | 6.7014 | 0.0037
GEN-2022-055 | 04 SOUTHEAST | 520900 | EMPIRE 4 | 138 | 5.0275 | 5.03 | 0.0025
GEN-2022-055 | 04 SOUTHEAST | 520911 | FLETCHR2 | 69 | 8.9392 | 8.9452 | 0.006
GEN-2022-055 | 04 SOUTHEAST | 520912 | FLETCH-4 | 138 | 7.5224 | 7.5316 | 0.0092
GEN-2022-055 | 04 SOUTHEAST | 520923 | GEORGIA4 | 138 | 19.1746 | 19.2553 | 0.0807
GEN-2022-055 | 04 SOUTHEAST | 521005 | SARA RD4 | 138 | 7.5756 | 7.6851 | 0.1095
GEN-2022-055 | 04 SOUTHEAST | 521017 | ONEY 4 | 138 | 11.5672 | 11.5787 | 0.0115
GEN-2022-055 | 04 SOUTHEAST | 521024 | PARADSE4 | 138 | 6.2624 | 6.2659 | 0.0035
GEN-2022-055 | 04 SOUTHEAST | 521031 | POCASET4 | 138 | 8.4936 | 9.0614 | 0.5678
GEN-2022-055 | 04 SOUTHEAST | 521059 | SUNSHIN4 | 138 | 9.9975 | 10.3496 | 0.3521
GEN-2022-055 | 04 SOUTHEAST | 521072 | TUTLETP4 | 138 | 7.6775 | 8.3877 | 0.7102
GEN-2022-055 | 04 SOUTHEAST | 521088 | WASHITA2 | 69 | 9.5126 | 9.518 | 0.0054
GEN-2022-055 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 31.2395 | 31.331 | 0.0915
GEN-2022-055 | 04 SOUTHEAST | 521103 | SLKHILLS 4 | 138 | 7.8149 | 7.8175 | 0.0026
GEN-2022-055 | 04 SOUTHEAST | 521123 | WMOORE 4 | 138 | 12.286 | 12.4575 | 0.1715
GEN-2022-055 | 04 SOUTHEAST | 521129 | CHERRYRD 4 | 138 | 6.6355 | 6.6396 | 0.0041
GEN-2022-055 | 04 SOUTHEAST | 560078 | G16-037-TAP | 345 | 7.5926 | 7.5951 | 0.0025
GEN-2022-055 | 04 SOUTHEAST | 587790 | GEN-2016-097 | 138 | 9.4508 | 9.456 | 0.0052
GEN-2022-055 | 04 SOUTHEAST | 587794 | G16-097-TAP | 138 | 11.7063 | 11.7145 | 0.0082
GEN-2022-055 | 04 SOUTHEAST | 765890 | GEN-2021-064 | 138 | 8.1306 | 8.1347 | 0.0041
GEN-2022-055 | 04 SOUTHEAST | 768080 | G22-055-TAP | 138 | 7.6599 | 8.5799 | 0.92
GEN-2022-055 | 04 SOUTHEAST | 768081 | GEN-2022-055 | 138 | 4.8901 | 5.8797 | 0.9896
GEN-2022-071 | 04 SOUTHEAST | 505592 | WELEETK4 | 138 | 16.1964 | 16.2118 | 0.0154
GEN-2022-071 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 14.0032 | 14.005 | 0.0018
GEN-2022-071 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 21.1467 | 21.1519 | 0.0052
GEN-2022-071 | 04 SOUTHEAST | 510865 | S-MCALT4 | 138 | 6.1203 | 6.1523 | 0.032
GEN-2022-071 | 04 SOUTHEAST | 510877 | FIXCT4 | 138 | 8.4059 | 8.4073 | 0.0014
GEN-2022-071 | 04 SOUTHEAST | 510892 | HENRYET4 | 138 | 9.0196 | 9.0231 | 0.0035
GEN-2022-071 | 04 SOUTHEAST | 510896 | LONEOAK2 | 69 | 7.4031 | 7.4155 | 0.0124
GEN-2022-071 | 04 SOUTHEAST | 510897 | LONEOAK4 | 138 | 9.0973 | 9.1452 | 0.0479
GEN-2022-071 | 04 SOUTHEAST | 510899 | MCALEST2 | 69 | 5.059 | 5.068 | 0.009
GEN-2022-071 | 04 SOUTHEAST | 510902 | WELETK4 | 138 | 15.7925 | 15.8091 | 0.0166
GEN-2022-071 | 04 SOUTHEAST | 510903 | WELEETK2 | 69 | 10.6058 | 10.6091 | 0.0033
GEN-2022-071 | 04 SOUTHEAST | 510905 | WILBURT2 | 69 | 4.3364 | 4.3386 | 0.0022
GEN-2022-071 | 04 SOUTHEAST | 510906 | SMCALTP4 | 138 | 8.8803 | 8.9481 | 0.0678
GEN-2022-071 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.3301 | 15.3733 | 0.0432
GEN-2022-071 | 04 SOUTHEAST | 510908 | MCALEST4 | 138 | 10.3255 | 10.4282 | 0.1027
GEN-2022-071 | 04 SOUTHEAST | 510909 | MCALESTIND 4 | 138 | 5.9225 | 5.9735 | 0.051
GEN-2022-071 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 14.3128 | 14.3192 | 0.0064
GEN-2022-071 | 04 SOUTHEAST | 510912 | A.DEPOT2 | 69 | 3.5609 | 3.5643 | 0.0034
GEN-2022-071 | 04 SOUTHEAST | 510913 | SAVANNA2 | 69 | 3.478 | 3.4811 | 0.0031
GEN-2022-071 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.4245 | 15.4277 | 0.0032
GEN-2022-071 | 04 SOUTHEAST | 510921 | DUSTIN-4 | 138 | 9.2647 | 9.279 | 0.0143
GEN-2022-071 | 04 SOUTHEAST | 510923 | EC.HEN-4 | 138 | 9.0807 | 9.0844 | 0.0037
GEN-2022-071 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 15.0418 | 15.0833 | 0.0415
GEN-2022-071 | 04 SOUTHEAST | 510926 | SARDIS 4 | 138 | 4.9563 | 4.9639 | 0.0076
GEN-2022-071 | 04 SOUTHEAST | 510944 | ENOWILT4 | 138 | 8.9448 | 8.9909 | 0.0461
GEN-2022-071 | 04 SOUTHEAST | 510945 | ENOWILB4 | 138 | 5.077 | 5.0918 | 0.0148
GEN-2022-071 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 14.1427 | 14.5034 | 0.3607
GEN-2022-071 | 04 SOUTHEAST | 510951 | TALAWANDA 4 | 138 | 10.2242 | 10.3777 | 0.1535
GEN-2022-071 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 17.4073 | 17.4114 | 0.0041
GEN-2022-071 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.4783 | 11.4848 | 0.0065
GEN-2022-071 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.2144 | 28.2163 | 0.0019
GEN-2022-071 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.0623 | 27.0684 | 0.0061
GEN-2022-071 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 42.4654 | 42.4768 | 0.0114
GEN-2022-071 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.8715 | 29.8897 | 0.0182
GEN-2022-071 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 28.7676 | 28.7923 | 0.0247
GEN-2022-071 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 23.2566 | 23.2677 | 0.0111
GEN-2022-071 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.6068 | 10.6074 | 0.0006
GEN-2022-071 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.7052 | 11.8094 | 0.1042
GEN-2022-071 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 8.1769 | 8.1798 | 0.0029
GEN-2022-071 | 04 SOUTHEAST | 516091 | OKTAHA 7 | 345 | 17.1232 | 17.1475 | 0.0243
GEN-2022-071 | 04 SOUTHEAST | 516092 | OKTAHA 5 | 161 | 10.9373 | 10.9416 | 0.0043
GEN-2022-071 | 04 SOUTHEAST | 520420 | TENASKAWP4 | 138 | 5.9732 | 5.989 | 0.0158
GEN-2022-071 | 04 SOUTHEAST | 520844 | CARBON 4 | 138 | 7.057 | 7.0824 | 0.0254
GEN-2022-071 | 04 SOUTHEAST | 520934 | HARTSHN4 | 138 | 8.8814 | 8.9266 | 0.0452
GEN-2022-071 | 04 SOUTHEAST | 520986 | MANNING4 | 138 | 4.5085 | 4.5201 | 0.0116
GEN-2022-071 | 04 SOUTHEAST | 521047 | SAVANNA4 | 138 | 5.4506 | 5.4627 | 0.0121
GEN-2022-071 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.8789 | 11.8828 | 0.0039
GEN-2022-071 | 04 SOUTHEAST | 588810 | GEN-2017-040 | 345 | 18.5997 | 18.6373 | 0.0376
GEN-2022-071 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 19.0241 | 19.0634 | 0.0393
GEN-2022-071 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 19.0241 | 19.0634 | 0.0393
GEN-2022-071 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 15.4951 | 15.521 | 0.0259
GEN-2022-071 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 3.9291 | 3.9297 | 0.0006
GEN-2022-071 | 04 SOUTHEAST | 762592 | GEN-2018-024 | 345 | 18.4431 | 18.4802 | 0.0371
GEN-2022-071 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 9.9014 | 9.9188 | 0.0174
GEN-2022-071 | 04 SOUTHEAST | 764520 | G20-020-TAP | 345 | 10.5593 | 10.5606 | 0.0013
GEN-2022-071 | 04 SOUTHEAST | 765451 | G21-016-TAP | 345 | 11.7594 | 11.7632 | 0.0038
GEN-2022-071 | 04 SOUTHEAST | 768400 | G22-071-TAP | 138 | 12.5359 | 12.9475 | 0.4116
GEN-2022-071 | 04 SOUTHEAST | 768401 | GEN-2022-071 | 138 | 11.7158 | 12.1281 | 0.4123
GEN-2022-098 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 22.1384 | 22.1506 | 0.0122
GEN-2022-098 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 9.6493 | 9.6546 | 0.0053
GEN-2022-098 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 27.0799 | 27.0997 | 0.0198
GEN-2022-098 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 14.5275 | 14.5454 | 0.0179
GEN-2022-098 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.9823 | 14.005 | 0.0227
GEN-2022-098 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 22.1384 | 22.1506 | 0.0122
GEN-2022-098 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 20.1548 | 20.1598 | 0.005
GEN-2022-098 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 16.4277 | 16.4302 | 0.0025
GEN-2022-098 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 9.9584 | 9.9726 | 0.0142
GEN-2022-098 | 04 SOUTHEAST | 510870 | WCITYTP2 | 69 | 6.724 | 6.7272 | 0.0032
GEN-2022-098 | 04 SOUTHEAST | 510876 | KIPUMPT2 | 69 | 5.1157 | 5.1175 | 0.0018
GEN-2022-098 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 7.1308 | 7.1356 | 0.0048
GEN-2022-098 | 04 SOUTHEAST | 510888 | B.BOWTP4 | 138 | 7.5246 | 7.5285 | 0.0039
GEN-2022-098 | 04 SOUTHEAST | 510893 | HUGO---2 | 69 | 5.3143 | 5.3162 | 0.0019
GEN-2022-098 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.6601 | 3.6619 | 0.0018
GEN-2022-098 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.336 | 15.3733 | 0.0373
GEN-2022-098 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.7339 | 7.738 | 0.0041
GEN-2022-098 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 14.2355 | 14.3192 | 0.0837
GEN-2022-098 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.3936 | 15.4277 | 0.0341
GEN-2022-098 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 15.0475 | 15.0833 | 0.0358
GEN-2022-098 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 14.4985 | 14.5034 | 0.0049
GEN-2022-098 | 04 SOUTHEAST | 511456 | O.K.U.-7 | 345 | 4.9 | 4.9016 | 0.0016
GEN-2022-098 | 04 SOUTHEAST | 511467 | L.E.S.-4 | 138 | 27.1316 | 27.148 | 0.0164
GEN-2022-098 | 04 SOUTHEAST | 511468 | L.E.S.-7 | 345 | 15.1052 | 15.1282 | 0.023
GEN-2022-098 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.6298 | 10.6714 | 0.0416
GEN-2022-098 | 04 SOUTHEAST | 511571 | RUSHSPR7 | 345 | 6.4479 | 6.4622 | 0.0143
GEN-2022-098 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 17.3663 | 17.4114 | 0.0451
GEN-2022-098 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.4121 | 11.4848 | 0.0727
GEN-2022-098 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.2145 | 28.2163 | 0.0018
GEN-2022-098 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.0608 | 27.0684 | 0.0076
GEN-2022-098 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 42.4608 | 42.4768 | 0.016
GEN-2022-098 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.8739 | 29.8897 | 0.0158
GEN-2022-098 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 13.0983 | 13.1211 | 0.0228
GEN-2022-098 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 12.2718 | 12.2901 | 0.0183
GEN-2022-098 | 04 SOUTHEAST | 515128 | RATLIFF2 | 69 | 5.4672 | 5.4692 | 0.002
GEN-2022-098 | 04 SOUTHEAST | 515129 | RATLIFF4 | 138 | 7.3246 | 7.3312 | 0.0066
GEN-2022-098 | 04 SOUTHEAST | 515130 | POOLVIL4 | 138 | 9.6516 | 9.6651 | 0.0135
GEN-2022-098 | 04 SOUTHEAST | 515131 | FOX 4 | 138 | 7.6618 | 7.6713 | 0.0095
GEN-2022-098 | 04 SOUTHEAST | 515134 | PRARPNT4 | 138 | 5.9262 | 5.9294 | 0.0032
GEN-2022-098 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 20.7171 | 20.8458 | 0.1287
GEN-2022-098 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.8784 | 12.0506 | 0.1722
GEN-2022-098 | 04 SOUTHEAST | 515137 | UNIROY 4 | 138 | 13.7437 | 13.7878 | 0.0441
GEN-2022-098 | 04 SOUTHEAST | 515138 | CARTER 4 | 138 | 13.6402 | 13.675 | 0.0348
GEN-2022-098 | 04 SOUTHEAST | 515143 | WOLFCRK4 | 138 | 10.4592 | 10.4885 | 0.0293
GEN-2022-098 | 04 SOUTHEAST | 515144 | LONEGRV4 | 138 | 14.6209 | 14.6823 | 0.0614
GEN-2022-098 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 11.1804 | 11.1943 | 0.0139
GEN-2022-098 | 04 SOUTHEAST | 515160 | MRIETA 2 | 138 | 8.0933 | 8.1027 | 0.0094
GEN-2022-098 | 04 SOUTHEAST | 515162 | FNDTION4 | 138 | 12.9006 | 12.9302 | 0.0296
GEN-2022-098 | 04 SOUTHEAST | 515163 | ROCKYPT2 | 69 | 8.3427 | 8.3493 | 0.0066
GEN-2022-098 | 04 SOUTHEAST | 515164 | ROCKYPT4 | 138 | 12.8863 | 12.9202 | 0.0339
GEN-2022-098 | 04 SOUTHEAST | 515172 | SPRNDAL4 | 138 | 12.8914 | 12.9212 | 0.0298
GEN-2022-098 | 04 SOUTHEAST | 515372 | ARDWEST4 | 138 | 13.5491 | 13.5909 | 0.0418
GEN-2022-098 | 04 SOUTHEAST | 515415 | CHEEKTP4 | 138 | 13.1629 | 13.2118 | 0.0489
GEN-2022-098 | 04 SOUTHEAST | 515420 | SCMMRCT2 | 69 | 9.6349 | 9.6434 | 0.0085
GEN-2022-098 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.7999 | 11.8094 | 0.0095
GEN-2022-098 | 04 SOUTHEAST | 515561 | CARTRCO4 | 138 | 9.9103 | 9.9244 | 0.0141
GEN-2022-098 | 04 SOUTHEAST | 515563 | ORIGINW4 | 138 | 6.4818 | 6.4848 | 0.003
GEN-2022-098 | 04 SOUTHEAST | 515873 | DRPSPRG4 | 138 | 11.9307 | 11.9557 | 0.025
GEN-2022-098 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 8.1466 | 8.1798 | 0.0332
GEN-2022-098 | 04 SOUTHEAST | 520411 | SAWYER4 | 138 | 11.0081 | 11.0245 | 0.0164
GEN-2022-098 | 04 SOUTHEAST | 520419 | GARVIN4 | 138 | 6.2518 | 6.2554 | 0.0036
GEN-2022-098 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 23.2589 | 23.3454 | 0.0865
GEN-2022-098 | 04 SOUTHEAST | 520918 | FROGVIL4 | 138 | 11.1849 | 11.2025 | 0.0176
GEN-2022-098 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 23.5814 | 23.6637 | 0.0823
GEN-2022-098 | 04 SOUTHEAST | 520988 | MARIETA4 | 138 | 8.0279 | 8.0365 | 0.0086
GEN-2022-098 | 04 SOUTHEAST | 521036 | RATTAN 4 | 138 | 7.1571 | 7.1632 | 0.0061
GEN-2022-098 | 04 SOUTHEAST | 521079 | VALLANT4 | 138 | 8.9953 | 9.0053 | 0.01
GEN-2022-098 | 04 SOUTHEAST | 521098 | WSBNKTP4 | 138 | 6.959 | 6.9653 | 0.0063
GEN-2022-098 | 04 SOUTHEAST | 521125 | CHEEK_4 | 138 | 9.1029 | 9.1265 | 0.0236
GEN-2022-098 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.7728 | 11.8828 | 0.11
GEN-2022-098 | 04 SOUTHEAST | 560088 | G17-075-TAP | 345 | 7.4714 | 7.8347 | 0.3633
GEN-2022-098 | 04 SOUTHEAST | 588670 | GEN-2017-023 | 138 | 19.4599 | 19.5162 | 0.0563
GEN-2022-098 | 04 SOUTHEAST | 588710 | GEN-2017-027 | 138 | 9.8526 | 9.8666 | 0.014
GEN-2022-098 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 19.0587 | 19.0634 | 0.0047
GEN-2022-098 | 04 SOUTHEAST | 589130 | GEN-2017-075 | 345 | 7.462 | 7.8243 | 0.3623
GEN-2022-098 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 3.9224 | 3.9297 | 0.0073
GEN-2022-098 | 04 SOUTHEAST | 760938 | G17-171-TAP | 345 | 11.9649 | 11.9953 | 0.0304
GEN-2022-098 | 04 SOUTHEAST | 760939 | GEN-2017-171 | 345 | 11.8964 | 11.9264 | 0.03
GEN-2022-098 | 04 SOUTHEAST | 762900 | GEN-2018-055 | 345 | 6.1593 | 6.1722 | 0.0129
GEN-2022-098 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 9.9037 | 9.9188 | 0.0151
GEN-2022-098 | 04 SOUTHEAST | 763318 | GEN-2018-115 | 345 | 14.8135 | 14.8356 | 0.0221
GEN-2022-098 | 04 SOUTHEAST | 764075 | GEN-2020-054 | 345 | 12.5363 | 12.5543 | 0.018
GEN-2022-098 | 04 SOUTHEAST | 764510 | GEN-2020-020 | 345 | 10.5304 | 10.5464 | 0.016
GEN-2022-098 | 04 SOUTHEAST | 764520 | G20-020-TAP | 345 | 10.5446 | 10.5606 | 0.016
GEN-2022-098 | 04 SOUTHEAST | 764550 | G20-087-TAP | 345 | 14.975 | 14.9923 | 0.0173
GEN-2022-098 | 04 SOUTHEAST | 765450 | GEN-2021-016 | 345 | 11.2509 | 11.3987 | 0.1478
GEN-2022-098 | 04 SOUTHEAST | 765451 | G21-016-TAP | 345 | 11.606 | 11.7632 | 0.1572
GEN-2022-098 | 04 SOUTHEAST | 765660 | GEN-2021-038 | 345 | 20.6166 | 20.6272 | 0.0106
GEN-2022-098 | 04 SOUTHEAST | 768941 | GEN-2022-098 | 345 | 6.9338 | 7.2984 | 0.3646
GEN-2022-104 | 04 SOUTHEAST | 505595 | GREASYC4 | 138 | 7.419 | 7.4212 | 0.0022
GEN-2022-104 | 04 SOUTHEAST | 505596 | EXPLOR 4 | 138 | 5.7281 | 5.7308 | 0.0027
GEN-2022-104 | 04 SOUTHEAST | 505598 | ALLEN 4 | 138 | 5.6621 | 5.6675 | 0.0054
GEN-2022-104 | 04 SOUTHEAST | 505600 | TUPELO 4 | 138 | 10.8793 | 10.9175 | 0.0382
GEN-2022-104 | 04 SOUTHEAST | 505602 | S BROWN4 | 138 | 10.5956 | 11.0867 | 0.4911
GEN-2022-104 | 04 SOUTHEAST | 505604 | DENISON4 | 138 | 3.4845 | 3.5361 | 0.0516
GEN-2022-104 | 04 SOUTHEAST | 505650 | GERTY 4 | 138 | 4.1935 | 4.1964 | 0.0029
GEN-2022-104 | 04 SOUTHEAST | 505665 | CENTRATAP4 | 138 | 10.6546 | 10.6912 | 0.0366
GEN-2022-104 | 04 SOUTHEAST | 505666 | CENTRAHOMA4 | 138 | 5.4316 | 5.441 | 0.0094
GEN-2022-104 | 04 SOUTHEAST | 505671 | UNION VLY4 | 138 | 5.5537 | 5.5636 | 0.0099
GEN-2022-104 | 04 SOUTHEAST | 505672 | AHLOSO4 | 138 | 4.9649 | 4.9727 | 0.0078
GEN-2022-104 | 04 SOUTHEAST | 505674 | MONTE VISTA4 | 138 | 3.855 | 3.8597 | 0.0047
GEN-2022-104 | 04 SOUTHEAST | 510862 | COALGAT4 | 138 | 6.1344 | 6.1447 | 0.0103
GEN-2022-104 | 04 SOUTHEAST | 510863 | ALLENNG4 | 138 | 5.7704 | 5.781 | 0.0106
GEN-2022-104 | 04 SOUTHEAST | 510880 | COALGTP4 | 138 | 6.3652 | 6.3763 | 0.0111
GEN-2022-104 | 04 SOUTHEAST | 510881 | ALLENGT4 | 138 | 10.5445 | 10.5802 | 0.0357
GEN-2022-104 | 04 SOUTHEAST | 510884 | HOLDEXP4 | 138 | 5.5935 | 5.5961 | 0.0026
GEN-2022-104 | 04 SOUTHEAST | 510887 | ATOKA--4 | 138 | 6.1905 | 6.1991 | 0.0086
GEN-2022-104 | 04 SOUTHEAST | 510895 | LEHIGH-4 | 138 | 5.9958 | 6.005 | 0.0092
GEN-2022-104 | 04 SOUTHEAST | 510916 | ALLEN--4 | 138 | 5.6545 | 5.6599 | 0.0054
GEN-2022-104 | 04 SOUTHEAST | 510935 | EXPCOLT4 | 138 | 7.7458 | 7.765 | 0.0192
GEN-2022-104 | 04 SOUTHEAST | 510936 | EXPCOLG4 | 138 | 7.6425 | 7.6612 | 0.0187
GEN-2022-104 | 04 SOUTHEAST | 510949 | WAPANUCKA 4 | 138 | 8.0404 | 8.0593 | 0.0189
GEN-2022-104 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 17.3026 | 17.4114 | 0.1088
GEN-2022-104 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.4557 | 11.4848 | 0.0291
GEN-2022-104 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 12.9584 | 13.1211 | 0.1627
GEN-2022-104 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 12.2495 | 12.2901 | 0.0406
GEN-2022-104 | 04 SOUTHEAST | 515147 | GLASSES4 | 138 | 9.6697 | 9.7718 | 0.1021
GEN-2022-104 | 04 SOUTHEAST | 515149 | MADINDT4 | 138 | 9.677 | 9.7796 | 0.1026
GEN-2022-104 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 11.0513 | 11.1943 | 0.143
GEN-2022-104 | 04 SOUTHEAST | 515151 | LTLCITY4 | 138 | 8.7623 | 8.9905 | 0.2282
GEN-2022-104 | 04 SOUTHEAST | 515152 | BROWNTP4 | 138 | 10.199 | 10.6507 | 0.4517
GEN-2022-104 | 04 SOUTHEAST | 515153 | COLEMNT4 | 138 | 7.2817 | 7.5087 | 0.227
GEN-2022-104 | 04 SOUTHEAST | 515154 | EXPLRPL4 | 138 | 5.0387 | 5.146 | 0.1073
GEN-2022-104 | 04 SOUTHEAST | 515155 | BODLE 4 | 138 | 7.7693 | 8.0176 | 0.2483
GEN-2022-104 | 04 SOUTHEAST | 515157 | BROWN 4 | 138 | 10.5751 | 11.0619 | 0.4868
GEN-2022-104 | 04 SOUTHEAST | 515159 | COLBRTP4 | 138 | 7.8819 | 8.1367 | 0.2548
GEN-2022-104 | 04 SOUTHEAST | 515176 | BUTRFLD4 | 138 | 7.3993 | 7.6191 | 0.2198
GEN-2022-104 | 04 SOUTHEAST | 515191 | LULA 2 | 69 | 6.1576 | 6.1608 | 0.0032
GEN-2022-104 | 04 SOUTHEAST | 515192 | LULA 4 | 138 | 9.5311 | 9.5539 | 0.0228
GEN-2022-104 | 04 SOUTHEAST | 515193 | COLBRT-4 | 138 | 6.3428 | 6.4907 | 0.1479
GEN-2022-104 | 04 SOUTHEAST | 515408 | REBAR 4 | 138 | 6.9639 | 7.1596 | 0.1957
GEN-2022-104 | 04 SOUTHEAST | 515568 | KEYSTNT4 | 138 | 4.0332 | 4.0695 | 0.0363
GEN-2022-104 | 04 SOUTHEAST | 515699 | EFITSTP4 | 138 | 8.3105 | 8.3222 | 0.0117
GEN-2022-104 | 04 SOUTHEAST | 515873 | DRPSPRG4 | 138 | 11.908 | 11.9557 | 0.0477
GEN-2022-104 | 04 SOUTHEAST | 515932 | STIRLNG4 | 138 | 10.8053 | 10.8538 | 0.0485
GEN-2022-104 | 04 SOUTHEAST | 515944 | STRRDTP4 | 138 | 10.4795 | 10.9571 | 0.4776
GEN-2022-104 | 04 SOUTHEAST | 520406 | TUPELO 4 | 138 | 9.9845 | 10.0157 | 0.0312
GEN-2022-104 | 04 SOUTHEAST | 520426 | SEAWAY4 | 138 | 5.1208 | 5.2157 | 0.0949
GEN-2022-104 | 04 SOUTHEAST | 520427 | TXI4 | 138 | 3.7766 | 3.8275 | 0.0509
GEN-2022-104 | 04 SOUTHEAST | 520448 | BOGYDPT4 | 138 | 5.372 | 5.3792 | 0.0072
GEN-2022-104 | 04 SOUTHEAST | 520463 | SCOLEMN4 | 138 | 4.9582 | 5.0845 | 0.1263
GEN-2022-104 | 04 SOUTHEAST | 520465 | REAGAN 4 | 138 | 4.5468 | 4.5672 | 0.0204
GEN-2022-104 | 04 SOUTHEAST | 520483 | DURANT 4 | 138 | 5.0821 | 5.1826 | 0.1005
GEN-2022-104 | 04 SOUTHEAST | 520527 | BOGGYDP4 | 138 | 3.9085 | 3.9123 | 0.0038
GEN-2022-104 | 04 SOUTHEAST | 520551 | SALTTP 4 | 138 | 5.4807 | 5.4869 | 0.0062
GEN-2022-104 | 04 SOUTHEAST | 520826 | BENNGTN4 | 138 | 5.0073 | 5.0633 | 0.056
GEN-2022-104 | 04 SOUTHEAST | 520860 | COLBERT4 | 138 | 6.3772 | 6.5254 | 0.1482
GEN-2022-104 | 04 SOUTHEAST | 520862 | COLGATE4 | 138 | 6.2856 | 6.2951 | 0.0095
GEN-2022-104 | 04 SOUTHEAST | 520884 | DURANTP4 | 138 | 6.121 | 6.2661 | 0.1451
GEN-2022-104 | 04 SOUTHEAST | 520963 | KIERSEY4 | 138 | 6.8421 | 7.0291 | 0.187
GEN-2022-104 | 04 SOUTHEAST | 520969 | LASALLE4 | 138 | 6.9438 | 6.9555 | 0.0117
GEN-2022-104 | 04 SOUTHEAST | 521044 | RUSSETT4 | 138 | 12.8768 | 13.039 | 0.1622
GEN-2022-104 | 04 SOUTHEAST | 521049 | SCLMNJC4 | 138 | 8.5105 | 8.8902 | 0.3797
GEN-2022-104 | 04 SOUTHEAST | 521067 | TEXOMAJ4 | 138 | 10.9172 | 11.0559 | 0.1387
GEN-2022-104 | 04 SOUTHEAST | 521071 | STNWLSW4 | 138 | 10.6507 | 10.6848 | 0.0341
GEN-2022-104 | 04 SOUTHEAST | 521074 | BOGGY4 | 138 | 9.0325 | 9.0573 | 0.0248
GEN-2022-104 | 04 SOUTHEAST | 521075 | STNWLTP4 | 138 | 9.2527 | 9.2771 | 0.0244
GEN-2022-104 | 04 SOUTHEAST | 521077 | UNGER 4 | 138 | 5.2608 | 5.2933 | 0.0325
GEN-2022-104 | 04 SOUTHEAST | 521098 | WSBNKTP4 | 138 | 6.9422 | 6.9653 | 0.0231
GEN-2022-104 | 04 SOUTHEAST | 521115 | BENNSUB4 | 138 | 4.7127 | 4.7623 | 0.0496
GEN-2022-104 | 04 SOUTHEAST | 587200 | GEN-2016-030 | 138 | 7.2046 | 7.4259 | 0.2213
GEN-2022-104 | 04 SOUTHEAST | 765300 | GEN-2021-001 | 138 | 10.4003 | 10.8698 | 0.4695
GEN-2022-104 | 04 SOUTHEAST | 769060 | G22-104-TAP | 138 | 9.5779 | 10.0947 | 0.5168
GEN-2022-104 | 04 SOUTHEAST | 769061 | GEN-2022-104 | 138 | 9.5624 | 10.0792 | 0.5168
GEN-2022-104 | 04 SOUTHEAST | 769701 | GEN-2022-136 | 138 | 6.2387 | 6.3789 | 0.1402
GEN-2022-104 | 04 SOUTHEAST | 769841 | GEN-2022-143 | 138 | 10.9835 | 11.1244 | 0.1409
GEN-2022-111 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 21.9686 | 22.1506 | 0.182
GEN-2022-111 | 04 SOUTHEAST | 5918 | DCEAST | 345 | 4.511 | 4.511 | 0
GEN-2022-111 | 04 SOUTHEAST | 5919 | WELSHDC1 | 345 | 21.9686 | 22.1506 | 0.182
GEN-2022-111 | 04 SOUTHEAST | 5921 | SPP-CAP1 | 345 | 21.9686 | 22.1506 | 0.182
GEN-2022-111 | 04 SOUTHEAST | 5922 | SPP-CAP2 | 345 | 21.9686 | 22.1506 | 0.182
GEN-2022-111 | 04 SOUTHEAST | 5923 | SPP-CAP3 | 345 | 21.9686 | 22.1506 | 0.182
GEN-2022-111 | 04 SOUTHEAST | 5924 | SPP-REAC1 | 345 | 21.9686 | 22.1506 | 0.182
GEN-2022-111 | 04 SOUTHEAST | 5925 | ERCOTMAINBUS | 345 | 4.511 | 4.511 | 0
GEN-2022-111 | 04 SOUTHEAST | 48723 | J1872 SUB | 500 | 23.2873 | 23.2902 | 0.0029
GEN-2022-111 | 04 SOUTHEAST | 48733 | J1873 SUB | 500 | 23.2873 | 23.2902 | 0.0029
GEN-2022-111 | 04 SOUTHEAST | 303302 | 3MINDEN_LG | 115 | 5.7525 | 5.7531 | 0.0006
GEN-2022-111 | 04 SOUTHEAST | 337360 | 3ADA_LA | 115 | 5.6654 | 5.666 | 0.0006
GEN-2022-111 | 04 SOUTHEAST | 337361 | 3MINDEN_LA! | 115 | 7.0131 | 7.0141 | 0.001
GEN-2022-111 | 04 SOUTHEAST | 337362 | 3LA_ORD_PLNT | 115 | 4.5669 | 4.5673 | 0.0004
GEN-2022-111 | 04 SOUTHEAST | 337363 | 3SAREPTA! | 115 | 20.3584 | 20.3788 | 0.0204
GEN-2022-111 | 04 SOUTHEAST | 337364 | 3CULLEN | 115 | 8.663 | 8.6668 | 0.0038
GEN-2022-111 | 04 SOUTHEAST | 337365 | 3SPRINGHILL | 115 | 10.0019 | 10.0059 | 0.004
GEN-2022-111 | 04 SOUTHEAST | 337366 | 3HAYNESVILLE | 115 | 6.0652 | 6.0661 | 0.0009
GEN-2022-111 | 04 SOUTHEAST | 337368 | 8MT_OLIVE% | 500 | 12.1188 | 12.1198 | 0.001
GEN-2022-111 | 04 SOUTHEAST | 337376 | 7SAREPTA% | 345 | 10.1633 | 10.1821 | 0.0188
GEN-2022-111 | 04 SOUTHEAST | 337420 | 8STERLING% | 500 | 20.0728 | 20.0733 | 0.0005
GEN-2022-111 | 04 SOUTHEAST | 337500 | 3TAYLOR | 115 | 7.3099 | 7.3115 | 0.0016
GEN-2022-111 | 04 SOUTHEAST | 337515 | 8MCNEIL% | 500 | 14.5249 | 14.526 | 0.0011
GEN-2022-111 | 04 SOUTHEAST | 337526 | 3EMERSON! | 115 | 6.0139 | 6.0145 | 0.0006
GEN-2022-111 | 04 SOUTHEAST | 337539 | 3EL DORADO! | 115 | 29.3498 | 29.3508 | 0.001
GEN-2022-111 | 04 SOUTHEAST | 337561 | 8EL DORADO% | 500 | 27.8035 | 27.8077 | 0.0042
GEN-2022-111 | 04 SOUTHEAST | 337562 | 7EL DORADO | 345 | 14.2154 | 14.2205 | 0.0051
GEN-2022-111 | 04 SOUTHEAST | 337643 | 8SHERIDAN% | 500 | 28.0168 | 28.0174 | 0.0006
GEN-2022-111 | 04 SOUTHEAST | 338440 | 8PANDA% | 500 | 27.7366 | 27.7408 | 0.0042
GEN-2022-111 | 04 SOUTHEAST | 500140 | CARROLL6 | 230 | 13.8758 | 13.8802 | 0.0044
GEN-2022-111 | 04 SOUTHEAST | 500250 | DOLHILL7 | 345 | 12.7006 | 12.7126 | 0.012
GEN-2022-111 | 04 SOUTHEAST | 500255 | REDBAYOU_6 | 230 | 10.783 | 10.7868 | 0.0038
GEN-2022-111 | 04 SOUTHEAST | 500260 | DOLHILL6 | 230 | 15.5012 | 15.5097 | 0.0085
GEN-2022-111 | 04 SOUTHEAST | 504029 | SFOREMAN 4 | 138 | 9.1456 | 9.1498 | 0.0042
GEN-2022-111 | 04 SOUTHEAST | 504123 | LOCKSBRG 4 | 138 | 6.1833 | 6.1846 | 0.0013
GEN-2022-111 | 04 SOUTHEAST | 507402 | ASHDWNR4 | 138 | 10.6591 | 10.663 | 0.0039
GEN-2022-111 | 04 SOUTHEAST | 507428 | OKAY 4 | 138 | 10.44 | 10.4431 | 0.0031
GEN-2022-111 | 04 SOUTHEAST | 507429 | PATTERS2 | 69 | 14.4013 | 14.4053 | 0.004
GEN-2022-111 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.8551 | 13.8622 | 0.0071
GEN-2022-111 | 04 SOUTHEAST | 507434 | SNASHVL4 | 138 | 3.9147 | 3.915 | 0.0003
GEN-2022-111 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 25.5897 | 25.6057 | 0.016
GEN-2022-111 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 9.6457 | 9.6546 | 0.0089
GEN-2022-111 | 04 SOUTHEAST | 507456 | TURK 3 | 115 | 19.9266 | 19.9335 | 0.0069
GEN-2022-111 | 04 SOUTHEAST | 507710 | ARSHILL2 | 69 | 28.8218 | 28.8469 | 0.0251
GEN-2022-111 | 04 SOUTHEAST | 507711 | ARSHILL4 | 138 | 26.3255 | 26.3645 | 0.039
GEN-2022-111 | 04 SOUTHEAST | 507726 | FLOURNY2 | 69 | 14.3905 | 14.3989 | 0.0084
GEN-2022-111 | 04 SOUTHEAST | 507727 | FLOURNY4 | 138 | 17.5035 | 17.5307 | 0.0272
GEN-2022-111 | 04 SOUTHEAST | 507731 | FTHUMBG4 | 138 | 20.3385 | 20.3631 | 0.0246
GEN-2022-111 | 04 SOUTHEAST | 507732 | GENMOTR4 | 138 | 18.7576 | 18.7887 | 0.0311
GEN-2022-111 | 04 SOUTHEAST | 507735 | HARTSIS4 | 138 | 17.1218 | 17.1405 | 0.0187
GEN-2022-111 | 04 SOUTHEAST | 507738 | LINWOOD4 | 138 | 23.5961 | 23.6337 | 0.0376
GEN-2022-111 | 04 SOUTHEAST | 507742 | MCWILLI4 | 138 | 22.306 | 22.3373 | 0.0313
GEN-2022-111 | 04 SOUTHEAST | 507748 | POWELL 4 | 138 | 20.4712 | 20.5013 | 0.0301
GEN-2022-111 | 04 SOUTHEAST | 507749 | RAINES 4 | 138 | 17.1111 | 17.1326 | 0.0215
GEN-2022-111 | 04 SOUTHEAST | 507754 | S SHV 2 | 69 | 18.6877 | 18.6996 | 0.0119
GEN-2022-111 | 04 SOUTHEAST | 507755 | S SHV 4 | 138 | 24.4447 | 24.4859 | 0.0412
GEN-2022-111 | 04 SOUTHEAST | 507757 | SPRIDGE4 | 138 | 11.8124 | 11.8223 | 0.0099
GEN-2022-111 | 04 SOUTHEAST | 507759 | SW SHV 4 | 138 | 32.8582 | 32.9515 | 0.0933
GEN-2022-111 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.5026 | 16.5784 | 0.0758
GEN-2022-111 | 04 SOUTHEAST | 507765 | WALLAKE4 | 138 | 11.2751 | 11.2825 | 0.0074
GEN-2022-111 | 04 SOUTHEAST | 507767 | WESTELC4 | 138 | 21.6509 | 21.6867 | 0.0358
GEN-2022-111 | 04 SOUTHEAST | 507771 | CEDARGR4 | 138 | 23.4678 | 23.505 | 0.0372
GEN-2022-111 | 04 SOUTHEAST | 507774 | NORAM 4 | 138 | 17.9823 | 18.0115 | 0.0292
GEN-2022-111 | 04 SOUTHEAST | 507788 | MINDEN-3 | 115 | 5.6721 | 5.6727 | 0.0006
GEN-2022-111 | 04 SOUTHEAST | 507789 | STLGENS4 | 138 | 25.906 | 25.9424 | 0.0364
GEN-2022-111 | 04 SOUTHEAST | 507793 | LEASIDE 4 | 138 | 23.5434 | 23.5869 | 0.0435
GEN-2022-111 | 04 SOUTHEAST | 507794 | LEASIDE 2 | 69 | 13.4781 | 13.4851 | 0.007
GEN-2022-111 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 20.9113 | 20.9349 | 0.0236
GEN-2022-111 | 04 SOUTHEAST | 508050 | ANDRSNC4 | 138 | 8.2425 | 8.2484 | 0.0059
GEN-2022-111 | 04 SOUTHEAST | 508052 | ATLANTA2 | 69 | 5.5606 | 5.5622 | 0.0016
GEN-2022-111 | 04 SOUTHEAST | 508054 | BANN 4 | 138 | 21.9162 | 21.9423 | 0.0261
GEN-2022-111 | 04 SOUTHEAST | 508055 | BLOOMBG2 | 69 | 5.8061 | 5.8074 | 0.0013
GEN-2022-111 | 04 SOUTHEAST | 508056 | BRYANML4 | 138 | 7.5711 | 7.578 | 0.0069
GEN-2022-111 | 04 SOUTHEAST | 508059 | IPC T 4 | 138 | 8.5247 | 8.5305 | 0.0058
GEN-2022-111 | 04 SOUTHEAST | 508060 | IPC-DOM4 | 138 | 9.0401 | 9.0463 | 0.0062
GEN-2022-111 | 04 SOUTHEAST | 508062 | LINDEN 2 | 69 | 5.8929 | 5.8952 | 0.0023
GEN-2022-111 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.6735 | 7.681 | 0.0075
GEN-2022-111 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 25.9839 | 26.02 | 0.0361
GEN-2022-111 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 27.0607 | 27.0997 | 0.039
GEN-2022-111 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 14.5161 | 14.5454 | 0.0293
GEN-2022-111 | 04 SOUTHEAST | 508079 | SUGARHL2 | 69 | 17.2739 | 17.2814 | 0.0075
GEN-2022-111 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.7739 | 12.7808 | 0.0069
GEN-2022-111 | 04 SOUTHEAST | 508089 | WATLANT2 | 69 | 8.0823 | 8.0863 | 0.004
GEN-2022-111 | 04 SOUTHEAST | 508090 | WATLANT4 | 138 | 7.8541 | 7.8614 | 0.0073
GEN-2022-111 | 04 SOUTHEAST | 508091 | ALUMAX 4 | 138 | 18.4298 | 18.4481 | 0.0183
GEN-2022-111 | 04 SOUTHEAST | 508095 | IPC 4 | 138 | 5.9759 | 5.9788 | 0.0029
GEN-2022-111 | 04 SOUTHEAST | 508104 | RIFFIN REC4 | 138 | 11.6364 | 11.645 | 0.0086
GEN-2022-111 | 04 SOUTHEAST | 508105 | MANDEVILTP4 | 138 | 9.8207 | 9.8241 | 0.0034
GEN-2022-111 | 04 SOUTHEAST | 508106 | CASSTP4 | 138 | 7.832 | 7.8391 | 0.0071
GEN-2022-111 | 04 SOUTHEAST | 508286 | CAMPCOR4 | 138 | 8.6017 | 8.6123 | 0.0106
GEN-2022-111 | 04 SOUTHEAST | 508291 | HUGHES 2 | 69 | 7.3036 | 7.3077 | 0.0041
GEN-2022-111 | 04 SOUTHEAST | 508294 | LSTARTP2 | 69 | 7.875 | 7.88 | 0.005
GEN-2022-111 | 04 SOUTHEAST | 508295 | LSREC 2 | 69 | 7.664 | 7.6686 | 0.0046
GEN-2022-111 | 04 SOUTHEAST | 508296 | LSSOUTH2 | 69 | 9.8135 | 9.8212 | 0.0077
GEN-2022-111 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 18.2101 | 18.2629 | 0.0528
GEN-2022-111 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.9713 | 14.005 | 0.0337
GEN-2022-111 | 04 SOUTHEAST | 508309 | PETTY 2 | 69 | 11.0192 | 11.0284 | 0.0092
GEN-2022-111 | 04 SOUTHEAST | 508310 | PETTY 4 | 138 | 8.4113 | 8.4218 | 0.0105
GEN-2022-111 | 04 SOUTHEAST | 508312 | PITTSB_2 | 69 | 8.709 | 8.714 | 0.005
GEN-2022-111 | 04 SOUTHEAST | 508313 | PITTSB_4 | 138 | 9.4052 | 9.4174 | 0.0122
GEN-2022-111 | 04 SOUTHEAST | 508317 | WINNSBO4 | 138 | 5.7947 | 5.7985 | 0.0038
GEN-2022-111 | 04 SOUTHEAST | 508319 | PITTSTP2 | 69 | 6.841 | 6.844 | 0.003
GEN-2022-111 | 04 SOUTHEAST | 508320 | LONSTAR2 | 69 | 8.2426 | 8.248 | 0.0054
GEN-2022-111 | 04 SOUTHEAST | 508337 | CHAPELH4 | 138 | 7.8763 | 7.8863 | 0.01
GEN-2022-111 | 04 SOUTHEAST | 508339 | FERNDTP2 | 69 | 5.9489 | 5.9512 | 0.0023
GEN-2022-111 | 04 SOUTHEAST | 508350 | PERDUE 2 | 69 | 13.5833 | 13.5897 | 0.0064
GEN-2022-111 | 04 SOUTHEAST | 508351 | PERDUE 4 | 138 | 11.0662 | 11.0747 | 0.0085
GEN-2022-111 | 04 SOUTHEAST | 508355 | WELSHRE4 | 138 | 7.8495 | 7.86 | 0.0105
GEN-2022-111 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 21.9686 | 22.1506 | 0.182
GEN-2022-111 | 04 SOUTHEAST | 508368 | SCROGNSSW4 | 138 | 6.1011 | 6.1056 | 0.0045
GEN-2022-111 | 04 SOUTHEAST | 508369 | EXXONM 4 | 138 | 6.961 | 6.9646 | 0.0036
GEN-2022-111 | 04 SOUTHEAST | 508552 | LLAMOND4 | 138 | 7.3576 | 7.3616 | 0.004
GEN-2022-111 | 04 SOUTHEAST | 508556 | MARSHAL2 | 69 | 18.065 | 18.0741 | 0.0091
GEN-2022-111 | 04 SOUTHEAST | 508557 | MARSHL-4 | 138 | 17.4608 | 17.478 | 0.0172
GEN-2022-111 | 04 SOUTHEAST | 508560 | NEWGLAD4 | 138 | 9.9142 | 9.9198 | 0.0056
GEN-2022-111 | 04 SOUTHEAST | 508562 | PIRKEY 4 | 138 | 43.7123 | 43.7802 | 0.0679
GEN-2022-111 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 18.4882 | 18.5242 | 0.036
GEN-2022-111 | 04 SOUTHEAST | 508564 | PLILER 4 | 138 | 12.0012 | 12.0098 | 0.0086
GEN-2022-111 | 04 SOUTHEAST | 508566 | SABMINT4 | 138 | 35.6101 | 35.6569 | 0.0468
GEN-2022-111 | 04 SOUTHEAST | 508567 | SCOTTSV4 | 138 | 12.8416 | 12.8523 | 0.0107
GEN-2022-111 | 04 SOUTHEAST | 508569 | SEMRSHL4 | 138 | 14.151 | 14.1617 | 0.0107
GEN-2022-111 | 04 SOUTHEAST | 508571 | SPRHILL4 | 138 | 8.6844 | 8.6907 | 0.0063
GEN-2022-111 | 04 SOUTHEAST | 508572 | LEBROCK7 | 345 | 17.1218 | 17.1503 | 0.0285
GEN-2022-111 | 04 SOUTHEAST | 508576 | MARAUTO2 | 69 | 18.2197 | 18.229 | 0.0093
GEN-2022-111 | 04 SOUTHEAST | 508585 | TENRUSK7 | 345 | 8.15 | 8.1548 | 0.0048
GEN-2022-111 | 04 SOUTHEAST | 508595 | HALLSVLS4 | 138 | 19.4936 | 19.5071 | 0.0135
GEN-2022-111 | 04 SOUTHEAST | 508801 | BLANCH-2 | 69 | 7.0831 | 7.0848 | 0.0017
GEN-2022-111 | 04 SOUTHEAST | 508805 | LIEBERM2 | 69 | 9.4065 | 9.4098 | 0.0033
GEN-2022-111 | 04 SOUTHEAST | 508806 | LIEBERM4 | 138 | 17.6466 | 17.675 | 0.0284
GEN-2022-111 | 04 SOUTHEAST | 508808 | LONGWD 4 | 138 | 26.1416 | 26.2132 | 0.0716
GEN-2022-111 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 16.4578 | 16.5842 | 0.1264
GEN-2022-111 | 04 SOUTHEAST | 508811 | NBENTON4 | 138 | 9.6706 | 9.6778 | 0.0072
GEN-2022-111 | 04 SOUTHEAST | 508812 | OILCITY2 | 69 | 7.5539 | 7.5559 | 0.002
GEN-2022-111 | 04 SOUTHEAST | 508816 | OAKPH 4 | 138 | 20.3963 | 20.4388 | 0.0425
GEN-2022-111 | 04 SOUTHEAST | 508827 | NGPL 4 | 138 | 9.7702 | 9.7773 | 0.0071
GEN-2022-111 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.9169 | 30.0091 | 0.0922
GEN-2022-111 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 20.0567 | 20.1598 | 0.1031
GEN-2022-111 | 04 SOUTHEAST | 508833 | IPCJEFF4 | 138 | 12.7457 | 12.7679 | 0.0222
GEN-2022-111 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 14.0752 | 14.1027 | 0.0275
GEN-2022-111 | 04 SOUTHEAST | 508837 | NGPLTAP4 | 138 | 12.6367 | 12.6486 | 0.0119
GEN-2022-111 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 31.543 | 31.7808 | 0.2378
GEN-2022-111 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 15.8874 | 16.4302 | 0.5428
GEN-2022-111 | 04 SOUTHEAST | 509052 | STONWAL4 | 138 | 10.8657 | 10.8738 | 0.0081
GEN-2022-111 | 04 SOUTHEAST | 509092 | EASTON 4 | 138 | 25.3648 | 25.3829 | 0.0181
GEN-2022-111 | 04 SOUTHEAST | 509103 | WLNTSPRINGS4 | 138 | 9.4334 | 9.4376 | 0.0042
GEN-2022-111 | 04 SOUTHEAST | 509603 | BIGSAND4 | 138 | 7.4852 | 7.4891 | 0.0039
GEN-2022-111 | 04 SOUTHEAST | 509607 | DIAN 4 | 138 | 12.0167 | 12.0315 | 0.0148
GEN-2022-111 | 04 SOUTHEAST | 509616 | HARLETT2 | 69 | 3.6746 | 3.6755 | 0.0009
GEN-2022-111 | 04 SOUTHEAST | 509618 | CAMPCTY2 | 69 | 5.1007 | 5.1025 | 0.0018
GEN-2022-111 | 04 SOUTHEAST | 509621 | JEFERSN2 | 69 | 2.2827 | 2.2831 | 0.0004
GEN-2022-111 | 04 SOUTHEAST | 509623 | LAKEPIN2 | 69 | 7.6861 | 7.6901 | 0.004
GEN-2022-111 | 04 SOUTHEAST | 509624 | LAKEPIN4 | 138 | 7.7507 | 7.759 | 0.0083
GEN-2022-111 | 04 SOUTHEAST | 509627 | NESBIT 2 | 69 | 3.3847 | 3.3855 | 0.0008
GEN-2022-111 | 04 SOUTHEAST | 509628 | NOONDAY4 | 138 | 6.075 | 6.0788 | 0.0038
GEN-2022-111 | 04 SOUTHEAST | 509635 | VICTORY2 | 69 | 2.7365 | 2.737 | 0.0005
GEN-2022-111 | 04 SOUTHEAST | 509639 | DIANASW4 | 138 | 12.5063 | 12.5223 | 0.016
GEN-2022-111 | 04 SOUTHEAST | 509643 | LIBERTH4 | 138 | 4.7001 | 4.7036 | 0.0035
GEN-2022-111 | 04 SOUTHEAST | 509644 | OMAHA 2 | 69 | 3.1002 | 3.1011 | 0.0009
GEN-2022-111 | 04 SOUTHEAST | 509645 | DUGLASV2 | 69 | 6.6122 | 6.615 | 0.0028
GEN-2022-111 | 04 SOUTHEAST | 509646 | BLALOCK2 | 69 | 3.9753 | 3.9763 | 0.001
GEN-2022-111 | 04 SOUTHEAST | 509651 | PEARLHL2 | 69 | 5.7169 | 5.719 | 0.0021
GEN-2022-111 | 04 SOUTHEAST | 509652 | NLINDEN2 | 69 | 5.1248 | 5.1264 | 0.0016
GEN-2022-111 | 04 SOUTHEAST | 509653 | MAUDT 2 | 69 | 3.1892 | 3.1896 | 0.0004
GEN-2022-111 | 04 SOUTHEAST | 509658 | ANDRCKT2 | 69 | 8.7417 | 8.7451 | 0.0034
GEN-2022-111 | 04 SOUTHEAST | 509664 | CHAPLHL4 | 138 | 7.6207 | 7.63 | 0.0093
GEN-2022-111 | 04 SOUTHEAST | 509666 | DUGLASV4 | 138 | 5.3316 | 5.3352 | 0.0036
GEN-2022-111 | 04 SOUTHEAST | 509668 | ROACH 2 | 69 | 6.2033 | 6.2057 | 0.0024
GEN-2022-111 | 04 SOUTHEAST | 509689 | KEYP37 4 | 138 | 4.2391 | 4.2412 | 0.0021
GEN-2022-111 | 04 SOUTHEAST | 510866 | V-WEYCO4 | 138 | 9.9707 | 9.9726 | 0.0019
GEN-2022-111 | 04 SOUTHEAST | 510886 | IDABEL-4 | 138 | 7.1347 | 7.1356 | 0.0009
GEN-2022-111 | 04 SOUTHEAST | 510901 | HUGO---4 | 138 | 3.6617 | 3.6619 | 0.0002
GEN-2022-111 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.3717 | 15.3733 | 0.0016
GEN-2022-111 | 04 SOUTHEAST | 510910 | VALIANT2 | 69 | 7.7375 | 7.738 | 0.0005
GEN-2022-111 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 14.3066 | 14.3192 | 0.0126
GEN-2022-111 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.4232 | 15.4277 | 0.0045
GEN-2022-111 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 15.0818 | 15.0833 | 0.0015
GEN-2022-111 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.4843 | 11.4848 | 0.0005
GEN-2022-111 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.8893 | 29.8897 | 0.0004
GEN-2022-111 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.8089 | 11.8094 | 0.0005
GEN-2022-111 | 04 SOUTHEAST | 520560 | HUGOITC4 | 138 | 23.3396 | 23.3454 | 0.0058
GEN-2022-111 | 04 SOUTHEAST | 520948 | HUGO PP4 | 138 | 23.6581 | 23.6637 | 0.0056
GEN-2022-111 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.8767 | 11.8828 | 0.0061
GEN-2022-111 | 04 SOUTHEAST | 560088 | G17-075-TAP | 345 | 7.8338 | 7.8347 | 0.0009
GEN-2022-111 | 04 SOUTHEAST | 588400 | GEN-2016-167 | 138 | 10.2678 | 10.2764 | 0.0086
GEN-2022-111 | 04 SOUTHEAST | 588404 | G16-167-TAP | 138 | 10.374 | 10.3828 | 0.0088
GEN-2022-111 | 04 SOUTHEAST | 762431 | G18-003-TAP | 138 | 12.8964 | 12.9062 | 0.0098
GEN-2022-111 | 04 SOUTHEAST | 762845 | GEN-2018-050 | 345 | 16.1081 | 16.2291 | 0.121
GEN-2022-111 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 9.9181 | 9.9188 | 0.0007
GEN-2022-111 | 04 SOUTHEAST | 764075 | GEN-2020-054 | 345 | 12.5275 | 12.5543 | 0.0268
GEN-2022-111 | 04 SOUTHEAST | 764510 | GEN-2020-020 | 345 | 10.5343 | 10.5464 | 0.0121
GEN-2022-111 | 04 SOUTHEAST | 764520 | G20-020-TAP | 345 | 10.5485 | 10.5606 | 0.0121
GEN-2022-111 | 04 SOUTHEAST | 765641 | G21-036-TAP | 138 | 11.3326 | 11.3371 | 0.0045
GEN-2022-111 | 04 SOUTHEAST | 765660 | GEN-2021-038 | 345 | 20.4693 | 20.6272 | 0.1579
GEN-2022-111 | 04 SOUTHEAST | 767740 | G22-038-TAP | 138 | 17.3149 | 17.3412 | 0.0263
GEN-2022-111 | 04 SOUTHEAST | 767741 | GEN-2022-038 | 138 | 16.1691 | 16.1918 | 0.0227
GEN-2022-111 | 04 SOUTHEAST | 769201 | GEN-2022-111 | 345 | 15.5319 | 16.0749 | 0.543
GEN-2022-111 | 04 SOUTHEAST | 769761 | GEN-2022-139 | 345 | 17.6862 | 17.7191 | 0.0329
GEN-2022-130 | 04 SOUTHEAST | 337811 | 8HAPPYVALY% | 500 | 25.7463 | 25.7695 | 0.0232
GEN-2022-130 | 04 SOUTHEAST | 337909 | 8ANO% | 500 | 18.2514 | 18.3093 | 0.0579
GEN-2022-130 | 04 SOUTHEAST | 337912 | 5ANO% | 161 | 17.9031 | 17.9209 | 0.0178
GEN-2022-130 | 04 SOUTHEAST | 337922 | 8P.HILL% | 500 | 15.8994 | 15.9241 | 0.0247
GEN-2022-130 | 04 SOUTHEAST | 504182 | BEVERLY5 | 161 | 20.3833 | 20.9128 | 0.5295
GEN-2022-130 | 04 SOUTHEAST | 504187 | CHAFFEEXING5 | 161 | 11.257 | 11.5638 | 0.3068
GEN-2022-130 | 04 SOUTHEAST | 504189 | CHAFXING-TP5 | 161 | 13.2705 | 13.6983 | 0.4278
GEN-2022-130 | 04 SOUTHEAST | 504190 | RYEHILL5 | 161 | 12.4719 | 12.8493 | 0.3774
GEN-2022-130 | 04 SOUTHEAST | 507182 | BONANZA5 | 161 | 16.0604 | 16.3231 | 0.2627
GEN-2022-130 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 28.767 | 28.7923 | 0.0253
GEN-2022-130 | 04 SOUTHEAST | 515261 | BONANZT5 | 161 | 16.1997 | 16.4673 | 0.2676
GEN-2022-130 | 04 SOUTHEAST | 515262 | AES 5 | 161 | 12.3633 | 12.4296 | 0.0663
GEN-2022-130 | 04 SOUTHEAST | 515285 | 28JCT 2 | 69 | 10.4911 | 10.5381 | 0.047
GEN-2022-130 | 04 SOUTHEAST | 515287 | CARNALL2 | 69 | 10.1432 | 10.1888 | 0.0456
GEN-2022-130 | 04 SOUTHEAST | 515288 | PARKVU 2 | 69 | 11.9774 | 12.044 | 0.0666
GEN-2022-130 | 04 SOUTHEAST | 515290 | BELLAVE2 | 69 | 13.9794 | 14.0663 | 0.0869
GEN-2022-130 | 04 SOUTHEAST | 515293 | JONSON 5 | 161 | 15.8002 | 16.1019 | 0.3017
GEN-2022-130 | 04 SOUTHEAST | 515299 | BEVYTAP5 | 161 | 21.2007 | 21.7738 | 0.5731
GEN-2022-130 | 04 SOUTHEAST | 515300 | FTSMTHE5 | 161 | 23.9877 | 24.7683 | 0.7806
GEN-2022-130 | 04 SOUTHEAST | 515301 | FTSMTHW5 | 161 | 23.8517 | 24.6083 | 0.7566
GEN-2022-130 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.4699 | 10.6074 | 0.1375
GEN-2022-130 | 04 SOUTHEAST | 515305 | FTSMITH8 | 500 | 8.7374 | 8.8906 | 0.1532
GEN-2022-130 | 04 SOUTHEAST | 515306 | ARKOMA 5 | 161 | 16.7683 | 17.1108 | 0.3425
GEN-2022-130 | 04 SOUTHEAST | 515308 | 3RDST 5 | 161 | 16.145 | 16.4492 | 0.3042
GEN-2022-130 | 04 SOUTHEAST | 515310 | QUANXTP5 | 161 | 18.4167 | 18.8864 | 0.4697
GEN-2022-130 | 04 SOUTHEAST | 515311 | BARLING5 | 161 | 16.93 | 17.3442 | 0.4142
GEN-2022-130 | 04 SOUTHEAST | 515315 | OAKPARK5 | 161 | 17.2358 | 17.5643 | 0.3285
GEN-2022-130 | 04 SOUTHEAST | 515326 | GERBRTP5 | 161 | 17.1662 | 17.4883 | 0.3221
GEN-2022-130 | 04 SOUTHEAST | 515339 | VBI 5 | 161 | 19.3048 | 19.614 | 0.3092
GEN-2022-130 | 04 SOUTHEAST | 515340 | OAKGROV5 | 161 | 16.146 | 16.4223 | 0.2763
GEN-2022-130 | 04 SOUTHEAST | 515341 | WHITESD5 | 161 | 16.0239 | 16.3045 | 0.2806
GEN-2022-130 | 04 SOUTHEAST | 515342 | MASSARD2 | 69 | 13.4527 | 13.5434 | 0.0907
GEN-2022-130 | 04 SOUTHEAST | 515343 | MASSARD5 | 161 | 18.5619 | 19.0813 | 0.5194
GEN-2022-130 | 04 SOUTHEAST | 515345 | COLONY 5 | 161 | 19.0687 | 19.8783 | 0.8096
GEN-2022-130 | 04 SOUTHEAST | 515349 | BATTLEF5 | 161 | 17.7495 | 18.6282 | 0.8787
GEN-2022-130 | 04 SOUTHEAST | 515356 | JSTREET5 | 161 | 16.0548 | 16.3538 | 0.299
GEN-2022-130 | 04 SOUTHEAST | 515474 | QUANEXS5 | 161 | 17.4711 | 17.8925 | 0.4214
GEN-2022-130 | 04 SOUTHEAST | 515523 | RYHLLTP5 | 161 | 16.8209 | 17.5125 | 0.6916
GEN-2022-130 | 04 SOUTHEAST | 515874 | MCSTL2 5 | 161 | 14.306 | 14.8042 | 0.4982
GEN-2022-130 | 04 SOUTHEAST | 515876 | MCSTLTP5 | 161 | 15.2494 | 15.8164 | 0.567
GEN-2022-130 | 04 SOUTHEAST | 769581 | GEN-2022-130 | 161 | 17.69 | 18.5689 | 0.8789
GEN-2022-136 | 04 SOUTHEAST | 505596 | EXPLOR 4 | 138 | 5.7261 | 5.7308 | 0.0047
GEN-2022-136 | 04 SOUTHEAST | 505598 | ALLEN 4 | 138 | 5.6582 | 5.6675 | 0.0093
GEN-2022-136 | 04 SOUTHEAST | 505600 | TUPELO 4 | 138 | 10.8517 | 10.9175 | 0.0658
GEN-2022-136 | 04 SOUTHEAST | 505602 | S BROWN4 | 138 | 10.2549 | 11.0867 | 0.8318
GEN-2022-136 | 04 SOUTHEAST | 505604 | DENISON4 | 138 | 3.4469 | 3.5361 | 0.0892
GEN-2022-136 | 04 SOUTHEAST | 505650 | GERTY 4 | 138 | 4.1914 | 4.1964 | 0.005
GEN-2022-136 | 04 SOUTHEAST | 505665 | CENTRATAP4 | 138 | 10.6282 | 10.6912 | 0.063
GEN-2022-136 | 04 SOUTHEAST | 505666 | CENTRAHOMA4 | 138 | 5.4249 | 5.441 | 0.0161
GEN-2022-136 | 04 SOUTHEAST | 505671 | UNION VLY4 | 138 | 5.5467 | 5.5636 | 0.0169
GEN-2022-136 | 04 SOUTHEAST | 510880 | COALGTP4 | 138 | 6.3574 | 6.3763 | 0.0189
GEN-2022-136 | 04 SOUTHEAST | 510881 | ALLENGT4 | 138 | 10.5187 | 10.5802 | 0.0615
GEN-2022-136 | 04 SOUTHEAST | 510916 | ALLEN--4 | 138 | 5.6507 | 5.6599 | 0.0092
GEN-2022-136 | 04 SOUTHEAST | 510935 | EXPCOLT4 | 138 | 7.7319 | 7.765 | 0.0331
GEN-2022-136 | 04 SOUTHEAST | 510949 | WAPANUCKA 4 | 138 | 8.0269 | 8.0593 | 0.0324
GEN-2022-136 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 17.2232 | 17.4114 | 0.1882
GEN-2022-136 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 12.8402 | 13.1211 | 0.2809
GEN-2022-136 | 04 SOUTHEAST | 515147 | GLASSES4 | 138 | 9.5943 | 9.7718 | 0.1775
GEN-2022-136 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 10.9462 | 11.1943 | 0.2481
GEN-2022-136 | 04 SOUTHEAST | 515151 | LTLCITY4 | 138 | 8.5967 | 8.9905 | 0.3938
GEN-2022-136 | 04 SOUTHEAST | 515152 | BROWNTP4 | 138 | 9.866 | 10.6507 | 0.7847
GEN-2022-136 | 04 SOUTHEAST | 515153 | COLEMNT4 | 138 | 7.1162 | 7.5087 | 0.3925
GEN-2022-136 | 04 SOUTHEAST | 515155 | BODLE 4 | 138 | 7.4007 | 8.0176 | 0.6169
GEN-2022-136 | 04 SOUTHEAST | 515157 | BROWN 4 | 138 | 10.2318 | 11.0619 | 0.8301
GEN-2022-136 | 04 SOUTHEAST | 515159 | COLBRTP4 | 138 | 7.486 | 8.1367 | 0.6507
GEN-2022-136 | 04 SOUTHEAST | 515176 | BUTRFLD4 | 138 | 6.9655 | 7.6191 | 0.6536
GEN-2022-136 | 04 SOUTHEAST | 515192 | LULA 4 | 138 | 9.5147 | 9.5539 | 0.0392
GEN-2022-136 | 04 SOUTHEAST | 515193 | COLBRT-4 | 138 | 5.6326 | 6.4907 | 0.8581
GEN-2022-136 | 04 SOUTHEAST | 515408 | REBAR 4 | 138 | 6.6239 | 7.1596 | 0.5357
GEN-2022-136 | 04 SOUTHEAST | 515932 | STIRLNG4 | 138 | 10.7694 | 10.8538 | 0.0844
GEN-2022-136 | 04 SOUTHEAST | 515944 | STRRDTP4 | 138 | 10.1389 | 10.9571 | 0.8182
GEN-2022-136 | 04 SOUTHEAST | 520406 | TUPELO 4 | 138 | 9.962 | 10.0157 | 0.0537
GEN-2022-136 | 04 SOUTHEAST | 520426 | SEAWAY4 | 138 | 4.6203 | 5.2157 | 0.5954
GEN-2022-136 | 04 SOUTHEAST | 520427 | TXI4 | 138 | 3.5009 | 3.8275 | 0.3266
GEN-2022-136 | 04 SOUTHEAST | 520428 | YUBA4 | 138 | 2.9699 | 3.1999 | 0.23
GEN-2022-136 | 04 SOUTHEAST | 520448 | BOGYDPT4 | 138 | 5.367 | 5.3792 | 0.0122
GEN-2022-136 | 04 SOUTHEAST | 520463 | SCOLEMN4 | 138 | 4.9232 | 5.0845 | 0.1613
GEN-2022-136 | 04 SOUTHEAST | 520465 | REAGAN 4 | 138 | 4.5317 | 4.5672 | 0.0355
GEN-2022-136 | 04 SOUTHEAST | 520860 | COLBERT4 | 138 | 5.6157 | 6.5254 | 0.9097
GEN-2022-136 | 04 SOUTHEAST | 520862 | COLGATE4 | 138 | 6.2788 | 6.2951 | 0.0163
GEN-2022-136 | 04 SOUTHEAST | 520884 | DURANTP4 | 138 | 6.0816 | 6.2661 | 0.1845
GEN-2022-136 | 04 SOUTHEAST | 520963 | KIERSEY4 | 138 | 6.3937 | 7.0291 | 0.6354
GEN-2022-136 | 04 SOUTHEAST | 521044 | RUSSETT4 | 138 | 12.7589 | 13.039 | 0.2801
GEN-2022-136 | 04 SOUTHEAST | 521049 | SCLMNJC4 | 138 | 8.4075 | 8.8902 | 0.4827
GEN-2022-136 | 04 SOUTHEAST | 521071 | STNWLSW4 | 138 | 10.6262 | 10.6848 | 0.0586
GEN-2022-136 | 04 SOUTHEAST | 521074 | BOGGY4 | 138 | 9.0148 | 9.0573 | 0.0425
GEN-2022-136 | 04 SOUTHEAST | 521075 | STNWLTP4 | 138 | 9.2352 | 9.2771 | 0.0419
GEN-2022-136 | 04 SOUTHEAST | 587200 | GEN-2016-030 | 138 | 7.0453 | 7.4259 | 0.3806
GEN-2022-136 | 04 SOUTHEAST | 765300 | GEN-2021-001 | 138 | 10.0689 | 10.8698 | 0.8009
GEN-2022-136 | 04 SOUTHEAST | 769060 | G22-104-TAP | 138 | 9.438 | 10.0947 | 0.6567
GEN-2022-136 | 04 SOUTHEAST | 769061 | GEN-2022-104 | 138 | 9.4246 | 10.0792 | 0.6546
GEN-2022-136 | 04 SOUTHEAST | 769701 | GEN-2022-136 | 138 | 5.4633 | 6.3789 | 0.9156
GEN-2022-139 | 04 SOUTHEAST | 5917 | SPPMAINBUS | 345 | 22.0489 | 22.1506 | 0.1017
GEN-2022-139 | 04 SOUTHEAST | 5918 | DCEAST | 345 | 4.511 | 4.511 | 0
GEN-2022-139 | 04 SOUTHEAST | 5919 | WELSHDC1 | 345 | 22.0489 | 22.1506 | 0.1017
GEN-2022-139 | 04 SOUTHEAST | 5921 | SPP-CAP1 | 345 | 22.0489 | 22.1506 | 0.1017
GEN-2022-139 | 04 SOUTHEAST | 5922 | SPP-CAP2 | 345 | 22.0489 | 22.1506 | 0.1017
GEN-2022-139 | 04 SOUTHEAST | 5923 | SPP-CAP3 | 345 | 22.0489 | 22.1506 | 0.1017
GEN-2022-139 | 04 SOUTHEAST | 5924 | SPP-REAC1 | 345 | 22.0489 | 22.1506 | 0.1017
GEN-2022-139 | 04 SOUTHEAST | 334026 | 4GRIMES% | 138 | 15.971 | 15.979 | 0.008
GEN-2022-139 | 04 SOUTHEAST | 334027 | 6GRIMES! | 230 | 7.3236 | 7.3261 | 0.0025
GEN-2022-139 | 04 SOUTHEAST | 334028 | 7GRIMES% | 345 | 8.5613 | 8.5685 | 0.0072
GEN-2022-139 | 04 SOUTHEAST | 334029 | 7FRONTR | 345 | 8.3477 | 8.3543 | 0.0066
GEN-2022-139 | 04 SOUTHEAST | 334197 | 7ROCKYCRK% | 345 | 7.0234 | 7.0276 | 0.0042
GEN-2022-139 | 04 SOUTHEAST | 337363 | 3SAREPTA! | 115 | 20.3743 | 20.3788 | 0.0045
GEN-2022-139 | 04 SOUTHEAST | 337376 | 7SAREPTA% | 345 | 10.178 | 10.1821 | 0.0041
GEN-2022-139 | 04 SOUTHEAST | 337562 | 7EL DORADO | 345 | 14.2194 | 14.2205 | 0.0011
GEN-2022-139 | 04 SOUTHEAST | 500140 | CARROLL6 | 230 | 13.8783 | 13.8802 | 0.0019
GEN-2022-139 | 04 SOUTHEAST | 500250 | DOLHILL7 | 345 | 12.7076 | 12.7126 | 0.005
GEN-2022-139 | 04 SOUTHEAST | 500255 | REDBAYOU_6 | 230 | 10.7852 | 10.7868 | 0.0016
GEN-2022-139 | 04 SOUTHEAST | 500260 | DOLHILL6 | 230 | 15.5061 | 15.5097 | 0.0036
GEN-2022-139 | 04 SOUTHEAST | 507431 | PATTERS4 | 138 | 13.8591 | 13.8622 | 0.0031
GEN-2022-139 | 04 SOUTHEAST | 507454 | TURK 4 | 138 | 25.5981 | 25.6057 | 0.0076
GEN-2022-139 | 04 SOUTHEAST | 507455 | TURK 7 | 345 | 9.6502 | 9.6546 | 0.0044
GEN-2022-139 | 04 SOUTHEAST | 507727 | FLOURNY4 | 138 | 17.5168 | 17.5307 | 0.0139
GEN-2022-139 | 04 SOUTHEAST | 507732 | GENMOTR4 | 138 | 18.7729 | 18.7887 | 0.0158
GEN-2022-139 | 04 SOUTHEAST | 507735 | HARTSIS4 | 138 | 17.1308 | 17.1405 | 0.0097
GEN-2022-139 | 04 SOUTHEAST | 507738 | LINWOOD4 | 138 | 23.6145 | 23.6337 | 0.0192
GEN-2022-139 | 04 SOUTHEAST | 507748 | POWELL 4 | 138 | 20.4861 | 20.5013 | 0.0152
GEN-2022-139 | 04 SOUTHEAST | 507754 | S SHV 2 | 69 | 18.6934 | 18.6996 | 0.0062
GEN-2022-139 | 04 SOUTHEAST | 507755 | S SHV 4 | 138 | 24.4648 | 24.4859 | 0.0211
GEN-2022-139 | 04 SOUTHEAST | 507757 | SPRIDGE4 | 138 | 11.8151 | 11.8223 | 0.0072
GEN-2022-139 | 04 SOUTHEAST | 507759 | SW SHV 4 | 138 | 32.9056 | 32.9515 | 0.0459
GEN-2022-139 | 04 SOUTHEAST | 507760 | SW SHV 7 | 345 | 16.5468 | 16.5784 | 0.0316
GEN-2022-139 | 04 SOUTHEAST | 507765 | WALLAKE4 | 138 | 11.2787 | 11.2825 | 0.0038
GEN-2022-139 | 04 SOUTHEAST | 507767 | WESTELC4 | 138 | 21.6682 | 21.6867 | 0.0185
GEN-2022-139 | 04 SOUTHEAST | 507771 | CEDARGR4 | 138 | 23.486 | 23.505 | 0.019
GEN-2022-139 | 04 SOUTHEAST | 507774 | NORAM 4 | 138 | 17.9964 | 18.0115 | 0.0151
GEN-2022-139 | 04 SOUTHEAST | 507793 | LEASIDE 4 | 138 | 23.5643 | 23.5869 | 0.0226
GEN-2022-139 | 04 SOUTHEAST | 507794 | LEASIDE 2 | 69 | 13.4813 | 13.4851 | 0.0038
GEN-2022-139 | 04 SOUTHEAST | 508049 | NASH 4 | 138 | 20.9243 | 20.9349 | 0.0106
GEN-2022-139 | 04 SOUTHEAST | 508064 | MUNZCTY4 | 138 | 7.679 | 7.681 | 0.002
GEN-2022-139 | 04 SOUTHEAST | 508070 | NWT-BNT4 | 138 | 26.0035 | 26.02 | 0.0165
GEN-2022-139 | 04 SOUTHEAST | 508071 | NWTXARK4 | 138 | 27.0817 | 27.0997 | 0.018
GEN-2022-139 | 04 SOUTHEAST | 508072 | NWTXARK7 | 345 | 14.5307 | 14.5454 | 0.0147
GEN-2022-139 | 04 SOUTHEAST | 508080 | SUGARHL4 | 138 | 12.7776 | 12.7808 | 0.0032
GEN-2022-139 | 04 SOUTHEAST | 508090 | WATLANT4 | 138 | 7.8592 | 7.8614 | 0.0022
GEN-2022-139 | 04 SOUTHEAST | 508286 | CAMPCOR4 | 138 | 8.6067 | 8.6123 | 0.0056
GEN-2022-139 | 04 SOUTHEAST | 508295 | LSREC 2 | 69 | 7.6662 | 7.6686 | 0.0024
GEN-2022-139 | 04 SOUTHEAST | 508296 | LSSOUTH2 | 69 | 9.8171 | 9.8212 | 0.0041
GEN-2022-139 | 04 SOUTHEAST | 508297 | LSSOUTH4 | 138 | 18.2329 | 18.2629 | 0.03
GEN-2022-139 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 13.987 | 14.005 | 0.018
GEN-2022-139 | 04 SOUTHEAST | 508312 | PITTSB_2 | 69 | 8.7105 | 8.714 | 0.0035
GEN-2022-139 | 04 SOUTHEAST | 508313 | PITTSB_4 | 138 | 9.4103 | 9.4174 | 0.0071
GEN-2022-139 | 04 SOUTHEAST | 508320 | LONSTAR2 | 69 | 8.2451 | 8.248 | 0.0029
GEN-2022-139 | 04 SOUTHEAST | 508335 | BIGSNDY2 | 69 | 7.024 | 7.0274 | 0.0034
GEN-2022-139 | 04 SOUTHEAST | 508341 | GILMER 2 | 69 | 5.2324 | 5.2341 | 0.0017
GEN-2022-139 | 04 SOUTHEAST | 508350 | PERDUE 2 | 69 | 13.5768 | 13.5897 | 0.0129
GEN-2022-139 | 04 SOUTHEAST | 508351 | PERDUE 4 | 138 | 11.0577 | 11.0747 | 0.017
GEN-2022-139 | 04 SOUTHEAST | 508355 | WELSHRE4 | 138 | 7.8561 | 7.86 | 0.0039
GEN-2022-139 | 04 SOUTHEAST | 508358 | LHAWKIN4 | 138 | 5.9898 | 5.994 | 0.0042
GEN-2022-139 | 04 SOUTHEAST | 508359 | WELSH 7 | 345 | 22.0489 | 22.1506 | 0.1017
GEN-2022-139 | 04 SOUTHEAST | 508368 | SCROGNSSW4 | 138 | 6.1023 | 6.1056 | 0.0033
GEN-2022-139 | 04 SOUTHEAST | 508369 | EXXONM 4 | 138 | 6.9585 | 6.9646 | 0.0061
GEN-2022-139 | 04 SOUTHEAST | 508540 | CLARKSV2 | 69 | 12.4199 | 12.4311 | 0.0112
GEN-2022-139 | 04 SOUTHEAST | 508543 | HALLSVL2 | 69 | 8.6438 | 8.6505 | 0.0067
GEN-2022-139 | 04 SOUTHEAST | 508544 | HARRISN4 | 138 | 14.7331 | 14.762 | 0.0289
GEN-2022-139 | 04 SOUTHEAST | 508547 | KNOXLEE2 | 69 | 13.8494 | 13.8643 | 0.0149
GEN-2022-139 | 04 SOUTHEAST | 508548 | KNOXLEE4 | 138 | 26.6578 | 26.7525 | 0.0947
GEN-2022-139 | 04 SOUTHEAST | 508549 | LETOURT2 | 69 | 19.898 | 19.931 | 0.033
GEN-2022-139 | 04 SOUTHEAST | 508550 | LIBCYTP4 | 138 | 10.0261 | 10.0398 | 0.0137
GEN-2022-139 | 04 SOUTHEAST | 508551 | LLAMOND2 | 69 | 18.2532 | 18.2804 | 0.0272
GEN-2022-139 | 04 SOUTHEAST | 508552 | LLAMOND4 | 138 | 7.3528 | 7.3616 | 0.0088
GEN-2022-139 | 04 SOUTHEAST | 508553 | LONGVHT2 | 69 | 13.162 | 13.1769 | 0.0149
GEN-2022-139 | 04 SOUTHEAST | 508554 | LONGVHT4 | 138 | 15.4981 | 15.5383 | 0.0402
GEN-2022-139 | 04 SOUTHEAST | 508555 | LONGVUE2 | 69 | 16.6567 | 16.6798 | 0.0231
GEN-2022-139 | 04 SOUTHEAST | 508556 | MARSHAL2 | 69 | 18.0408 | 18.0741 | 0.0333
GEN-2022-139 | 04 SOUTHEAST | 508557 | MARSHL-4 | 138 | 17.4045 | 17.478 | 0.0735
GEN-2022-139 | 04 SOUTHEAST | 508558 | MONROCR2 | 69 | 7.1847 | 7.1889 | 0.0042
GEN-2022-139 | 04 SOUTHEAST | 508560 | NEWGLAD4 | 138 | 9.9064 | 9.9198 | 0.0134
GEN-2022-139 | 04 SOUTHEAST | 508561 | NTXEAST4 | 138 | 22.191 | 22.2525 | 0.0615
GEN-2022-139 | 04 SOUTHEAST | 508562 | PIRKEY 4 | 138 | 43.1076 | 43.7802 | 0.6726
GEN-2022-139 | 04 SOUTHEAST | 508563 | PIRKEY 7 | 345 | 17.9022 | 18.5242 | 0.622
GEN-2022-139 | 04 SOUTHEAST | 508564 | PLILER 4 | 138 | 11.9854 | 12.0098 | 0.0244
GEN-2022-139 | 04 SOUTHEAST | 508566 | SABMINT4 | 138 | 35.2229 | 35.6569 | 0.434
GEN-2022-139 | 04 SOUTHEAST | 508567 | SCOTTSV4 | 138 | 12.8255 | 12.8523 | 0.0268
GEN-2022-139 | 04 SOUTHEAST | 508569 | SEMRSHL4 | 138 | 14.1173 | 14.1617 | 0.0444
GEN-2022-139 | 04 SOUTHEAST | 508570 | SOTXEST4 | 138 | 22.9011 | 22.9704 | 0.0693
GEN-2022-139 | 04 SOUTHEAST | 508571 | SPRHILL4 | 138 | 8.6782 | 8.6907 | 0.0125
GEN-2022-139 | 04 SOUTHEAST | 508572 | LEBROCK7 | 345 | 16.6582 | 17.1503 | 0.4921
GEN-2022-139 | 04 SOUTHEAST | 508574 | WHITNEY2 | 69 | 22.5092 | 22.5518 | 0.0426
GEN-2022-139 | 04 SOUTHEAST | 508575 | WHITNEY4 | 138 | 22.5712 | 22.6554 | 0.0842
GEN-2022-139 | 04 SOUTHEAST | 508576 | MARAUTO2 | 69 | 18.1949 | 18.229 | 0.0341
GEN-2022-139 | 04 SOUTHEAST | 508577 | SABINEM4 | 138 | 23.2322 | 23.4213 | 0.1891
GEN-2022-139 | 04 SOUTHEAST | 508582 | EASTEX 4 | 138 | 23.8699 | 23.9451 | 0.0752
GEN-2022-139 | 04 SOUTHEAST | 508585 | TENRUSK7 | 345 | 8.0711 | 8.1548 | 0.0837
GEN-2022-139 | 04 SOUTHEAST | 508586 | TENGEN 7 | 345 | 7.9973 | 8.0795 | 0.0822
GEN-2022-139 | 04 SOUTHEAST | 508595 | HALLSVLS4 | 138 | 19.4275 | 19.5071 | 0.0796
GEN-2022-139 | 04 SOUTHEAST | 508596 | BRANDYBR | 138 | 25.5643 | 25.6557 | 0.0914
GEN-2022-139 | 04 SOUTHEAST | 508806 | LIEBERM4 | 138 | 17.6594 | 17.675 | 0.0156
GEN-2022-139 | 04 SOUTHEAST | 508808 | LONGWD 4 | 138 | 26.1761 | 26.2132 | 0.0371
GEN-2022-139 | 04 SOUTHEAST | 508809 | LONGWD 7 | 345 | 16.5568 | 16.5842 | 0.0274
GEN-2022-139 | 04 SOUTHEAST | 508816 | OAKPH 4 | 138 | 20.4168 | 20.4388 | 0.022
GEN-2022-139 | 04 SOUTHEAST | 508827 | NGPL 4 | 138 | 9.7608 | 9.7773 | 0.0165
GEN-2022-139 | 04 SOUTHEAST | 508831 | DIANA 4 | 138 | 29.8521 | 30.0091 | 0.157
GEN-2022-139 | 04 SOUTHEAST | 508832 | DIANA 7 | 345 | 19.9563 | 20.1598 | 0.2035
GEN-2022-139 | 04 SOUTHEAST | 508833 | IPCJEFF4 | 138 | 12.7527 | 12.7679 | 0.0152
GEN-2022-139 | 04 SOUTHEAST | 508835 | JEFFRSN4 | 138 | 14.0836 | 14.1027 | 0.0191
GEN-2022-139 | 04 SOUTHEAST | 508837 | NGPLTAP4 | 138 | 12.6212 | 12.6486 | 0.0274
GEN-2022-139 | 04 SOUTHEAST | 508838 | NMARSHL2 | 69 | 10.1089 | 10.1182 | 0.0093
GEN-2022-139 | 04 SOUTHEAST | 508840 | WILKES 4 | 138 | 31.7324 | 31.7808 | 0.0484
GEN-2022-139 | 04 SOUTHEAST | 508841 | WILKES 7 | 345 | 16.3977 | 16.4302 | 0.0325
GEN-2022-139 | 04 SOUTHEAST | 509052 | STONWAL4 | 138 | 10.8688 | 10.8738 | 0.005
GEN-2022-139 | 04 SOUTHEAST | 509055 | BLOCKRT2 | 69 | 9.4895 | 9.497 | 0.0075
GEN-2022-139 | 04 SOUTHEAST | 509059 | CHEROKE4 | 138 | 17.0452 | 17.0807 | 0.0355
GEN-2022-139 | 04 SOUTHEAST | 509073 | MONROER4 | 138 | 12.3987 | 12.4192 | 0.0205
GEN-2022-139 | 04 SOUTHEAST | 509078 | OAK2HIL4 | 138 | 11.738 | 11.7564 | 0.0184
GEN-2022-139 | 04 SOUTHEAST | 509092 | EASTON 4 | 138 | 25.2921 | 25.3829 | 0.0908
GEN-2022-139 | 04 SOUTHEAST | 509103 | WLNTSPRINGS4 | 138 | 9.4307 | 9.4376 | 0.0069
GEN-2022-139 | 04 SOUTHEAST | 509240 | CROCKET4 | 138 | 7.1077 | 7.1175 | 0.0098
GEN-2022-139 | 04 SOUTHEAST | 509241 | CROCKET7 | 345 | 5.8763 | 5.8936 | 0.0173
GEN-2022-139 | 04 SOUTHEAST | 509322 | GRAPLND4 | 138 | 4.7135 | 4.7177 | 0.0042
GEN-2022-139 | 04 SOUTHEAST | 509602 | BIGSAND2 | 69 | 4.9689 | 4.9705 | 0.0016
GEN-2022-139 | 04 SOUTHEAST | 509603 | BIGSAND4 | 138 | 7.4814 | 7.4891 | 0.0077
GEN-2022-139 | 04 SOUTHEAST | 509606 | DIAN 2 | 69 | 8.4446 | 8.4509 | 0.0063
GEN-2022-139 | 04 SOUTHEAST | 509607 | DIAN 4 | 138 | 12.0063 | 12.0315 | 0.0252
GEN-2022-139 | 04 SOUTHEAST | 509612 | GILMR 4 | 138 | 4.5366 | 4.5394 | 0.0028
GEN-2022-139 | 04 SOUTHEAST | 509615 | HALLSVL4 | 138 | 4.5241 | 4.5277 | 0.0036
GEN-2022-139 | 04 SOUTHEAST | 509623 | LAKEPIN2 | 69 | 7.6873 | 7.6901 | 0.0028
GEN-2022-139 | 04 SOUTHEAST | 509624 | LAKEPIN4 | 138 | 7.7533 | 7.759 | 0.0057
GEN-2022-139 | 04 SOUTHEAST | 509628 | NOONDAY4 | 138 | 6.0723 | 6.0788 | 0.0065
GEN-2022-139 | 04 SOUTHEAST | 509639 | DIANASW4 | 138 | 12.495 | 12.5223 | 0.0273
GEN-2022-139 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.3725 | 15.3733 | 0.0008
GEN-2022-139 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 14.3127 | 14.3192 | 0.0065
GEN-2022-139 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.4254 | 15.4277 | 0.0023
GEN-2022-139 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.8796 | 11.8828 | 0.0032
GEN-2022-139 | 04 SOUTHEAST | 762845 | GEN-2018-050 | 345 | 16.2029 | 16.2291 | 0.0262
GEN-2022-139 | 04 SOUTHEAST | 764075 | GEN-2020-054 | 345 | 12.54 | 12.5543 | 0.0143
GEN-2022-139 | 04 SOUTHEAST | 764120 | GEN-2020-081 | 345 | 8.0441 | 8.1273 | 0.0832
GEN-2022-139 | 04 SOUTHEAST | 764510 | GEN-2020-020 | 345 | 10.5403 | 10.5464 | 0.0061
GEN-2022-139 | 04 SOUTHEAST | 764520 | G20-020-TAP | 345 | 10.5545 | 10.5606 | 0.0061
GEN-2022-139 | 04 SOUTHEAST | 765660 | GEN-2021-038 | 345 | 20.539 | 20.6272 | 0.0882
GEN-2022-139 | 04 SOUTHEAST | 767740 | G22-038-TAP | 138 | 17.3179 | 17.3412 | 0.0233
GEN-2022-139 | 04 SOUTHEAST | 769201 | GEN-2022-111 | 345 | 16.0438 | 16.0749 | 0.0311
GEN-2022-139 | 04 SOUTHEAST | 769761 | GEN-2022-139 | 345 | 17.0961 | 17.7191 | 0.623
GEN-2022-143 | 04 SOUTHEAST | 505598 | ALLEN 4 | 138 | 5.6629 | 5.6675 | 0.0046
GEN-2022-143 | 04 SOUTHEAST | 505600 | TUPELO 4 | 138 | 10.886 | 10.9175 | 0.0315
GEN-2022-143 | 04 SOUTHEAST | 505602 | S BROWN4 | 138 | 10.7906 | 11.0867 | 0.2961
GEN-2022-143 | 04 SOUTHEAST | 505604 | DENISON4 | 138 | 3.5054 | 3.5361 | 0.0307
GEN-2022-143 | 04 SOUTHEAST | 505665 | CENTRATAP4 | 138 | 10.661 | 10.6912 | 0.0302
GEN-2022-143 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 14.0006 | 14.005 | 0.0044
GEN-2022-143 | 04 SOUTHEAST | 510881 | ALLENGT4 | 138 | 10.5507 | 10.5802 | 0.0295
GEN-2022-143 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.341 | 15.3733 | 0.0323
GEN-2022-143 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 14.3031 | 14.3192 | 0.0161
GEN-2022-143 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.4193 | 15.4277 | 0.0084
GEN-2022-143 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 15.0522 | 15.0833 | 0.0311
GEN-2022-143 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 14.498 | 14.5034 | 0.0054
GEN-2022-143 | 04 SOUTHEAST | 511568 | TERRYRD7 | 345 | 10.6501 | 10.6714 | 0.0213
GEN-2022-143 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 16.9988 | 17.4114 | 0.4126
GEN-2022-143 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.3816 | 11.4848 | 0.1032
GEN-2022-143 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.2136 | 28.2163 | 0.0027
GEN-2022-143 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.0567 | 27.0684 | 0.0117
GEN-2022-143 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 42.4286 | 42.4768 | 0.0482
GEN-2022-143 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.8653 | 29.8897 | 0.0244
GEN-2022-143 | 04 SOUTHEAST | 515116 | ARBUCKL2 | 69 | 6.4866 | 6.4928 | 0.0062
GEN-2022-143 | 04 SOUTHEAST | 515117 | ARBUCKL4 | 138 | 16.8569 | 16.9608 | 0.1039
GEN-2022-143 | 04 SOUTHEAST | 515120 | RUSSET-4 | 138 | 12.6679 | 13.1211 | 0.4532
GEN-2022-143 | 04 SOUTHEAST | 515121 | MILLCKT4 | 138 | 11.9788 | 12.1197 | 0.1409
GEN-2022-143 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 12.1403 | 12.2901 | 0.1498
GEN-2022-143 | 04 SOUTHEAST | 515123 | OAKLAW-4 | 138 | 13.5984 | 13.6612 | 0.0628
GEN-2022-143 | 04 SOUTHEAST | 515133 | BLUERIV4 | 138 | 11.0708 | 11.0977 | 0.0269
GEN-2022-143 | 04 SOUTHEAST | 515135 | SUNNYSD4 | 138 | 20.6765 | 20.8458 | 0.1693
GEN-2022-143 | 04 SOUTHEAST | 515136 | SUNNYSD7 | 345 | 11.9675 | 12.0506 | 0.0831
GEN-2022-143 | 04 SOUTHEAST | 515147 | GLASSES4 | 138 | 9.2289 | 9.7718 | 0.5429
GEN-2022-143 | 04 SOUTHEAST | 515149 | MADINDT4 | 138 | 9.2274 | 9.7796 | 0.5522
GEN-2022-143 | 04 SOUTHEAST | 515150 | CANEYCK4 | 138 | 10.1887 | 11.1943 | 1.0056
GEN-2022-143 | 04 SOUTHEAST | 515151 | LTLCITY4 | 138 | 8.6583 | 8.9905 | 0.3322
GEN-2022-143 | 04 SOUTHEAST | 515152 | BROWNTP4 | 138 | 10.376 | 10.6507 | 0.2747
GEN-2022-143 | 04 SOUTHEAST | 515153 | COLEMNT4 | 138 | 7.3713 | 7.5087 | 0.1374
GEN-2022-143 | 04 SOUTHEAST | 515154 | EXPLRPL4 | 138 | 5.0813 | 5.146 | 0.0647
GEN-2022-143 | 04 SOUTHEAST | 515155 | BODLE 4 | 138 | 7.8673 | 8.0176 | 0.1503
GEN-2022-143 | 04 SOUTHEAST | 515157 | BROWN 4 | 138 | 10.7656 | 11.0619 | 0.2963
GEN-2022-143 | 04 SOUTHEAST | 515158 | MADLIND4 | 138 | 8.5582 | 9.0299 | 0.4717
GEN-2022-143 | 04 SOUTHEAST | 515159 | COLBRTP4 | 138 | 7.9825 | 8.1367 | 0.1542
GEN-2022-143 | 04 SOUTHEAST | 515172 | SPRNDAL4 | 138 | 12.7529 | 12.9212 | 0.1683
GEN-2022-143 | 04 SOUTHEAST | 515173 | BERWYN 4 | 138 | 8.8138 | 8.8615 | 0.0477
GEN-2022-143 | 04 SOUTHEAST | 515176 | BUTRFLD4 | 138 | 7.4863 | 7.6191 | 0.1328
GEN-2022-143 | 04 SOUTHEAST | 515193 | COLBRT-4 | 138 | 6.4018 | 6.4907 | 0.0889
GEN-2022-143 | 04 SOUTHEAST | 515196 | MILLCRK4 | 138 | 9.778 | 9.8717 | 0.0937
GEN-2022-143 | 04 SOUTHEAST | 515408 | REBAR 4 | 138 | 7.0415 | 7.1596 | 0.1181
GEN-2022-143 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.8003 | 11.8094 | 0.0091
GEN-2022-143 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 14.038 | 14.0664 | 0.0284
GEN-2022-143 | 04 SOUTHEAST | 515559 | SULPHR 4 | 138 | 15.2814 | 15.368 | 0.0866
GEN-2022-143 | 04 SOUTHEAST | 515873 | DRPSPRG4 | 138 | 11.7962 | 11.9557 | 0.1595
GEN-2022-143 | 04 SOUTHEAST | 515932 | STIRLNG4 | 138 | 10.6983 | 10.8538 | 0.1555
GEN-2022-143 | 04 SOUTHEAST | 515944 | STRRDTP4 | 138 | 10.6664 | 10.9571 | 0.2907
GEN-2022-143 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 8.1316 | 8.1798 | 0.0482
GEN-2022-143 | 04 SOUTHEAST | 520406 | TUPELO 4 | 138 | 9.9899 | 10.0157 | 0.0258
GEN-2022-143 | 04 SOUTHEAST | 520455 | MRIETA 4 | 138 | 7.3341 | 7.4922 | 0.1581
GEN-2022-143 | 04 SOUTHEAST | 520465 | REAGAN 4 | 138 | 4.5106 | 4.5672 | 0.0566
GEN-2022-143 | 04 SOUTHEAST | 520467 | ENOSJCT4 | 138 | 8.4232 | 9.0962 | 0.673
GEN-2022-143 | 04 SOUTHEAST | 520488 | LEBANON4 | 138 | 6.5205 | 6.797 | 0.2765
GEN-2022-143 | 04 SOUTHEAST | 520511 | ENVILLE4 | 138 | 6.9695 | 7.1985 | 0.229
GEN-2022-143 | 04 SOUTHEAST | 520860 | COLBERT4 | 138 | 6.4363 | 6.5254 | 0.0891
GEN-2022-143 | 04 SOUTHEAST | 520901 | ENOS 4 | 138 | 5.267 | 5.5235 | 0.2565
GEN-2022-143 | 04 SOUTHEAST | 520963 | KIERSEY4 | 138 | 6.9168 | 7.0291 | 0.1123
GEN-2022-143 | 04 SOUTHEAST | 520972 | LEBANTP4 | 138 | 7.5116 | 7.879 | 0.3674
GEN-2022-143 | 04 SOUTHEAST | 520988 | MARIETA4 | 138 | 7.8912 | 8.0365 | 0.1453
GEN-2022-143 | 04 SOUTHEAST | 521044 | RUSSETT4 | 138 | 12.5916 | 13.039 | 0.4474
GEN-2022-143 | 04 SOUTHEAST | 521049 | SCLMNJC4 | 138 | 8.7198 | 8.8902 | 0.1704
GEN-2022-143 | 04 SOUTHEAST | 521066 | TEXOMA 4 | 138 | 6.2633 | 6.6293 | 0.366
GEN-2022-143 | 04 SOUTHEAST | 521067 | TEXOMAJ4 | 138 | 10.0798 | 11.0559 | 0.9761
GEN-2022-143 | 04 SOUTHEAST | 521071 | STNWLSW4 | 138 | 10.6559 | 10.6848 | 0.0289
GEN-2022-143 | 04 SOUTHEAST | 521074 | BOGGY4 | 138 | 9.0367 | 9.0573 | 0.0206
GEN-2022-143 | 04 SOUTHEAST | 521122 | HOWE 4 | 138 | 12.0197 | 12.1666 | 0.1469
GEN-2022-143 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.8669 | 11.8828 | 0.0159
GEN-2022-143 | 04 SOUTHEAST | 560088 | G17-075-TAP | 345 | 7.8157 | 7.8347 | 0.019
GEN-2022-143 | 04 SOUTHEAST | 587200 | GEN-2016-030 | 138 | 7.2921 | 7.4259 | 0.1338
GEN-2022-143 | 04 SOUTHEAST | 588180 | GEN-2016-126 | 138 | 13.8693 | 13.9384 | 0.0691
GEN-2022-143 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 19.0583 | 19.0634 | 0.0051
GEN-2022-143 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 3.9193 | 3.9297 | 0.0104
GEN-2022-143 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 9.9058 | 9.9188 | 0.013
GEN-2022-143 | 04 SOUTHEAST | 764520 | G20-020-TAP | 345 | 10.5575 | 10.5606 | 0.0031
GEN-2022-143 | 04 SOUTHEAST | 765300 | GEN-2021-001 | 138 | 10.5842 | 10.8698 | 0.2856
GEN-2022-143 | 04 SOUTHEAST | 765450 | GEN-2021-016 | 345 | 11.3224 | 11.3987 | 0.0763
GEN-2022-143 | 04 SOUTHEAST | 765451 | G21-016-TAP | 345 | 11.6821 | 11.7632 | 0.0811
GEN-2022-143 | 04 SOUTHEAST | 769060 | G22-104-TAP | 138 | 9.8619 | 10.0947 | 0.2328
GEN-2022-143 | 04 SOUTHEAST | 769061 | GEN-2022-104 | 138 | 9.8472 | 10.0792 | 0.232
GEN-2022-143 | 04 SOUTHEAST | 769841 | GEN-2022-143 | 138 | 10.1178 | 11.1244 | 1.0066
GEN-2022-145 | 04 SOUTHEAST | 511433 | HINTON 4 | 138 | 6.1965 | 6.5692 | 0.3727
GEN-2022-145 | 04 SOUTHEAST | 511481 | WEATHER2 | 69 | 4.4951 | 4.7164 | 0.2213
GEN-2022-145 | 04 SOUTHEAST | 511489 | WTH_JCT4 | 138 | 5.3527 | 6.2743 | 0.9216
GEN-2022-145 | 04 SOUTHEAST | 511496 | WTH_SE 2 | 69 | 4.9547 | 5.2373 | 0.2826
GEN-2022-145 | 04 SOUTHEAST | 511497 | WTH_SE 4 | 138 | 5.3792 | 6.2523 | 0.8731
GEN-2022-145 | 04 SOUTHEAST | 511506 | WTH WF 4 | 138 | 5.575 | 6.2068 | 0.6318
GEN-2022-145 | 04 SOUTHEAST | 511517 | THOMAST2 | 69 | 4.3529 | 4.5557 | 0.2028
GEN-2022-145 | 04 SOUTHEAST | 511532 | WEATHER4 | 138 | 4.7378 | 5.2838 | 0.546
GEN-2022-145 | 04 SOUTHEAST | 511534 | CL-NGTP4 | 138 | 5.7101 | 6.2096 | 0.4995
GEN-2022-145 | 04 SOUTHEAST | 511536 | WEATHTP4 | 138 | 5.4375 | 6.1684 | 0.7309
GEN-2022-145 | 04 SOUTHEAST | 511540 | CAN_GAS4 | 138 | 9.7355 | 9.9695 | 0.234
GEN-2022-145 | 04 SOUTHEAST | 511548 | REDROCKRD4 | 138 | 9.4815 | 9.7291 | 0.2476
GEN-2022-145 | 04 SOUTHEAST | 511559 | DARLINGTNRD4 | 138 | 7.2301 | 7.3424 | 0.1123
GEN-2022-145 | 04 SOUTHEAST | 511581 | MAPLERD4 | 138 | 6.9539 | 7.0527 | 0.0988
GEN-2022-145 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 19.482 | 19.5845 | 0.1025
GEN-2022-145 | 04 SOUTHEAST | 514821 | JENSEN 4 | 138 | 16.8274 | 16.9859 | 0.1585
GEN-2022-145 | 04 SOUTHEAST | 515347 | MPLROAD4 | 138 | 6.2697 | 6.35 | 0.0803
GEN-2022-145 | 04 SOUTHEAST | 515460 | TALBEAR4 | 138 | 8.5432 | 8.7231 | 0.1799
GEN-2022-145 | 04 SOUTHEAST | 515472 | TLBEART4 | 138 | 9.676 | 9.9071 | 0.2311
GEN-2022-145 | 04 SOUTHEAST | 515931 | GEARYTP4 | 138 | 5.848 | 5.8862 | 0.0382
GEN-2022-145 | 04 SOUTHEAST | 520893 | EL RENO4 | 138 | 15.7289 | 15.8379 | 0.109
GEN-2022-145 | 04 SOUTHEAST | 769880 | G22-145-TAP | 138 | 5.3435 | 6.2864 | 0.9429
GEN-2022-145 | 04 SOUTHEAST | 769881 | GEN-2022-145 | 138 | 5.11 | 6.0617 | 0.9517
GEN-2022-147 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 5.4555 | 5.4635 | 0.008
GEN-2022-147 | 05 SOUTHWEST | 511467 | L.E.S.-4 | 138 | 24.7098 | 24.7136 | 0.0038
GEN-2022-147 | 05 SOUTHWEST | 511468 | L.E.S.-7 | 345 | 12.4511 | 12.4557 | 0.0046
GEN-2022-147 | 05 SOUTHWEST | 511490 | ELKCITY6 | 230 | 6.4217 | 6.4218 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 511541 | SWEETWT6 | 230 | 7.1968 | 7.1969 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 5.5559 | 5.5561 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 8.2331 | 8.2333 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 5.438 | 5.4459 | 0.0079
GEN-2022-147 | 05 SOUTHWEST | 514785 | WOODWRD4 | 138 | 17.6752 | 17.6759 | 0.0007
GEN-2022-147 | 05 SOUTHWEST | 514796 | IODINE-4 | 138 | 7.7283 | 7.7284 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 18.8941 | 18.8985 | 0.0044
GEN-2022-147 | 05 SOUTHWEST | 515376 | WWRDEHV4 | 138 | 25.3986 | 25.4006 | 0.002
GEN-2022-147 | 05 SOUTHWEST | 515394 | KEENAN 4 | 138 | 9.0934 | 9.0936 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 515398 | OUSPRT 4 | 138 | 9.945 | 9.9453 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 515407 | TATONGA7 | 345 | 17.1451 | 17.1467 | 0.0016
GEN-2022-147 | 05 SOUTHWEST | 515425 | WWDPST 4 | 138 | 19.1752 | 19.1762 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 515448 | CRSRDSW7 | 345 | 12.1325 | 12.1333 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 4.5209 | 4.5275 | 0.0066
GEN-2022-147 | 05 SOUTHWEST | 515497 | MATHWSN7 | 345 | 30.8878 | 30.8894 | 0.0016
GEN-2022-147 | 05 SOUTHWEST | 515582 | SLNGWND7 | 345 | 8.549 | 8.5494 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 515585 | MAMTHPW7 | 345 | 13.662 | 13.663 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 14.002 | 14.0029 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 515800 | GRACMNT7 | 345 | 15.9365 | 15.9388 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 515825 | GRTWSRN7 | 345 | 8.623 | 8.6239 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 515852 | DGRASSE7 | 345 | 13.8362 | 13.8373 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 515853 | DGRASSE4 | 138 | 14.8474 | 14.8477 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 515951 | PERSIMN7 | 345 | 10.4593 | 10.4607 | 0.0014
GEN-2022-147 | 05 SOUTHWEST | 515961 | GUTHRIE7 | 345 | 11.8132 | 11.8149 | 0.0017
GEN-2022-147 | 05 SOUTHWEST | 516059 | BECKHAM7 | 345 | 5.0681 | 5.0739 | 0.0058
GEN-2022-147 | 05 SOUTHWEST | 516146 | 25MILE 7 | 345 | 10.1481 | 10.1491 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 9.5302 | 9.5306 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.7364 | 7.7366 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 5.7482 | 5.7484 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.4783 | 4.4784 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 21.8592 | 21.8623 | 0.0031
GEN-2022-147 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 10.2925 | 10.2933 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 27.4822 | 27.486 | 0.0038
GEN-2022-147 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 27.4822 | 27.486 | 0.0038
GEN-2022-147 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 27.4822 | 27.486 | 0.0038
GEN-2022-147 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.4332 | 20.4356 | 0.0024
GEN-2022-147 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 30.7891 | 30.7912 | 0.0021
GEN-2022-147 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.6229 | 26.6266 | 0.0037
GEN-2022-147 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1038 | 10.1048 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 21.3151 | 21.3175 | 0.0024
GEN-2022-147 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 15.19 | 15.1921 | 0.0021
GEN-2022-147 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 15.8885 | 15.8897 | 0.0012
GEN-2022-147 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 14.0617 | 14.0626 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 524404 | OWENSCORN 3 | 115 | 15.4507 | 15.4518 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 17.297 | 17.2984 | 0.0014
GEN-2022-147 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 14.2199 | 14.2225 | 0.0026
GEN-2022-147 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.6588 | 6.659 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.3707 | 8.3719 | 0.0012
GEN-2022-147 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 10.1397 | 10.1415 | 0.0018
GEN-2022-147 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.6062 | 10.6073 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.4779 | 6.4788 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.1165 | 11.1179 | 0.0014
GEN-2022-147 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 9.7829 | 9.784 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8549 | 7.8562 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.6058 | 4.606 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 10.7085 | 10.7098 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.7185 | 9.7206 | 0.0021
GEN-2022-147 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.5606 | 7.5612 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.4663 | 5.4668 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.2165 | 8.2179 | 0.0014
GEN-2022-147 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.7221 | 7.7244 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.7662 | 6.7681 | 0.0019
GEN-2022-147 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.3751 | 4.3757 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 12.1912 | 12.1995 | 0.0083
GEN-2022-147 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 11.532 | 11.5399 | 0.0079
GEN-2022-147 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 11.0285 | 11.0453 | 0.0168
GEN-2022-147 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.7457 | 6.7485 | 0.0028
GEN-2022-147 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.6239 | 5.626 | 0.0021
GEN-2022-147 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.3945 | 6.3963 | 0.0018
GEN-2022-147 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.6978 | 2.6981 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.2337 | 3.2342 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.7556 | 6.759 | 0.0034
GEN-2022-147 | 05 SOUTHWEST | 525351 | LH-AIKEN 2 | 69 | 2.2599 | 2.2602 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 4.7247 | 4.7253 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.8573 | 7.8599 | 0.0026
GEN-2022-147 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 5.8245 | 5.826 | 0.0015
GEN-2022-147 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.2763 | 7.2782 | 0.0019
GEN-2022-147 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 9.4807 | 9.4832 | 0.0025
GEN-2022-147 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 6.7828 | 6.7848 | 0.002
GEN-2022-147 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.6395 | 10.6477 | 0.0082
GEN-2022-147 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 14.9334 | 14.9414 | 0.008
GEN-2022-147 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 11.629 | 11.6383 | 0.0093
GEN-2022-147 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 15.5622 | 15.568 | 0.0058
GEN-2022-147 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 24.1129 | 24.1322 | 0.0193
GEN-2022-147 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 30.228 | 30.2561 | 0.0281
GEN-2022-147 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 13.3535 | 13.3607 | 0.0072
GEN-2022-147 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.6227 | 10.6264 | 0.0037
GEN-2022-147 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.216 | 11.2202 | 0.0042
GEN-2022-147 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.216 | 11.2202 | 0.0042
GEN-2022-147 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 6.078 | 6.0784 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.5365 | 8.5382 | 0.0017
GEN-2022-147 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.8497 | 5.8509 | 0.0012
GEN-2022-147 | 05 SOUTHWEST | 525723 | CNTYLINE_TP2 | 69 | 2.3006 | 2.3012 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.1356 | 3.1368 | 0.0012
GEN-2022-147 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.6025 | 2.6033 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 525745 | LH-HALECTR 2 | 69 | 2.5735 | 2.5743 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 6.144 | 6.1475 | 0.0035
GEN-2022-147 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.486 | 5.4879 | 0.0019
GEN-2022-147 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 7.0349 | 7.0398 | 0.0049
GEN-2022-147 | 05 SOUTHWEST | 525790 | FLOYDADA_TP2 | 69 | 2.7045 | 2.7049 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 525801 | LRNZ_MPT 3 | 115 | 6.1119 | 6.1148 | 0.0029
GEN-2022-147 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 6.1129 | 6.1158 | 0.0029
GEN-2022-147 | 05 SOUTHWEST | 525811 | LH-HARMONY 2 | 69 | 4.4159 | 4.4171 | 0.0012
GEN-2022-147 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.6866 | 4.6891 | 0.0025
GEN-2022-147 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 8.1395 | 8.147 | 0.0075
GEN-2022-147 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 20.6526 | 20.7387 | 0.0861
GEN-2022-147 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 22.8699 | 23.2093 | 0.3394
GEN-2022-147 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 13.4686 | 13.8895 | 0.4209
GEN-2022-147 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 22.6771 | 23.0104 | 0.3333
GEN-2022-147 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.3564 | 13.7692 | 0.4128
GEN-2022-147 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.7436 | 2.7445 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 525860 | SP-BECTON +2 | 69 | 2.4399 | 2.4406 | 0.0007
GEN-2022-147 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.5089 | 3.5103 | 0.0014
GEN-2022-147 | 05 SOUTHWEST | 525892 | MONROE 2 | 69 | 2.8258 | 2.8267 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 525925 | CROSBY 2 | 69 | 5.3568 | 5.358 | 0.0012
GEN-2022-147 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 5.4536 | 5.4559 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 12.1425 | 12.2148 | 0.0723
GEN-2022-147 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.6856 | 5.6866 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 9.321 | 9.3329 | 0.0119
GEN-2022-147 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 11.3482 | 11.3639 | 0.0157
GEN-2022-147 | 05 SOUTHWEST | 526130 | SP-CARLISLE2 | 69 | 2.2747 | 2.275 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.7062 | 9.7186 | 0.0124
GEN-2022-147 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.7964 | 2.7969 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 13.0988 | 13.1187 | 0.0199
GEN-2022-147 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.9519 | 10.9865 | 0.0346
GEN-2022-147 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.6988 | 11.7136 | 0.0148
GEN-2022-147 | 05 SOUTHWEST | 526176 | LP-DOUD 3 | 115 | 9.1804 | 9.1896 | 0.0092
GEN-2022-147 | 05 SOUTHWEST | 526184 | SW_6878 2 | 69 | 2.3517 | 2.3521 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 10.7652 | 10.7775 | 0.0123
GEN-2022-147 | 05 SOUTHWEST | 526195 | QUINCY 3 | 115 | 10.2055 | 10.2161 | 0.0106
GEN-2022-147 | 05 SOUTHWEST | 526213 | ALLEN 3 | 115 | 11.1585 | 11.1698 | 0.0113
GEN-2022-147 | 05 SOUTHWEST | 526267 | LUBBCK_STH 2 | 69 | 4.3403 | 4.3412 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 18.9816 | 19.0112 | 0.0296
GEN-2022-147 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 16.6931 | 16.7338 | 0.0407
GEN-2022-147 | 05 SOUTHWEST | 526284 | PLANTERS 2 | 69 | 6.3717 | 6.3737 | 0.002
GEN-2022-147 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 8.8702 | 8.8741 | 0.0039
GEN-2022-147 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 15.6191 | 15.6416 | 0.0225
GEN-2022-147 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 12.5636 | 12.5852 | 0.0216
GEN-2022-147 | 05 SOUTHWEST | 526310 | CLUTTER 2 | 69 | 5.9009 | 5.9026 | 0.0017
GEN-2022-147 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 18.8102 | 18.8585 | 0.0483
GEN-2022-147 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 10.9356 | 10.9398 | 0.0042
GEN-2022-147 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.6933 | 11.7054 | 0.0121
GEN-2022-147 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.3811 | 10.3901 | 0.009
GEN-2022-147 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 11.0694 | 11.0818 | 0.0124
GEN-2022-147 | 05 SOUTHWEST | 526481 | SP-WOLF_TP 3 | 115 | 11.2374 | 11.2505 | 0.0131
GEN-2022-147 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.5479 | 11.5595 | 0.0116
GEN-2022-147 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.4639 | 13.4967 | 0.0328
GEN-2022-147 | 05 SOUTHWEST | 526562 | SLATON 2 | 69 | 2.6898 | 2.6902 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 526602 | WOODROW 3 | 115 | 9.7907 | 9.7983 | 0.0076
GEN-2022-147 | 05 SOUTHWEST | 526656 | LYNN_CNTY 3 | 115 | 6.4142 | 6.4171 | 0.0029
GEN-2022-147 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 7.4448 | 7.4486 | 0.0038
GEN-2022-147 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.5872 | 6.593 | 0.0058
GEN-2022-147 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 5.1618 | 5.1653 | 0.0035
GEN-2022-147 | 05 SOUTHWEST | 526694 | GRAHAM 3 | 115 | 3.0632 | 3.0638 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 11.2142 | 11.2185 | 0.0043
GEN-2022-147 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.8836 | 15.8932 | 0.0096
GEN-2022-147 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.3525 | 6.3537 | 0.0012
GEN-2022-147 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.7761 | 10.7789 | 0.0028
GEN-2022-147 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 19.9638 | 19.9734 | 0.0096
GEN-2022-147 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 21.8261 | 21.8532 | 0.0271
GEN-2022-147 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 12.7501 | 12.7761 | 0.026
GEN-2022-147 | 05 SOUTHWEST | 527000 | GAINES_PLNT7 | 345 | 14.6739 | 14.6765 | 0.0026
GEN-2022-147 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 16.5772 | 16.5901 | 0.0129
GEN-2022-147 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 16.4211 | 16.4337 | 0.0126
GEN-2022-147 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 16.0865 | 16.0979 | 0.0114
GEN-2022-147 | 05 SOUTHWEST | 527020 | SIDEWINDER 7 | 345 | 15.0224 | 15.0258 | 0.0034
GEN-2022-147 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 14.184 | 14.1863 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 12.1008 | 12.1056 | 0.0048
GEN-2022-147 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 14.4571 | 14.4606 | 0.0035
GEN-2022-147 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 25.1781 | 25.1859 | 0.0078
GEN-2022-147 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 17.5864 | 17.5969 | 0.0105
GEN-2022-147 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 17.5864 | 17.5969 | 0.0105
GEN-2022-147 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 8.3828 | 8.3841 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.7119 | 8.7141 | 0.0022
GEN-2022-147 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 10.0599 | 10.0623 | 0.0024
GEN-2022-147 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 10.1498 | 10.1521 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 11.6741 | 11.6773 | 0.0032
GEN-2022-147 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 8.2826 | 8.2833 | 0.0007
GEN-2022-147 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 19.4285 | 19.4314 | 0.0029
GEN-2022-147 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 34.446 | 34.4498 | 0.0038
GEN-2022-147 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 21.7873 | 21.7918 | 0.0045
GEN-2022-147 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 16.8857 | 16.8926 | 0.0069
GEN-2022-147 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 10.9583 | 10.9603 | 0.002
GEN-2022-147 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 19.4095 | 19.4111 | 0.0016
GEN-2022-147 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 7.0436 | 7.0443 | 0.0007
GEN-2022-147 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 31.6375 | 31.6437 | 0.0062
GEN-2022-147 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 12.4873 | 12.4902 | 0.0029
GEN-2022-147 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 7.9994 | 8.0003 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 528604 | ANDREWS 6 | 345 | 11.7471 | 11.7493 | 0.0022
GEN-2022-147 | 05 SOUTHWEST | 539801 | THISTLE7 | 345 | 15.05 | 15.0505 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 560071 | G16-003-TAP | 345 | 14.7367 | 14.7387 | 0.002
GEN-2022-147 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 6.7476 | 6.7479 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 587230 | GEN-2016-037 | 345 | 6.5073 | 6.5076 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 588560 | GEN-2017-011 | 345 | 12.0416 | 12.043 | 0.0014
GEN-2022-147 | 05 SOUTHWEST | 588760 | GEN-2017-033 | 345 | 4.067 | 4.0712 | 0.0042
GEN-2022-147 | 05 SOUTHWEST | 599891 | OKLAUN 7 | 345 | 4.2384 | 4.2384 | 0
GEN-2022-147 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.7185 | 9.7206 | 0.0021
GEN-2022-147 | 05 SOUTHWEST | 599956 | PNM-DC7 | 345 | #VALUE! | #VALUE! | #VALUE!
GEN-2022-147 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.7705 | 7.7718 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 8.0708 | 8.0722 | 0.0014
GEN-2022-147 | 05 SOUTHWEST | 760938 | G17-171-TAP | 345 | 9.9105 | 9.9128 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 14.0108 | 14.0161 | 0.0053
GEN-2022-147 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.3558 | 8.4776 | 0.1218
GEN-2022-147 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 6.182 | 6.2453 | 0.0633
GEN-2022-147 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 5.1603 | 5.1786 | 0.0183
GEN-2022-147 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 5.1693 | 5.1876 | 0.0183
GEN-2022-147 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 11.2997 | 11.3084 | 0.0087
GEN-2022-147 | 05 SOUTHWEST | 763318 | GEN-2018-115 | 345 | 12.2348 | 12.2392 | 0.0044
GEN-2022-147 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.7893 | 8.791 | 0.0017
GEN-2022-147 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 11.7488 | 11.7708 | 0.022
GEN-2022-147 | 05 SOUTHWEST | 763527 | GEN-2019-012 | 345 | 16.7366 | 16.74 | 0.0034
GEN-2022-147 | 05 SOUTHWEST | 764550 | G20-087-TAP | 345 | 12.1915 | 12.195 | 0.0035
GEN-2022-147 | 05 SOUTHWEST | 764875 | GEN-2020-060 | 230 | 12.3669 | 12.3878 | 0.0209
GEN-2022-147 | 05 SOUTHWEST | 764935 | GEN-2020-067 | 345 | 6.9021 | 6.9314 | 0.0293
GEN-2022-147 | 05 SOUTHWEST | 764945 | G20-067-TAP | 345 | 8.3312 | 8.3753 | 0.0441
GEN-2022-147 | 05 SOUTHWEST | 766120 | GEN-2021-090 | 345 | 12.675 | 12.7006 | 0.0256
GEN-2022-147 | 05 SOUTHWEST | 767221 | GEN-2022-012 | 345 | 18.6487 | 18.6529 | 0.0042
GEN-2022-147 | 05 SOUTHWEST | 767301 | GEN-2022-016 | 345 | 18.6636 | 18.6679 | 0.0043
GEN-2022-147 | 05 SOUTHWEST | 767321 | GEN-2022-017 | 345 | 18.4241 | 18.4282 | 0.0041
GEN-2022-147 | 05 SOUTHWEST | 769921 | GEN-2022-147 | 345 | 13.327 | 13.748 | 0.421
GEN-2022-154 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 22.4358 | 22.608 | 0.1722
GEN-2022-154 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 43.568 | 43.7133 | 0.1453
GEN-2022-154 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 35.5132 | 35.6921 | 0.1789
GEN-2022-154 | 04 SOUTHEAST | 514947 | CANADN-4 | 138 | 23.1357 | 23.629 | 0.4933
GEN-2022-154 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 24.9418 | 25.2202 | 0.2784
GEN-2022-154 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 23.9064 | 24.1149 | 0.2085
GEN-2022-154 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 36.7667 | 36.9272 | 0.1605
GEN-2022-154 | 04 SOUTHEAST | 514957 | CHERYCK4 | 138 | 23.1838 | 23.2905 | 0.1067
GEN-2022-154 | 04 SOUTHEAST | 514958 | BOYD 4 | 138 | 21.538 | 21.6678 | 0.1298
GEN-2022-154 | 04 SOUTHEAST | 515007 | NOBLE 4 | 138 | 19.638 | 19.9736 | 0.3356
GEN-2022-154 | 04 SOUTHEAST | 515097 | WLNUTCK4 | 138 | 10.0386 | 10.0875 | 0.0489
GEN-2022-154 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 11.0132 | 11.0286 | 0.0154
GEN-2022-154 | 04 SOUTHEAST | 515475 | PURCELL4 | 138 | 10.7272 | 10.7907 | 0.0635
GEN-2022-154 | 04 SOUTHEAST | 520400 | NOBLE4 | 138 | 22.6902 | 23.162 | 0.4718
GEN-2022-154 | 04 SOUTHEAST | 520401 | BAILEY4 | 138 | 10.7863 | 10.7974 | 0.0111
GEN-2022-154 | 04 SOUTHEAST | 520403 | LAMAR4 | 138 | 13.2931 | 13.3481 | 0.055
GEN-2022-154 | 04 SOUTHEAST | 520489 | MOORE 2 | 69 | 3.1038 | 3.1047 | 0.0009
GEN-2022-154 | 04 SOUTHEAST | 520508 | CLVLDSW4 | 138 | 13.2998 | 13.3069 | 0.0071
GEN-2022-154 | 04 SOUTHEAST | 520530 | AMBERTP4 | 138 | 8.6397 | 8.6501 | 0.0104
GEN-2022-154 | 04 SOUTHEAST | 520531 | AMBER 4 | 138 | 7.6909 | 7.6991 | 0.0082
GEN-2022-154 | 04 SOUTHEAST | 520802 | ACME 4 | 138 | 14.5246 | 14.5743 | 0.0497
GEN-2022-154 | 04 SOUTHEAST | 520828 | BLANCHD4 | 138 | 12.9736 | 13.0272 | 0.0536
GEN-2022-154 | 04 SOUTHEAST | 520841 | CANADNS2 | 69 | 8.6216 | 8.6497 | 0.0281
GEN-2022-154 | 04 SOUTHEAST | 520842 | CANADNS4 | 138 | 23.0986 | 23.5968 | 0.4982
GEN-2022-154 | 04 SOUTHEAST | 520861 | COLE 4 | 138 | 11.545 | 11.5839 | 0.0389
GEN-2022-154 | 04 SOUTHEAST | 520868 | CRINER 4 | 138 | 8.9588 | 8.9723 | 0.0135
GEN-2022-154 | 04 SOUTHEAST | 520888 | PAYNESW4 | 138 | 9.5715 | 9.5812 | 0.0097
GEN-2022-154 | 04 SOUTHEAST | 520898 | ELMORE 2 | 69 | 4.4554 | 4.4562 | 0.0008
GEN-2022-154 | 04 SOUTHEAST | 520913 | FRANKLN4 | 138 | 12.4712 | 12.4923 | 0.0211
GEN-2022-154 | 04 SOUTHEAST | 520916 | FRNKLNS2 | 69 | 5.5727 | 5.5754 | 0.0027
GEN-2022-154 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 30.9132 | 31.0876 | 0.1744
GEN-2022-154 | 04 SOUTHEAST | 520924 | GOLDSBY4 | 138 | 15.4262 | 15.5689 | 0.1427
GEN-2022-154 | 04 SOUTHEAST | 520973 | LEXNGTN2 | 69 | 3.4821 | 3.4842 | 0.0021
GEN-2022-154 | 04 SOUTHEAST | 520975 | LIDDELL4 | 138 | 18.9438 | 19.1103 | 0.1665
GEN-2022-154 | 04 SOUTHEAST | 520976 | LIL AXE2 | 69 | 4.2345 | 4.2395 | 0.005
GEN-2022-154 | 04 SOUTHEAST | 521022 | PAOLI 2 | 69 | 6.3887 | 6.3909 | 0.0022
GEN-2022-154 | 04 SOUTHEAST | 521023 | PAOLI 4 | 138 | 7.547 | 7.5513 | 0.0043
GEN-2022-154 | 04 SOUTHEAST | 521028 | PINK SW4 | 138 | 8.5403 | 8.5461 | 0.0058
GEN-2022-154 | 04 SOUTHEAST | 521095 | WNORMAN4 | 138 | 13.0351 | 13.0807 | 0.0456
GEN-2022-154 | 04 SOUTHEAST | 521104 | OU SW 4 | 138 | 15.4148 | 15.498 | 0.0832
GEN-2022-154 | 04 SOUTHEAST | 521123 | WMOORE 4 | 138 | 12.4387 | 12.4575 | 0.0188
GEN-2022-154 | 04 SOUTHEAST | 766110 | GEN-2021-088 | 138 | 22.0065 | 22.4247 | 0.4182
GEN-2022-154 | 04 SOUTHEAST | 766111 | G21-088-TAP | 138 | 23.0633 | 23.5245 | 0.4612
GEN-2022-154 | 04 SOUTHEAST | 770061 | GEN-2022-154 | 138 | 22.6621 | 23.1604 | 0.4983
GEN-2022-155 | 04 SOUTHEAST | 300135 | 4LUTHER | 138 | 8.7927 | 8.8037 | 0.011
GEN-2022-155 | 04 SOUTHEAST | 300136 | 4MEMORALT | 138 | 21.5012 | 21.589 | 0.0878
GEN-2022-155 | 04 SOUTHEAST | 300834 | 2CARNEY | 69 | 5.2231 | 5.2236 | 0.0005
GEN-2022-155 | 04 SOUTHEAST | 300839 | 2MERIDAN | 69 | 5.4589 | 5.4598 | 0.0009
GEN-2022-155 | 04 SOUTHEAST | 300856 | 2LUTHER | 69 | 6.9184 | 6.9201 | 0.0017
GEN-2022-155 | 04 SOUTHEAST | 300915 | 4WARWICK | 138 | 4.9631 | 4.9658 | 0.0027
GEN-2022-155 | 04 SOUTHEAST | 301372 | 4LUTHERD | 138 | 8.7821 | 8.7931 | 0.011
GEN-2022-155 | 04 SOUTHEAST | 301541 | 4MEMORAL | 138 | 21.2878 | 21.3739 | 0.0861
GEN-2022-155 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.4446 | 33.447 | 0.0024
GEN-2022-155 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.3716 | 15.3733 | 0.0017
GEN-2022-155 | 04 SOUTHEAST | 514501 | KELLYAV4 | 138 | 27.1905 | 27.2564 | 0.0659
GEN-2022-155 | 04 SOUTHEAST | 514510 | BURGETT4 | 138 | 23.5557 | 23.5891 | 0.0334
GEN-2022-155 | 04 SOUTHEAST | 514714 | WOODRNG4 | 138 | 20.2978 | 20.2994 | 0.0016
GEN-2022-155 | 04 SOUTHEAST | 514733 | MARSHL 4 | 138 | 8.3539 | 8.3546 | 0.0007
GEN-2022-155 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 19.1772 | 19.1878 | 0.0106
GEN-2022-155 | 04 SOUTHEAST | 514829 | PINE ST4 | 138 | 13.0866 | 13.091 | 0.0044
GEN-2022-155 | 04 SOUTHEAST | 514830 | FITZGRD4 | 138 | 9.8856 | 9.8875 | 0.0019
GEN-2022-155 | 04 SOUTHEAST | 514831 | WATRLOO4 | 138 | 15.3035 | 15.3129 | 0.0094
GEN-2022-155 | 04 SOUTHEAST | 514832 | EASTERN4 | 138 | 25.3735 | 25.4215 | 0.048
GEN-2022-155 | 04 SOUTHEAST | 514833 | DANFRTH4 | 138 | 27.5832 | 27.6297 | 0.0465
GEN-2022-155 | 04 SOUTHEAST | 514835 | MEMRIAL4 | 138 | 38.0352 | 38.1626 | 0.1274
GEN-2022-155 | 04 SOUTHEAST | 514837 | TENESTP4 | 138 | 32.4365 | 32.5217 | 0.0852
GEN-2022-155 | 04 SOUTHEAST | 514839 | BRYANT 4 | 138 | 30.7994 | 30.9142 | 0.1148
GEN-2022-155 | 04 SOUTHEAST | 514842 | CHTWOOD4 | 138 | 21.8787 | 21.9719 | 0.0932
GEN-2022-155 | 04 SOUTHEAST | 514850 | SKYLINE4 | 138 | 34.1436 | 34.2285 | 0.0849
GEN-2022-155 | 04 SOUTHEAST | 514875 | OUMED 4 | 138 | 23.2387 | 23.2977 | 0.059
GEN-2022-155 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 46.9685 | 47.0292 | 0.0607
GEN-2022-155 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.089 | 35.126 | 0.037
GEN-2022-155 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.6253 | 24.6397 | 0.0144
GEN-2022-155 | 04 SOUTHEAST | 514884 | DUNJEE 4 | 138 | 22.2089 | 22.3591 | 0.1502
GEN-2022-155 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 37.6691 | 37.7045 | 0.0354
GEN-2022-155 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 21.6625 | 21.7518 | 0.0893
GEN-2022-155 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 43.1697 | 43.2808 | 0.1111
GEN-2022-155 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.1811 | 28.2163 | 0.0352
GEN-2022-155 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.229 | 27.258 | 0.029
GEN-2022-155 | 04 SOUTHEAST | 514923 | LIGHTCK4 | 138 | 26.1685 | 26.2271 | 0.0586
GEN-2022-155 | 04 SOUTHEAST | 514927 | HSLEAST2 | 69 | 11.8003 | 11.8237 | 0.0234
GEN-2022-155 | 04 SOUTHEAST | 514930 | OAKTRET4 | 138 | 22.5956 | 22.608 | 0.0124
GEN-2022-155 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 43.6502 | 43.7133 | 0.0631
GEN-2022-155 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.0393 | 27.0684 | 0.0291
GEN-2022-155 | 04 SOUTHEAST | 514937 | HSLWEST2 | 69 | 12.4517 | 12.4789 | 0.0272
GEN-2022-155 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 43.7834 | 44.7905 | 1.0071
GEN-2022-155 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 35.6558 | 35.6921 | 0.0363
GEN-2022-155 | 04 SOUTHEAST | 514948 | CEDARLN4 | 138 | 25.2056 | 25.2202 | 0.0146
GEN-2022-155 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 24.1009 | 24.1149 | 0.014
GEN-2022-155 | 04 SOUTHEAST | 514951 | LITTLAX2 | 69 | 3.4864 | 3.4875 | 0.0011
GEN-2022-155 | 04 SOUTHEAST | 514953 | HOLLYWD4 | 138 | 36.8892 | 36.9272 | 0.038
GEN-2022-155 | 04 SOUTHEAST | 514956 | MACOCTP2 | 69 | 3.4402 | 3.4411 | 0.0009
GEN-2022-155 | 04 SOUTHEAST | 514959 | FOSTER 4 | 138 | 27.1533 | 27.2115 | 0.0582
GEN-2022-155 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.8428 | 20.8622 | 0.0194
GEN-2022-155 | 04 SOUTHEAST | 514963 | TROSPER4 | 138 | 29.6974 | 29.7929 | 0.0955
GEN-2022-155 | 04 SOUTHEAST | 514964 | NE10TH 4 | 138 | 19.0476 | 19.1337 | 0.0861
GEN-2022-155 | 04 SOUTHEAST | 514966 | MIDWAY 4 | 138 | 19.1825 | 19.3234 | 0.1409
GEN-2022-155 | 04 SOUTHEAST | 514969 | NE30TH 2 | 69 | 9.2883 | 9.2955 | 0.0072
GEN-2022-155 | 04 SOUTHEAST | 514970 | DEEPFKT2 | 69 | 7.955 | 7.9607 | 0.0057
GEN-2022-155 | 04 SOUTHEAST | 514971 | GRNPAST2 | 69 | 6.0414 | 6.0459 | 0.0045
GEN-2022-155 | 04 SOUTHEAST | 514972 | RENO 2 | 69 | 14.5257 | 14.5408 | 0.0151
GEN-2022-155 | 04 SOUTHEAST | 514973 | RENO 4 | 138 | 29.306 | 29.4558 | 0.1498
GEN-2022-155 | 04 SOUTHEAST | 514974 | DEEPFRK2 | 69 | 6.6934 | 6.6974 | 0.004
GEN-2022-155 | 04 SOUTHEAST | 514979 | 44&SUNL2 | 69 | 12.0235 | 12.0317 | 0.0082
GEN-2022-155 | 04 SOUTHEAST | 514980 | SUNNYLN2 | 69 | 12.3361 | 12.3452 | 0.0091
GEN-2022-155 | 04 SOUTHEAST | 514981 | TINKER32 | 69 | 9.3121 | 9.3174 | 0.0053
GEN-2022-155 | 04 SOUTHEAST | 514983 | LTLRLKT2 | 69 | 2.9151 | 2.916 | 0.0009
GEN-2022-155 | 04 SOUTHEAST | 514985 | TXSTELA2 | 69 | 4.1014 | 4.1033 | 0.0019
GEN-2022-155 | 04 SOUTHEAST | 514986 | GLENDAL4 | 138 | 14.0751 | 14.1047 | 0.0296
GEN-2022-155 | 04 SOUTHEAST | 514987 | DALE 4 | 138 | 14.6369 | 14.6981 | 0.0612
GEN-2022-155 | 04 SOUTHEAST | 514989 | TXPLSTE2 | 69 | 3.1549 | 3.156 | 0.0011
GEN-2022-155 | 04 SOUTHEAST | 514993 | SE15TH 4 | 138 | 16.1568 | 16.1982 | 0.0414
GEN-2022-155 | 04 SOUTHEAST | 514994 | TINKER54 | 138 | 14.7309 | 14.76 | 0.0291
GEN-2022-155 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 17.0162 | 17.0533 | 0.0371
GEN-2022-155 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 42.4558 | 42.4768 | 0.021
GEN-2022-155 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.8702 | 29.8897 | 0.0195
GEN-2022-155 | 04 SOUTHEAST | 515046 | HAMMTAP4 | 138 | 17.6072 | 17.7105 | 0.1033
GEN-2022-155 | 04 SOUTHEAST | 515047 | WARWICK4 | 138 | 10.6902 | 10.7034 | 0.0132
GEN-2022-155 | 04 SOUTHEAST | 515051 | JACKTWN4 | 138 | 10.1955 | 10.2166 | 0.0211
GEN-2022-155 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 21.7995 | 21.817 | 0.0175
GEN-2022-155 | 04 SOUTHEAST | 515056 | WOLVERN4 | 138 | 8.8474 | 8.8623 | 0.0149
GEN-2022-155 | 04 SOUTHEAST | 515057 | MOBIL 4 | 138 | 8.9262 | 8.9413 | 0.0151
GEN-2022-155 | 04 SOUTHEAST | 515059 | SQUIRCK4 | 138 | 14.7778 | 14.8166 | 0.0388
GEN-2022-155 | 04 SOUTHEAST | 515060 | INGLEWD4 | 138 | 10.8175 | 10.8386 | 0.0211
GEN-2022-155 | 04 SOUTHEAST | 515061 | STGREG 4 | 138 | 9.5949 | 9.6116 | 0.0167
GEN-2022-155 | 04 SOUTHEAST | 515062 | NE45TAP4 | 138 | 9.2811 | 9.297 | 0.0159
GEN-2022-155 | 04 SOUTHEAST | 515065 | MCLOUD 2 | 69 | 5.0931 | 5.0965 | 0.0034
GEN-2022-155 | 04 SOUTHEAST | 515068 | SHAWNEE2 | 69 | 8.4181 | 8.4235 | 0.0054
GEN-2022-155 | 04 SOUTHEAST | 515072 | SINCPAN2 | 69 | 6.0938 | 6.0971 | 0.0033
GEN-2022-155 | 04 SOUTHEAST | 515074 | FRSTHIL2 | 69 | 11.863 | 11.8712 | 0.0082
GEN-2022-155 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 14.7037 | 14.7322 | 0.0285
GEN-2022-155 | 04 SOUTHEAST | 515156 | WASHPRK4 | 138 | 22.3637 | 22.4325 | 0.0688
GEN-2022-155 | 04 SOUTHEAST | 515286 | STRLGTP4 | 138 | 14.6199 | 14.6546 | 0.0347
GEN-2022-155 | 04 SOUTHEAST | 515366 | WFROSST4 | 138 | 12.8279 | 12.857 | 0.0291
GEN-2022-155 | 04 SOUTHEAST | 515369 | BELLCOW4 | 138 | 6.8593 | 6.8632 | 0.0039
GEN-2022-155 | 04 SOUTHEAST | 515373 | LBRTYLK4 | 138 | 14.893 | 14.901 | 0.008
GEN-2022-155 | 04 SOUTHEAST | 515377 | CRESENT4 | 138 | 11.0495 | 11.0512 | 0.0017
GEN-2022-155 | 04 SOUTHEAST | 515387 | NEWDOMI4 | 138 | 27.8981 | 27.9732 | 0.0751
GEN-2022-155 | 04 SOUTHEAST | 515442 | LINCOLN4 | 138 | 15.6727 | 15.7249 | 0.0522
GEN-2022-155 | 04 SOUTHEAST | 515457 | AIRDEPT4 | 138 | 21.2554 | 21.2763 | 0.0209
GEN-2022-155 | 04 SOUTHEAST | 515459 | ACORN 4 | 138 | 27.7217 | 27.855 | 0.1333
GEN-2022-155 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 41.0786 | 41.1792 | 0.1006
GEN-2022-155 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 22.1528 | 22.206 | 0.0532
GEN-2022-155 | 04 SOUTHEAST | 515480 | JONESSB4 | 138 | 30.2743 | 30.5066 | 0.2323
GEN-2022-155 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 35.0184 | 35.0446 | 0.0262
GEN-2022-155 | 04 SOUTHEAST | 515502 | LITLAXT2 | 69 | 3.4915 | 3.4925 | 0.001
GEN-2022-155 | 04 SOUTHEAST | 515504 | MCLOUDT2 | 69 | 5.1173 | 5.1208 | 0.0035
GEN-2022-155 | 04 SOUTHEAST | 515516 | TXPLSTP2 | 69 | 3.1589 | 3.16 | 0.0011
GEN-2022-155 | 04 SOUTHEAST | 515532 | WOLVRNT4 | 138 | 8.9218 | 8.9369 | 0.0151
GEN-2022-155 | 04 SOUTHEAST | 515642 | SINCPNT2 | 69 | 6.1288 | 6.1321 | 0.0033
GEN-2022-155 | 04 SOUTHEAST | 515675 | TRYON 4 | 138 | 9.2146 | 9.2189 | 0.0043
GEN-2022-155 | 04 SOUTHEAST | 515806 | TINKER64 | 138 | 14.2495 | 14.2772 | 0.0277
GEN-2022-155 | 04 SOUTHEAST | 515851 | CROSTWN4 | 138 | 26.6742 | 26.7316 | 0.0574
GEN-2022-155 | 04 SOUTHEAST | 515959 | TINKER74 | 138 | 13.7311 | 13.7582 | 0.0271
GEN-2022-155 | 04 SOUTHEAST | 515963 | GATEWAY4 | 138 | 22.1265 | 22.1863 | 0.0598
GEN-2022-155 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 28.1225 | 28.1509 | 0.0284
GEN-2022-155 | 04 SOUTHEAST | 520449 | STERLNG4 | 138 | 11.85 | 11.8729 | 0.0229
GEN-2022-155 | 04 SOUTHEAST | 520464 | MEEKER 4 | 138 | 9.349 | 9.3616 | 0.0126
GEN-2022-155 | 04 SOUTHEAST | 520526 | GRDGVTP4 | 138 | 7.2834 | 7.289 | 0.0056
GEN-2022-155 | 04 SOUTHEAST | 520917 | FRNKLNS4 | 138 | 31.0614 | 31.0876 | 0.0262
GEN-2022-155 | 04 SOUTHEAST | 520951 | HAMMETT4 | 138 | 13.1103 | 13.1677 | 0.0574
GEN-2022-155 | 04 SOUTHEAST | 520994 | MEEKRSW4 | 138 | 8.5915 | 8.6 | 0.0085
GEN-2022-155 | 04 SOUTHEAST | 521006 | MARSHAL4 | 138 | 8.3539 | 8.3546 | 0.0007
GEN-2022-155 | 04 SOUTHEAST | 521073 | TWNLKSW4 | 138 | 10.2893 | 10.2906 | 0.0013
GEN-2022-155 | 04 SOUTHEAST | 521097 | WREDHIL4 | 138 | 7.4719 | 7.4776 | 0.0057
GEN-2022-155 | 04 SOUTHEAST | 521107 | RSSVILE4 | 138 | 12.8279 | 12.857 | 0.0291
GEN-2022-155 | 04 SOUTHEAST | 587210 | GEN-2016-032 | 138 | 8.1283 | 8.129 | 0.0007
GEN-2022-155 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 19.0621 | 19.0634 | 0.0013
GEN-2022-155 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 4.9604 | 4.9611 | 0.0007
GEN-2022-155 | 04 SOUTHEAST | 762647 | GEN-2018-029 | 138 | 43.7696 | 44.776 | 1.0064
GEN-2022-155 | 04 SOUTHEAST | 770081 | GEN-2022-155 | 138 | 39.1304 | 40.1417 | 1.0113
GEN-2022-156 | 04 SOUTHEAST | 300131 | 4FISHERTP | 138 | 15.9521 | 16.0498 | 0.0977
GEN-2022-156 | 04 SOUTHEAST | 300137 | 4BRISTOW | 138 | 10.8362 | 10.8715 | 0.0353
GEN-2022-156 | 04 SOUTHEAST | 300138 | 4CLEVLND | 138 | 18.0231 | 18.0741 | 0.051
GEN-2022-156 | 04 SOUTHEAST | 300139 | 4FAIRFAX | 138 | 8.6036 | 8.607 | 0.0034
GEN-2022-156 | 04 SOUTHEAST | 300140 | 4SILVCTY | 138 | 18.1163 | 18.6133 | 0.497
GEN-2022-156 | 04 SOUTHEAST | 300141 | 4STILWTR | 138 | 19.7699 | 19.8039 | 0.034
GEN-2022-156 | 04 SOUTHEAST | 300143 | 4VALLEY | 138 | 8.3187 | 8.3222 | 0.0035
GEN-2022-156 | 04 SOUTHEAST | 300145 | 4FISHER | 138 | 13.4175 | 13.4869 | 0.0694
GEN-2022-156 | 04 SOUTHEAST | 300146 | 4SKIAETP | 138 | 7.2947 | 7.297 | 0.0023
GEN-2022-156 | 04 SOUTHEAST | 300165 | 4SFORKK | 138 | 4.6355 | 4.6365 | 0.001
GEN-2022-156 | 04 SOUTHEAST | 300196 | 2WOODY | 69 | 5.0271 | 5.0285 | 0.0014
GEN-2022-156 | 04 SOUTHEAST | 300686 | 4WOODY | 138 | 8.5059 | 8.5124 | 0.0065
GEN-2022-156 | 04 SOUTHEAST | 300841 | 2ORLANDO | 69 | 3.2502 | 3.2506 | 0.0004
GEN-2022-156 | 04 SOUTHEAST | 300843 | 2PERRYKM | 69 | 3.959 | 3.9596 | 0.0006
GEN-2022-156 | 04 SOUTHEAST | 300844 | 4RAMSEY | 138 | 12.512 | 12.5199 | 0.0079
GEN-2022-156 | 04 SOUTHEAST | 300850 | 2VALLEY | 69 | 8.16 | 8.1618 | 0.0018
GEN-2022-156 | 04 SOUTHEAST | 300889 | 2BRIISTOW | 69 | 11.1538 | 11.1706 | 0.0168
GEN-2022-156 | 04 SOUTHEAST | 300897 | 2GLENPOL | 69 | 3.6171 | 3.6184 | 0.0013
GEN-2022-156 | 04 SOUTHEAST | 300898 | 2GYPSY | 69 | 4.6341 | 4.6359 | 0.0018
GEN-2022-156 | 04 SOUTHEAST | 300901 | 2KELYVIL | 69 | 6.0002 | 6.0057 | 0.0055
GEN-2022-156 | 04 SOUTHEAST | 300906 | 2NUYAKA | 69 | 4.0695 | 4.0707 | 0.0012
GEN-2022-156 | 04 SOUTHEAST | 300907 | 2OKEMAH | 69 | 3.5368 | 3.5375 | 0.0007
GEN-2022-156 | 04 SOUTHEAST | 300920 | 2ALPINE | 69 | 6.2144 | 6.2224 | 0.008
GEN-2022-156 | 04 SOUTHEAST | 300923 | 2CEDARPT | 69 | 2.8332 | 2.8359 | 0.0027
GEN-2022-156 | 04 SOUTHEAST | 300927 | 2CLEVLND | 69 | 10.2926 | 10.3021 | 0.0095
GEN-2022-156 | 04 SOUTHEAST | 300928 | 2DIXIE | 69 | 5.7935 | 5.8009 | 0.0074
GEN-2022-156 | 04 SOUTHEAST | 300929 | 2FAIRFAX | 69 | 5.0629 | 5.0639 | 0.001
GEN-2022-156 | 04 SOUTHEAST | 300931 | 2FISHER | 69 | 7.8929 | 7.9071 | 0.0142
GEN-2022-156 | 04 SOUTHEAST | 300935 | 2HISSOM | 69 | 4.375 | 4.3793 | 0.0043
GEN-2022-156 | 04 SOUTHEAST | 300936 | 2MANFORD | 69 | 6.7626 | 6.7784 | 0.0158
GEN-2022-156 | 04 SOUTHEAST | 300943 | 2SILVCTY | 69 | 11.2727 | 11.325 | 0.0523
GEN-2022-156 | 04 SOUTHEAST | 300944 | 2SINNETT | 69 | 2.8383 | 2.8401 | 0.0018
GEN-2022-156 | 04 SOUTHEAST | 300945 | 2YALE | 69 | 5.5069 | 5.5142 | 0.0073
GEN-2022-156 | 04 SOUTHEAST | 300977 | 2BRISTOWTP | 69 | 9.8785 | 9.8918 | 0.0133
GEN-2022-156 | 04 SOUTHEAST | 300996 | 4JAVINE | 138 | 6.9185 | 6.9212 | 0.0027
GEN-2022-156 | 04 SOUTHEAST | 301339 | 4SFORKKTP | 138 | 7.223 | 7.2255 | 0.0025
GEN-2022-156 | 04 SOUTHEAST | 301369 | 4REMNGTON | 138 | 9.1954 | 9.1976 | 0.0022
GEN-2022-156 | 04 SOUTHEAST | 301410 | 2STROUD138 | 69 | 5.8493 | 5.8508 | 0.0015
GEN-2022-156 | 04 SOUTHEAST | 301413 | 2STILWTRKAMO | 69 | 15.4532 | 15.464 | 0.0108
GEN-2022-156 | 04 SOUTHEAST | 301433 | 2CIMARRON | 69 | 4.4386 | 4.4395 | 0.0009
GEN-2022-156 | 04 SOUTHEAST | 301546 | 4RAMSEYCP | 138 | 12.4764 | 12.4843 | 0.0079
GEN-2022-156 | 04 SOUTHEAST | 301553 | 4WELEETKA | 138 | 16.1859 | 16.1904 | 0.0045
GEN-2022-156 | 04 SOUTHEAST | 505609 | KEYSTON5 | 161 | 7.4579 | 7.4699 | 0.012
GEN-2022-156 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 23.8186 | 23.9308 | 0.1122
GEN-2022-156 | 04 SOUTHEAST | 509714 | CIP 4 | 138 | 14.1108 | 14.1135 | 0.0027
GEN-2022-156 | 04 SOUTHEAST | 509724 | 36&OLY-4 | 138 | 33.9207 | 33.9409 | 0.0202
GEN-2022-156 | 04 SOUTHEAST | 509726 | OWASO1_4 | 138 | 14.5669 | 14.5692 | 0.0023
GEN-2022-156 | 04 SOUTHEAST | 509739 | CARSN-T4 | 138 | 33.3692 | 33.3891 | 0.0199
GEN-2022-156 | 04 SOUTHEAST | 509740 | UNIONAV4 | 138 | 21.5842 | 21.5925 | 0.0083
GEN-2022-156 | 04 SOUTHEAST | 509741 | CARSN-N4 | 138 | 9.6604 | 9.6672 | 0.0068
GEN-2022-156 | 04 SOUTHEAST | 509743 | DENVR-E4 | 138 | 8.3262 | 8.3273 | 0.0011
GEN-2022-156 | 04 SOUTHEAST | 509746 | DENVTAP4 | 138 | 9.7659 | 9.7675 | 0.0016
GEN-2022-156 | 04 SOUTHEAST | 509748 | DENVR-W4 | 138 | 9.9313 | 9.9363 | 0.005
GEN-2022-156 | 04 SOUTHEAST | 509754 | WHORSE-4 | 138 | 4.0953 | 4.0962 | 0.0009
GEN-2022-156 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.3236 | 23.3598 | 0.0362
GEN-2022-156 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 34.1531 | 34.3126 | 0.1595
GEN-2022-156 | 04 SOUTHEAST | 509758 | PRATTV-4 | 138 | 21.2212 | 21.2403 | 0.0191
GEN-2022-156 | 04 SOUTHEAST | 509759 | JENKS--4 | 138 | 26.4069 | 26.4154 | 0.0085
GEN-2022-156 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 52.5899 | 52.6125 | 0.0226
GEN-2022-156 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.428 | 33.447 | 0.019
GEN-2022-156 | 04 SOUTHEAST | 509784 | A.A.---4 | 138 | 17.4661 | 17.4697 | 0.0036
GEN-2022-156 | 04 SOUTHEAST | 509796 | DX----W2 | 69 | 3.8531 | 3.8535 | 0.0004
GEN-2022-156 | 04 SOUTHEAST | 509805 | PP----W4 | 138 | 8.7274 | 8.7326 | 0.0052
GEN-2022-156 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 30.3466 | 30.3563 | 0.0097
GEN-2022-156 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 26.9397 | 26.9815 | 0.0418
GEN-2022-156 | 04 SOUTHEAST | 509815 | S.S.---4 | 138 | 29.7925 | 29.8376 | 0.0451
GEN-2022-156 | 04 SOUTHEAST | 509816 | S.S.---2 | 69 | 6.4331 | 6.4341 | 0.001
GEN-2022-156 | 04 SOUTHEAST | 509817 | T.NO.--4 | 138 | 36.1952 | 36.2165 | 0.0213
GEN-2022-156 | 04 SOUTHEAST | 509821 | HWY20-T4 | 138 | 4.1043 | 4.1052 | 0.0009
GEN-2022-156 | 04 SOUTHEAST | 509822 | W.ED.-E4 | 138 | 8.1601 | 8.1612 | 0.0011
GEN-2022-156 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 19.9321 | 19.9607 | 0.0286
GEN-2022-156 | 04 SOUTHEAST | 509832 | W.ED.-W4 | 138 | 12.0107 | 12.0212 | 0.0105
GEN-2022-156 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 31.0007 | 31.0168 | 0.0161
GEN-2022-156 | 04 SOUTHEAST | 509837 | 46ST--E4 | 138 | 3.0619 | 3.0621 | 0.0002
GEN-2022-156 | 04 SOUTHEAST | 509839 | CDC-ET 4 | 138 | 19.5846 | 19.59 | 0.0054
GEN-2022-156 | 04 SOUTHEAST | 509840 | WHIRLPO4 | 138 | 19.2305 | 19.2358 | 0.0053
GEN-2022-156 | 04 SOUTHEAST | 509842 | CDC-WT 4 | 138 | 20.3114 | 20.3174 | 0.006
GEN-2022-156 | 04 SOUTHEAST | 509843 | OWASO2_4 | 138 | 14.6075 | 14.6088 | 0.0013
GEN-2022-156 | 04 SOUTHEAST | 509844 | OWASOTP4 | 138 | 15.6714 | 15.674 | 0.0026
GEN-2022-156 | 04 SOUTHEAST | 509848 | OAKSWTP4 | 138 | 25.7558 | 25.7664 | 0.0106
GEN-2022-156 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 15.8472 | 15.8642 | 0.017
GEN-2022-156 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.6191 | 24.6425 | 0.0234
GEN-2022-156 | 04 SOUTHEAST | 509860 | OWAS1094 | 138 | 15.0637 | 15.0658 | 0.0021
GEN-2022-156 | 04 SOUTHEAST | 509863 | PPTAP 4 | 138 | 10.8437 | 10.8452 | 0.0015
GEN-2022-156 | 04 SOUTHEAST | 509864 | CLARTOK4 | 138 | 14.2995 | 14.3007 | 0.0012
GEN-2022-156 | 04 SOUTHEAST | 509865 | CARSONT4 | 138 | 12.4399 | 12.4511 | 0.0112
GEN-2022-156 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 23.7393 | 23.7592 | 0.0199
GEN-2022-156 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 34.2726 | 34.294 | 0.0214
GEN-2022-156 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 53.5278 | 53.5512 | 0.0234
GEN-2022-156 | 04 SOUTHEAST | 509884 | SKIATOK4 | 138 | 10.9655 | 10.9672 | 0.0017
GEN-2022-156 | 04 SOUTHEAST | 509887 | OWAS88_4 | 138 | 17.4449 | 17.4487 | 0.0038
GEN-2022-156 | 04 SOUTHEAST | 509888 | 72ELWOD4 | 138 | 24.1537 | 24.1631 | 0.0094
GEN-2022-156 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 36.1363 | 36.1575 | 0.0212
GEN-2022-156 | 04 SOUTHEAST | 509896 | DENV_WTAP4 | 138 | 29.0415 | 29.0837 | 0.0422
GEN-2022-156 | 04 SOUTHEAST | 509897 | WLDCT_HIL4 | 138 | 4.0962 | 4.0971 | 0.0009
GEN-2022-156 | 04 SOUTHEAST | 509900 | 46ST-TP-4 | 138 | 10.04 | 10.0413 | 0.0013
GEN-2022-156 | 04 SOUTHEAST | 510384 | WATOVA 4 | 138 | 9.4387 | 9.4391 | 0.0004
GEN-2022-156 | 04 SOUTHEAST | 510385 | RICE CK4 | 138 | 11.7439 | 11.7446 | 0.0007
GEN-2022-156 | 04 SOUTHEAST | 510388 | BARNSAL4 | 138 | 6.9462 | 6.9468 | 0.0006
GEN-2022-156 | 04 SOUTHEAST | 510396 | N.E.S.-4 | 138 | 36.9736 | 36.9788 | 0.0052
GEN-2022-156 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 17.5044 | 17.5099 | 0.0055
GEN-2022-156 | 04 SOUTHEAST | 510413 | HAWTHRN4 | 138 | 21.1141 | 21.1158 | 0.0017
GEN-2022-156 | 04 SOUTHEAST | 512641 | MANFORD2 | 69 | 4.235 | 4.2412 | 0.0062
GEN-2022-156 | 04 SOUTHEAST | 512664 | FERGUSN2 | 69 | 11.4911 | 11.4958 | 0.0047
GEN-2022-156 | 04 SOUTHEAST | 512674 | CUSH GR2 | 69 | 5.5128 | 5.5153 | 0.0025
GEN-2022-156 | 04 SOUTHEAST | 512675 | PAWNEGR2 | 69 | 3.5405 | 3.5414 | 0.0009
GEN-2022-156 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.7278 | 15.743 | 0.0152
GEN-2022-156 | 04 SOUTHEAST | 512710 | KINZEGR4 | 138 | 16.9242 | 16.9347 | 0.0105
GEN-2022-156 | 04 SOUTHEAST | 512712 | 19TH ST4 | 138 | 14.7499 | 14.7586 | 0.0087
GEN-2022-156 | 04 SOUTHEAST | 512713 | KINZEGR2 | 69 | 9.1982 | 9.2006 | 0.0024
GEN-2022-156 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 17.9045 | 18.4075 | 0.503
GEN-2022-156 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 18.0231 | 18.0741 | 0.051
GEN-2022-156 | 04 SOUTHEAST | 512731 | NORTHTP4 | 138 | 13.4499 | 13.4614 | 0.0115
GEN-2022-156 | 04 SOUTHEAST | 512732 | NORTHTP2 | 69 | 11.165 | 11.1692 | 0.0042
GEN-2022-156 | 04 SOUTHEAST | 512733 | INDUSTL2 | 69 | 9.0656 | 9.0683 | 0.0027
GEN-2022-156 | 04 SOUTHEAST | 512749 | PAWNSW4 | 138 | 11.3244 | 11.3359 | 0.0115
GEN-2022-156 | 04 SOUTHEAST | 512809 | STILLWTR2 | 69 | 15.35 | 15.3607 | 0.0107
GEN-2022-156 | 04 SOUTHEAST | 512875 | PRUEK2 | 69 | 4.5896 | 4.5912 | 0.0016
GEN-2022-156 | 04 SOUTHEAST | 512876 | OSAGEK2 | 69 | 7.4156 | 7.4215 | 0.0059
GEN-2022-156 | 04 SOUTHEAST | 512877 | CLEVDSTK2 | 69 | 6.7567 | 6.7627 | 0.006
GEN-2022-156 | 04 SOUTHEAST | 513089 | BALDHILLKM 2 | 69 | 3.1643 | 3.1647 | 0.0004
GEN-2022-156 | 04 SOUTHEAST | 513092 | BEGGS 2 | 69 | 5.3142 | 5.3165 | 0.0023
GEN-2022-156 | 04 SOUTHEAST | 513095 | GLENCOKM 4 | 138 | 12.4292 | 12.4427 | 0.0135
GEN-2022-156 | 04 SOUTHEAST | 513098 | HALLETTAP 2 | 69 | 4.2329 | 4.2348 | 0.0019
GEN-2022-156 | 04 SOUTHEAST | 513100 | CUSHING 2 | 69 | 7.3384 | 7.3429 | 0.0045
GEN-2022-156 | 04 SOUTHEAST | 513103 | KASTLEKM 2 | 69 | 7.4105 | 7.4138 | 0.0033
GEN-2022-156 | 04 SOUTHEAST | 513106 | STROUDTPKM 2 | 69 | 5.014 | 5.0156 | 0.0016
GEN-2022-156 | 04 SOUTHEAST | 513109 | SHAMROCKM 2 | 69 | 2.3793 | 2.3796 | 0.0003
GEN-2022-156 | 04 SOUTHEAST | 513112 | BRISTOSWKM 2 | 69 | 1.5795 | 1.5797 | 0.0002
GEN-2022-156 | 04 SOUTHEAST | 513115 | BRISTWKM 2 | 69 | 1.5795 | 1.5797 | 0.0002
GEN-2022-156 | 04 SOUTHEAST | 513118 | AGRAKM 2 | 69 | 4.8605 | 4.8619 | 0.0014
GEN-2022-156 | 04 SOUTHEAST | 513124 | OOLOGAHKM 4 | 138 | 21.4259 | 21.4278 | 0.0019
GEN-2022-156 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 21.2385 | 21.2409 | 0.0024
GEN-2022-156 | 04 SOUTHEAST | 514704 | MILLERT4 | 138 | 21.5371 | 21.5388 | 0.0017
GEN-2022-156 | 04 SOUTHEAST | 514707 | PERRY 4 | 138 | 11.5827 | 11.5835 | 0.0008
GEN-2022-156 | 04 SOUTHEAST | 514715 | WOODRNG7 | 345 | 19.6748 | 19.6762 | 0.0014
GEN-2022-156 | 04 SOUTHEAST | 514798 | SNRPMPT4 | 138 | 21.5888 | 21.5906 | 0.0018
GEN-2022-156 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 33.4037 | 33.4078 | 0.0041
GEN-2022-156 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 30.2626 | 30.2745 | 0.0119
GEN-2022-156 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.6383 | 24.6397 | 0.0014
GEN-2022-156 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.2566 | 27.258 | 0.0014
GEN-2022-156 | 04 SOUTHEAST | 515008 | KINZE 4 | 138 | 16.9424 | 16.9528 | 0.0104
GEN-2022-156 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 23.2646 | 23.2677 | 0.0031
GEN-2022-156 | 04 SOUTHEAST | 515242 | BLUEBEL4 | 138 | 17.8032 | 17.8103 | 0.0071
GEN-2022-156 | 04 SOUTHEAST | 515447 | MORISNT4 | 138 | 14.9859 | 14.9884 | 0.0025
GEN-2022-156 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 15.8353 | 15.8366 | 0.0013
GEN-2022-156 | 04 SOUTHEAST | 515621 | OPENSKY7 | 345 | 13.6647 | 13.6654 | 0.0007
GEN-2022-156 | 04 SOUTHEAST | 515688 | FRNTWND7 | 345 | 12.7261 | 12.7269 | 0.0008
GEN-2022-156 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 13.9596 | 13.9617 | 0.0021
GEN-2022-156 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.5429 | 17.5449 | 0.002
GEN-2022-156 | 04 SOUTHEAST | 516019 | KINGWD 7 | 345 | 17.482 | 17.484 | 0.002
GEN-2022-156 | 04 SOUTHEAST | 520886 | DUSTIN 4 | 138 | 8.4092 | 8.4103 | 0.0011
GEN-2022-156 | 04 SOUTHEAST | 521026 | PHAROAH4 | 138 | 15.8427 | 15.8473 | 0.0046
GEN-2022-156 | 04 SOUTHEAST | 521084 | WTMKATP4 | 138 | 8.6281 | 8.6291 | 0.001
GEN-2022-156 | 04 SOUTHEAST | 529200 | OMCDLEC7 | 345 | 15.8033 | 15.8045 | 0.0012
GEN-2022-156 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 20.2156 | 20.2248 | 0.0092
GEN-2022-156 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 34.1531 | 34.3126 | 0.1595
GEN-2022-156 | 04 SOUTHEAST | 585040 | GEN-2015-066 | 345 | 20.016 | 20.025 | 0.009
GEN-2022-156 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.9477 | 15.9494 | 0.0017
GEN-2022-156 | 04 SOUTHEAST | 587950 | GEN-2016-119 | 345 | 9.4085 | 9.409 | 0.0005
GEN-2022-156 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 33.428 | 33.447 | 0.019
GEN-2022-156 | 04 SOUTHEAST | 762636 | GEN-2018-028 | 138 | 29.773 | 29.7873 | 0.0143
GEN-2022-156 | 04 SOUTHEAST | 763069 | G18-071-TAP | 345 | 15.4042 | 15.4053 | 0.0011
GEN-2022-156 | 04 SOUTHEAST | 765470 | GEN-2021-018 | 345 | 7.7821 | 7.7827 | 0.0006
GEN-2022-156 | 04 SOUTHEAST | 765480 | GEN-2021-019 | 345 | 13.8022 | 13.8043 | 0.0021
GEN-2022-156 | 04 SOUTHEAST | 765720 | GEN-2021-047 | 345 | 16.3808 | 16.3833 | 0.0025
GEN-2022-156 | 04 SOUTHEAST | 765721 | G21-047-TAP | 345 | 16.7455 | 16.7482 | 0.0027
GEN-2022-156 | 04 SOUTHEAST | 770101 | GEN-2022-156 | 138 | 17.3864 | 17.8895 | 0.5031
GEN-2022-156 | 04 SOUTHEAST | 770500 | G22-176-TAP | 345 | 10.9314 | 10.9334 | 0.002
GEN-2022-176 | 04 SOUTHEAST | 300138 | 4CLEVLND | 138 | 18.0677 | 18.0741 | 0.0064
GEN-2022-176 | 04 SOUTHEAST | 505610 | KEYSTON4 | 138 | 23.9177 | 23.9308 | 0.0131
GEN-2022-176 | 04 SOUTHEAST | 506944 | CHAMSPR5 | 161 | 24.3154 | 24.318 | 0.0026
GEN-2022-176 | 04 SOUTHEAST | 506945 | CHAMSPR7 | 345 | 10.6445 | 10.646 | 0.0015
GEN-2022-176 | 04 SOUTHEAST | 506959 | TONTITN7 | 345 | 9.5902 | 9.5913 | 0.0011
GEN-2022-176 | 04 SOUTHEAST | 509721 | BA.NO-S4 | 138 | 12.6537 | 12.6584 | 0.0047
GEN-2022-176 | 04 SOUTHEAST | 509737 | BA101 S4 | 138 | 18.6429 | 18.6526 | 0.0097
GEN-2022-176 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 21.1327 | 21.1519 | 0.0192
GEN-2022-176 | 04 SOUTHEAST | 509746 | DENVTAP4 | 138 | 9.7633 | 9.7675 | 0.0042
GEN-2022-176 | 04 SOUTHEAST | 509747 | BA81---4 | 138 | 18.5957 | 18.605 | 0.0093
GEN-2022-176 | 04 SOUTHEAST | 509755 | WEKIWA-7 | 345 | 23.3134 | 23.3598 | 0.0464
GEN-2022-176 | 04 SOUTHEAST | 509757 | WEKIWA-4 | 138 | 34.2837 | 34.3126 | 0.0289
GEN-2022-176 | 04 SOUTHEAST | 509767 | B111---4 | 138 | 16.5212 | 16.5271 | 0.0059
GEN-2022-176 | 04 SOUTHEAST | 509768 | BA101ST4 | 138 | 19.3412 | 19.3516 | 0.0104
GEN-2022-176 | 04 SOUTHEAST | 509769 | BA101-N4 | 138 | 20.1776 | 20.1893 | 0.0117
GEN-2022-176 | 04 SOUTHEAST | 509773 | RSS T1 4 | 138 | 52.5753 | 52.6125 | 0.0372
GEN-2022-176 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.4008 | 33.447 | 0.0462
GEN-2022-176 | 04 SOUTHEAST | 509783 | R.S.S.-4 | 138 | 63.3859 | 63.438 | 0.0521
GEN-2022-176 | 04 SOUTHEAST | 509785 | BANNTAP4 | 138 | 19.2351 | 19.2442 | 0.0091
GEN-2022-176 | 04 SOUTHEAST | 509786 | BA.N-ST4 | 138 | 24.6031 | 24.6207 | 0.0176
GEN-2022-176 | 04 SOUTHEAST | 509804 | LLANETP4 | 138 | 28.2647 | 28.2816 | 0.0169
GEN-2022-176 | 04 SOUTHEAST | 509806 | ONETA--4 | 138 | 50.105 | 50.1915 | 0.0865
GEN-2022-176 | 04 SOUTHEAST | 509807 | ONETA--7 | 345 | 30.2625 | 30.3563 | 0.0938
GEN-2022-176 | 04 SOUTHEAST | 509812 | SHEFFD-4 | 138 | 26.9676 | 26.9815 | 0.0139
GEN-2022-176 | 04 SOUTHEAST | 509817 | T.NO.--4 | 138 | 36.1599 | 36.2165 | 0.0566
GEN-2022-176 | 04 SOUTHEAST | 509823 | WED-TAP4 | 138 | 19.9526 | 19.9607 | 0.0081
GEN-2022-176 | 04 SOUTHEAST | 509834 | COGENT 7 | 345 | 30.9777 | 31.0168 | 0.0391
GEN-2022-176 | 04 SOUTHEAST | 509836 | OEC 7 | 345 | 29.9751 | 30.0664 | 0.0913
GEN-2022-176 | 04 SOUTHEAST | 509839 | CDC-ET 4 | 138 | 19.576 | 19.59 | 0.014
GEN-2022-176 | 04 SOUTHEAST | 509842 | CDC-WT 4 | 138 | 20.3016 | 20.3174 | 0.0158
GEN-2022-176 | 04 SOUTHEAST | 509844 | OWASOTP4 | 138 | 15.6669 | 15.674 | 0.0071
GEN-2022-176 | 04 SOUTHEAST | 509851 | P&P WTP4 | 138 | 15.856 | 15.8642 | 0.0082
GEN-2022-176 | 04 SOUTHEAST | 509852 | T.NO.--7 | 345 | 24.5128 | 24.6425 | 0.1297
GEN-2022-176 | 04 SOUTHEAST | 509869 | 121LYNN4 | 138 | 18.258 | 18.2676 | 0.0096
GEN-2022-176 | 04 SOUTHEAST | 509870 | SAPLPRD7 | 345 | 23.7275 | 23.7592 | 0.0317
GEN-2022-176 | 04 SOUTHEAST | 509871 | SAPLPRD4 | 138 | 34.274 | 34.294 | 0.02
GEN-2022-176 | 04 SOUTHEAST | 509875 | RSS T2 4 | 138 | 53.5128 | 53.5512 | 0.0384
GEN-2022-176 | 04 SOUTHEAST | 509884 | SKIATOK4 | 138 | 10.9624 | 10.9672 | 0.0048
GEN-2022-176 | 04 SOUTHEAST | 509889 | E_121ST4 | 138 | 16.333 | 16.3398 | 0.0068
GEN-2022-176 | 04 SOUTHEAST | 509891 | BA_71ST4 | 138 | 23.8918 | 23.9093 | 0.0175
GEN-2022-176 | 04 SOUTHEAST | 509895 | T.NO.2-4 | 138 | 36.1002 | 36.1575 | 0.0573
GEN-2022-176 | 04 SOUTHEAST | 509900 | 46ST-TP-4 | 138 | 10.0379 | 10.0413 | 0.0034
GEN-2022-176 | 04 SOUTHEAST | 510378 | SCOFCTY4 | 138 | 8.9249 | 8.9362 | 0.0113
GEN-2022-176 | 04 SOUTHEAST | 510379 | DELWARE4 | 138 | 10.3636 | 10.4541 | 0.0905
GEN-2022-176 | 04 SOUTHEAST | 510380 | DELWARE7 | 345 | 7.7369 | 7.9306 | 0.1937
GEN-2022-176 | 04 SOUTHEAST | 510396 | N.E.S.-4 | 138 | 36.9636 | 36.9788 | 0.0152
GEN-2022-176 | 04 SOUTHEAST | 510406 | N.E.S.-7 | 345 | 17.1469 | 17.5099 | 0.363
GEN-2022-176 | 04 SOUTHEAST | 512694 | CLEVLND7 | 345 | 15.7224 | 15.743 | 0.0206
GEN-2022-176 | 04 SOUTHEAST | 512726 | SILVCTYGR4 | 138 | 18.4029 | 18.4075 | 0.0046
GEN-2022-176 | 04 SOUTHEAST | 512729 | CLEVLND 4 | 138 | 18.0676 | 18.0741 | 0.0065
GEN-2022-176 | 04 SOUTHEAST | 512734 | FARML 4 | 138 | 8.5217 | 8.5393 | 0.0176
GEN-2022-176 | 04 SOUTHEAST | 512735 | COFCTY2 | 69 | 9.2382 | 9.2448 | 0.0066
GEN-2022-176 | 04 SOUTHEAST | 512865 | GREC TAP5 | 345 | 26.6911 | 26.702 | 0.0109
GEN-2022-176 | 04 SOUTHEAST | 513593 | IGLOOV1 5 | 161 | 17.7318 | 17.7353 | 0.0035
GEN-2022-176 | 04 SOUTHEAST | 513595 | IGLOOV2 5 | 161 | 17.7318 | 17.7353 | 0.0035
GEN-2022-176 | 04 SOUTHEAST | 513596 | IGLOOV 7 | 345 | 21.23 | 21.2409 | 0.0109
GEN-2022-176 | 04 SOUTHEAST | 514802 | SOONER 4 | 138 | 33.4056 | 33.4078 | 0.0022
GEN-2022-176 | 04 SOUTHEAST | 514803 | SOONER 7 | 345 | 30.2604 | 30.2745 | 0.0141
GEN-2022-176 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.2149 | 28.2163 | 0.0014
GEN-2022-176 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.2566 | 27.258 | 0.0014
GEN-2022-176 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 28.7798 | 28.7923 | 0.0125
GEN-2022-176 | 04 SOUTHEAST | 515234 | PECANCK5 | 161 | 22.3081 | 22.312 | 0.0039
GEN-2022-176 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 23.258 | 23.2677 | 0.0097
GEN-2022-176 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.6071 | 10.6074 | 0.0003
GEN-2022-176 | 04 SOUTHEAST | 515576 | RANCHRD7 | 345 | 15.835 | 15.8366 | 0.0016
GEN-2022-176 | 04 SOUTHEAST | 515894 | THUNDER7 | 345 | 13.9592 | 13.9617 | 0.0025
GEN-2022-176 | 04 SOUTHEAST | 516010 | PINTAIL7 | 345 | 17.5426 | 17.5449 | 0.0023
GEN-2022-176 | 04 SOUTHEAST | 516091 | OKTAHA 7 | 345 | 17.1443 | 17.1475 | 0.0032
GEN-2022-176 | 04 SOUTHEAST | 560056 | G15-066T | 345 | 20.2132 | 20.2248 | 0.0116
GEN-2022-176 | 04 SOUTHEAST | 560389 | GEN-2010-055 | 138 | 34.2837 | 34.3126 | 0.0289
GEN-2022-176 | 04 SOUTHEAST | 585040 | GEN-2015-066 | 345 | 20.0137 | 20.025 | 0.0113
GEN-2022-176 | 04 SOUTHEAST | 587804 | G16-119-TAP | 345 | 15.9474 | 15.9494 | 0.002
GEN-2022-176 | 04 SOUTHEAST | 588039 | G16133G16146 | 345 | 33.4008 | 33.447 | 0.0462
GEN-2022-176 | 04 SOUTHEAST | 588040 | G16133_345GS | 345 | 18.2619 | 18.2741 | 0.0122
GEN-2022-176 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 19.06 | 19.0634 | 0.0034
GEN-2022-176 | 04 SOUTHEAST | 760389 | GEN-2017-140 | 345 | 1.8998 | 1.8999 | 0.0001
GEN-2022-176 | 04 SOUTHEAST | 760393 | G17-140-BUS | 345 | 1.887 | 1.887 | 0
GEN-2022-176 | 04 SOUTHEAST | 762636 | GEN-2018-028 | 138 | 29.7485 | 29.7873 | 0.0388
GEN-2022-176 | 04 SOUTHEAST | 762823 | GEN-2018-048 | 345 | 17.0724 | 17.0773 | 0.0049
GEN-2022-176 | 04 SOUTHEAST | 763109 | GEN-2018-079 | 138 | 6.8893 | 6.9174 | 0.0281
GEN-2022-176 | 04 SOUTHEAST | 763113 | G18-079-TAP | 138 | 9.2282 | 9.282 | 0.0538
GEN-2022-176 | 04 SOUTHEAST | 765720 | GEN-2021-047 | 345 | 16.3709 | 16.3833 | 0.0124
GEN-2022-176 | 04 SOUTHEAST | 765721 | G21-047-TAP | 345 | 16.7352 | 16.7482 | 0.013
GEN-2022-176 | 04 SOUTHEAST | 770500 | G22-176-TAP | 345 | 10.536 | 10.9334 | 0.3974
GEN-2022-176 | 04 SOUTHEAST | 770501 | GEN-2022-176 | 345 | 10.5138 | 10.9112 | 0.3974
GEN-2022-235 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.6243 | 10.6309 | 0.0066
GEN-2022-235 | 04 SOUTHEAST | 511433 | HINTON 4 | 138 | 6.534 | 6.5692 | 0.0352
GEN-2022-235 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 10.4411 | 10.4472 | 0.0061
GEN-2022-235 | 04 SOUTHEAST | 511540 | CAN_GAS4 | 138 | 9.8383 | 9.9695 | 0.1312
GEN-2022-235 | 04 SOUTHEAST | 511548 | REDROCKRD4 | 138 | 9.6103 | 9.7291 | 0.1188
GEN-2022-235 | 04 SOUTHEAST | 511559 | DARLINGTNRD4 | 138 | 7.2851 | 7.3424 | 0.0573
GEN-2022-235 | 04 SOUTHEAST | 511576 | CEMRD_TP4 | 138 | 7.063 | 7.0659 | 0.0029
GEN-2022-235 | 04 SOUTHEAST | 511581 | MAPLERD4 | 138 | 7.0015 | 7.0527 | 0.0512
GEN-2022-235 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 24.1792 | 24.1967 | 0.0175
GEN-2022-235 | 04 SOUTHEAST | 514817 | SVCELRN2 | 69 | 6.7656 | 6.7698 | 0.0042
GEN-2022-235 | 04 SOUTHEAST | 514818 | ELRENO 2 | 69 | 7.7731 | 7.7801 | 0.007
GEN-2022-235 | 04 SOUTHEAST | 514819 | EL-RENO4 | 138 | 17.698 | 17.8519 | 0.1539
GEN-2022-235 | 04 SOUTHEAST | 514820 | JENSENT4 | 138 | 19.2419 | 19.5845 | 0.3426
GEN-2022-235 | 04 SOUTHEAST | 514821 | JENSEN 4 | 138 | 16.4022 | 16.9859 | 0.5837
GEN-2022-235 | 04 SOUTHEAST | 514823 | ROMNOSE4 | 138 | 6.3756 | 6.3971 | 0.0215
GEN-2022-235 | 04 SOUTHEAST | 514853 | DVISION4 | 138 | 38.3335 | 38.3789 | 0.0454
GEN-2022-235 | 04 SOUTHEAST | 514863 | HAYMAKR4 | 138 | 28.0342 | 28.0773 | 0.0431
GEN-2022-235 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.0916 | 35.126 | 0.0344
GEN-2022-235 | 04 SOUTHEAST | 514893 | XEROX 4 | 138 | 31.6661 | 31.71 | 0.0439
GEN-2022-235 | 04 SOUTHEAST | 514894 | CZECHAL4 | 138 | 30.2286 | 30.2753 | 0.0467
GEN-2022-235 | 04 SOUTHEAST | 514895 | SARA 4 | 138 | 20.2239 | 20.2473 | 0.0234
GEN-2022-235 | 04 SOUTHEAST | 514898 | CIMARON4 | 138 | 47.039 | 47.2649 | 0.2259
GEN-2022-235 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 37.6454 | 37.7045 | 0.0591
GEN-2022-235 | 04 SOUTHEAST | 514902 | MCCLAIN4 | 138 | 33.5796 | 33.6032 | 0.0236
GEN-2022-235 | 04 SOUTHEAST | 515314 | REDCORN4 | 138 | 8.868 | 8.9403 | 0.0723
GEN-2022-235 | 04 SOUTHEAST | 515460 | TALBEAR4 | 138 | 8.6224 | 8.7231 | 0.1007
GEN-2022-235 | 04 SOUTHEAST | 515472 | TLBEART4 | 138 | 9.7775 | 9.9071 | 0.1296
GEN-2022-235 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 35.0083 | 35.0446 | 0.0363
GEN-2022-235 | 04 SOUTHEAST | 515506 | OKRCHET2 | 69 | 3.8681 | 3.8696 | 0.0015
GEN-2022-235 | 04 SOUTHEAST | 515610 | FSHRTAP7 | 345 | 18.8364 | 18.8486 | 0.0122
GEN-2022-235 | 04 SOUTHEAST | 515962 | OMEGA 4 | 138 | 6.1468 | 6.1666 | 0.0198
GEN-2022-235 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 28.1244 | 28.1509 | 0.0265
GEN-2022-235 | 04 SOUTHEAST | 520401 | BAILEY4 | 138 | 10.7735 | 10.7974 | 0.0239
GEN-2022-235 | 04 SOUTHEAST | 520412 | MUSTANG4 | 138 | 7.5414 | 7.6025 | 0.0611
GEN-2022-235 | 04 SOUTHEAST | 520501 | BRIDGCR4 | 138 | 9.092 | 9.1141 | 0.0221
GEN-2022-235 | 04 SOUTHEAST | 520502 | CANA 4 | 138 | 10.4429 | 10.6006 | 0.1577
GEN-2022-235 | 04 SOUTHEAST | 520508 | CLVLDSW4 | 138 | 13.2665 | 13.3069 | 0.0404
GEN-2022-235 | 04 SOUTHEAST | 520530 | AMBERTP4 | 138 | 8.6404 | 8.6501 | 0.0097
GEN-2022-235 | 04 SOUTHEAST | 520533 | KGFSHSW4 | 138 | 8.8511 | 8.874 | 0.0229
GEN-2022-235 | 04 SOUTHEAST | 520536 | WATNGSW4 | 138 | 7.2824 | 7.3034 | 0.021
GEN-2022-235 | 04 SOUTHEAST | 520552 | REDCNTP4 | 138 | 9.5628 | 9.6469 | 0.0841
GEN-2022-235 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 37.431 | 37.4742 | 0.0432
GEN-2022-235 | 04 SOUTHEAST | 520839 | CALUMET4 | 138 | 8.8097 | 8.8713 | 0.0616
GEN-2022-235 | 04 SOUTHEAST | 520859 | COGAR 4 | 138 | 9.5378 | 9.6151 | 0.0773
GEN-2022-235 | 04 SOUTHEAST | 520865 | CONCHO 4 | 138 | 7.4092 | 7.4359 | 0.0267
GEN-2022-235 | 04 SOUTHEAST | 520893 | EL RENO4 | 138 | 15.0869 | 15.8379 | 0.751
GEN-2022-235 | 04 SOUTHEAST | 520899 | SCOTTSW4 | 138 | 12.3133 | 12.5783 | 0.265
GEN-2022-235 | 04 SOUTHEAST | 520964 | OMEGA 4 | 138 | 6.2785 | 6.2929 | 0.0144
GEN-2022-235 | 04 SOUTHEAST | 521005 | SARA RD4 | 138 | 7.6312 | 7.6851 | 0.0539
GEN-2022-235 | 04 SOUTHEAST | 521016 | OKEENE 4 | 138 | 7.3455 | 7.3557 | 0.0102
GEN-2022-235 | 04 SOUTHEAST | 521059 | SUNSHIN4 | 138 | 10.3155 | 10.3496 | 0.0341
GEN-2022-235 | 04 SOUTHEAST | 521072 | TUTLETP4 | 138 | 8.3753 | 8.3877 | 0.0124
GEN-2022-235 | 04 SOUTHEAST | 521091 | WATONGA4 | 138 | 4.6322 | 4.6406 | 0.0084
GEN-2022-235 | 04 SOUTHEAST | 521123 | WMOORE 4 | 138 | 12.437 | 12.4575 | 0.0205
GEN-2022-235 | 04 SOUTHEAST | 588720 | GEN-2017-117 | 138 | 15.0869 | 15.8379 | 0.751
GEN-2022-235 | 04 SOUTHEAST | 769880 | G22-145-TAP | 138 | 6.2742 | 6.2864 | 0.0122
GEN-2022-235 | 04 SOUTHEAST | 771681 | GEN-2022-235 | 138 | 15.0869 | 15.8379 | 0.751
GEN-2022-238 | 04 SOUTHEAST | 301551 | 4CHECOTA | 138 | 6.4779 | 6.4784 | 0.0005
GEN-2022-238 | 04 SOUTHEAST | 301553 | 4WELEETKA | 138 | 16.1775 | 16.1904 | 0.0129
GEN-2022-238 | 04 SOUTHEAST | 505590 | WELEETK5 | 161 | 6.6858 | 6.6877 | 0.0019
GEN-2022-238 | 04 SOUTHEAST | 505592 | WELEETK4 | 138 | 16.1988 | 16.2118 | 0.013
GEN-2022-238 | 04 SOUTHEAST | 505595 | GREASYC4 | 138 | 7.4186 | 7.4212 | 0.0026
GEN-2022-238 | 04 SOUTHEAST | 508298 | LYDIA 7 | 345 | 14.0046 | 14.005 | 0.0004
GEN-2022-238 | 04 SOUTHEAST | 509745 | CLARKSV7 | 345 | 21.151 | 21.1519 | 0.0009
GEN-2022-238 | 04 SOUTHEAST | 509782 | R.S.S.-7 | 345 | 33.4446 | 33.447 | 0.0024
GEN-2022-238 | 04 SOUTHEAST | 510871 | OKEMAH 2 | 69 | 2.7144 | 2.7147 | 0.0003
GEN-2022-238 | 04 SOUTHEAST | 510877 | FIXCT4 | 138 | 8.3509 | 8.4073 | 0.0564
GEN-2022-238 | 04 SOUTHEAST | 510883 | WETUMTP2 | 69 | 5.4069 | 5.4096 | 0.0027
GEN-2022-238 | 04 SOUTHEAST | 510892 | HENRYET4 | 138 | 9.0198 | 9.0231 | 0.0033
GEN-2022-238 | 04 SOUTHEAST | 510898 | OKMULGE4 | 138 | 11.941 | 11.9442 | 0.0032
GEN-2022-238 | 04 SOUTHEAST | 510902 | WELETK4 | 138 | 15.7929 | 15.8091 | 0.0162
GEN-2022-238 | 04 SOUTHEAST | 510903 | WELEETK2 | 69 | 10.6037 | 10.6091 | 0.0054
GEN-2022-238 | 04 SOUTHEAST | 510907 | PITTSB-7 | 345 | 15.3663 | 15.3733 | 0.007
GEN-2022-238 | 04 SOUTHEAST | 510908 | MCALEST4 | 138 | 10.4259 | 10.4282 | 0.0023
GEN-2022-238 | 04 SOUTHEAST | 510911 | VALIANT7 | 345 | 14.3178 | 14.3192 | 0.0014
GEN-2022-238 | 04 SOUTHEAST | 510918 | VALIANT4 | 138 | 15.427 | 15.4277 | 0.0007
GEN-2022-238 | 04 SOUTHEAST | 510921 | DUSTIN-4 | 138 | 9.2744 | 9.279 | 0.0046
GEN-2022-238 | 04 SOUTHEAST | 510923 | EC.HEN-4 | 138 | 9.0808 | 9.0844 | 0.0036
GEN-2022-238 | 04 SOUTHEAST | 510925 | KIOWA 7 | 345 | 15.0766 | 15.0833 | 0.0067
GEN-2022-238 | 04 SOUTHEAST | 510931 | KELCO 4 | 138 | 10.6717 | 10.6745 | 0.0028
GEN-2022-238 | 04 SOUTHEAST | 510946 | C-RIVER4 | 138 | 14.5009 | 14.5034 | 0.0025
GEN-2022-238 | 04 SOUTHEAST | 510948 | EARLSBORO 4 | 138 | 8.7938 | 8.869 | 0.0752
GEN-2022-238 | 04 SOUTHEAST | 511421 | VERDEN 4 | 138 | 10.3339 | 10.335 | 0.0011
GEN-2022-238 | 04 SOUTHEAST | 511425 | TUTCONT4 | 138 | 10.6296 | 10.6309 | 0.0013
GEN-2022-238 | 04 SOUTHEAST | 511426 | RUSHSP 4 | 138 | 6.6208 | 6.6216 | 0.0008
GEN-2022-238 | 04 SOUTHEAST | 511427 | RUSHNG 4 | 138 | 6.5132 | 6.514 | 0.0008
GEN-2022-238 | 04 SOUTHEAST | 511445 | CARNEG-4 | 138 | 8.1916 | 8.1918 | 0.0002
GEN-2022-238 | 04 SOUTHEAST | 511449 | CORNVIL4 | 138 | 16.9028 | 16.9096 | 0.0068
GEN-2022-238 | 04 SOUTHEAST | 511450 | CORNVIL2 | 69 | 6.7921 | 6.7925 | 0.0004
GEN-2022-238 | 04 SOUTHEAST | 511451 | CYRIL--2 | 69 | 4.9095 | 4.9095 | 0
GEN-2022-238 | 04 SOUTHEAST | 511476 | S.W.S.-2 | 69 | 4.4134 | 4.4134 | 0
GEN-2022-238 | 04 SOUTHEAST | 511477 | S.W.S.-4 | 138 | 35.4373 | 35.4415 | 0.0042
GEN-2022-238 | 04 SOUTHEAST | 511483 | NORGE--4 | 138 | 11.8297 | 11.8323 | 0.0026
GEN-2022-238 | 04 SOUTHEAST | 511487 | ELGINJT2 | 69 | 8.9871 | 8.9873 | 0.0002
GEN-2022-238 | 04 SOUTHEAST | 511491 | RUSHSPT4 | 138 | 7.6062 | 7.6072 | 0.001
GEN-2022-238 | 04 SOUTHEAST | 511492 | SANTAFE4 | 138 | 7.9155 | 7.9167 | 0.0012
GEN-2022-238 | 04 SOUTHEAST | 511501 | TUTTLE4 | 138 | 10.4459 | 10.4472 | 0.0013
GEN-2022-238 | 04 SOUTHEAST | 511502 | N29CHIK4 | 138 | 10.8485 | 10.8504 | 0.0019
GEN-2022-238 | 04 SOUTHEAST | 511508 | BLANCHD4 | 138 | 6.8522 | 6.8581 | 0.0059
GEN-2022-238 | 04 SOUTHEAST | 511514 | PHILPS 4 | 138 | 5.8795 | 5.8801 | 0.0006
GEN-2022-238 | 04 SOUTHEAST | 511515 | TEXAS 4 | 138 | 5.8998 | 5.9004 | 0.0006
GEN-2022-238 | 04 SOUTHEAST | 511516 | ALEX BR4 | 138 | 6.4845 | 6.4853 | 0.0008
GEN-2022-238 | 04 SOUTHEAST | 511560 | GRADY 4 | 138 | 6.0567 | 6.0574 | 0.0007
GEN-2022-238 | 04 SOUTHEAST | 511562 | ROUNDCK4 | 138 | 6.5475 | 6.5483 | 0.0008
GEN-2022-238 | 04 SOUTHEAST | 511563 | ELSWORTH 4 | 138 | 10.5119 | 10.5123 | 0.0004
GEN-2022-238 | 04 SOUTHEAST | 511569 | DRFTSND4 | 138 | 6.2157 | 6.2164 | 0.0007
GEN-2022-238 | 04 SOUTHEAST | 511573 | REDBDPLN4 | 138 | 4.2588 | 4.259 | 0.0002
GEN-2022-238 | 04 SOUTHEAST | 511575 | LEONARD4 | 138 | 10.2407 | 10.242 | 0.0013
GEN-2022-238 | 04 SOUTHEAST | 514801 | MINCO 7 | 345 | 24.1896 | 24.1967 | 0.0071
GEN-2022-238 | 04 SOUTHEAST | 514808 | JOHNCO 4 | 138 | 17.4063 | 17.4114 | 0.0051
GEN-2022-238 | 04 SOUTHEAST | 514809 | JOHNCO 7 | 345 | 11.4816 | 11.4848 | 0.0032
GEN-2022-238 | 04 SOUTHEAST | 514827 | CTNWOOD4 | 138 | 19.1862 | 19.1878 | 0.0016
GEN-2022-238 | 04 SOUTHEAST | 514879 | NORTWST4 | 138 | 47.0175 | 47.0292 | 0.0117
GEN-2022-238 | 04 SOUTHEAST | 514880 | NORTWST7 | 345 | 35.1144 | 35.126 | 0.0116
GEN-2022-238 | 04 SOUTHEAST | 514881 | SPRNGCK7 | 345 | 24.6351 | 24.6397 | 0.0046
GEN-2022-238 | 04 SOUTHEAST | 514901 | CIMARON7 | 345 | 37.6889 | 37.7045 | 0.0156
GEN-2022-238 | 04 SOUTHEAST | 514906 | JNSKAMO4 | 138 | 21.7449 | 21.7518 | 0.0069
GEN-2022-238 | 04 SOUTHEAST | 514907 | ARCADIA4 | 138 | 43.2662 | 43.2808 | 0.0146
GEN-2022-238 | 04 SOUTHEAST | 514908 | ARCADIA7 | 345 | 28.2062 | 28.2163 | 0.0101
GEN-2022-238 | 04 SOUTHEAST | 514909 | REDBUD 7 | 345 | 27.2496 | 27.258 | 0.0084
GEN-2022-238 | 04 SOUTHEAST | 514933 | DRAPER 4 | 138 | 43.6834 | 43.7133 | 0.0299
GEN-2022-238 | 04 SOUTHEAST | 514934 | DRAPER 7 | 345 | 27.0388 | 27.0684 | 0.0296
GEN-2022-238 | 04 SOUTHEAST | 514941 | HSL 4 | 138 | 44.7335 | 44.7905 | 0.057
GEN-2022-238 | 04 SOUTHEAST | 514946 | MIDWEST4 | 138 | 35.6742 | 35.6921 | 0.0179
GEN-2022-238 | 04 SOUTHEAST | 514949 | SOONRTP4 | 138 | 24.1069 | 24.1149 | 0.008
GEN-2022-238 | 04 SOUTHEAST | 514961 | GM 4 | 138 | 20.8566 | 20.8622 | 0.0056
GEN-2022-238 | 04 SOUTHEAST | 514987 | DALE 4 | 138 | 14.6435 | 14.6981 | 0.0546
GEN-2022-238 | 04 SOUTHEAST | 514996 | ETOWAH 2 | 69 | 3.3251 | 3.3254 | 0.0003
GEN-2022-238 | 04 SOUTHEAST | 515003 | BARNES 4 | 138 | 17.0477 | 17.0533 | 0.0056
GEN-2022-238 | 04 SOUTHEAST | 515004 | ROSEDAL2 | 69 | 4.8217 | 4.8223 | 0.0006
GEN-2022-238 | 04 SOUTHEAST | 515005 | SPRHILT2 | 69 | 3.5885 | 3.5889 | 0.0004
GEN-2022-238 | 04 SOUTHEAST | 515007 | NOBLE 4 | 138 | 19.9671 | 19.9736 | 0.0065
GEN-2022-238 | 04 SOUTHEAST | 515044 | SEMINOL4 | 138 | 42.0666 | 42.4768 | 0.4102
GEN-2022-238 | 04 SOUTHEAST | 515045 | SEMINOL7 | 345 | 29.8153 | 29.8897 | 0.0744
GEN-2022-238 | 04 SOUTHEAST | 515052 | TRIBBEY2 | 69 | 2.6691 | 2.6733 | 0.0042
GEN-2022-238 | 04 SOUTHEAST | 515053 | PEARSNT2 | 69 | 4.4891 | 4.501 | 0.0119
GEN-2022-238 | 04 SOUTHEAST | 515054 | MAUD 2 | 69 | 11.0655 | 11.1353 | 0.0698
GEN-2022-238 | 04 SOUTHEAST | 515055 | MAUD 4 | 138 | 21.0518 | 21.817 | 0.7652
GEN-2022-238 | 04 SOUTHEAST | 515059 | SQUIRCK4 | 138 | 14.7076 | 14.8166 | 0.109
GEN-2022-238 | 04 SOUTHEAST | 515060 | INGLEWD4 | 138 | 10.7909 | 10.8386 | 0.0477
GEN-2022-238 | 04 SOUTHEAST | 515061 | STGREG 4 | 138 | 9.5806 | 9.6116 | 0.031
GEN-2022-238 | 04 SOUTHEAST | 515067 | PEARSON2 | 69 | 3.0249 | 3.0303 | 0.0054
GEN-2022-238 | 04 SOUTHEAST | 515070 | MISSION2 | 69 | 9.0099 | 9.0298 | 0.0199
GEN-2022-238 | 04 SOUTHEAST | 515071 | TECUMSH2 | 69 | 9.9877 | 10.0148 | 0.0271
GEN-2022-238 | 04 SOUTHEAST | 515073 | ERLSBOR2 | 69 | 8.6751 | 8.7054 | 0.0303
GEN-2022-238 | 04 SOUTHEAST | 515074 | FRSTHIL2 | 69 | 11.8292 | 11.8712 | 0.042
GEN-2022-238 | 04 SOUTHEAST | 515075 | FRSTHIL4 | 138 | 14.5772 | 14.7322 | 0.155
GEN-2022-238 | 04 SOUTHEAST | 515076 | FIXICOT2 | 69 | 5.7077 | 5.7177 | 0.01
GEN-2022-238 | 04 SOUTHEAST | 515077 | FIXICO 2 | 69 | 8.6898 | 8.7172 | 0.0274
GEN-2022-238 | 04 SOUTHEAST | 515078 | FIXICO 4 | 138 | 7.7751 | 7.8238 | 0.0487
GEN-2022-238 | 04 SOUTHEAST | 515079 | KOLACHE2 | 69 | 2.3874 | 2.3891 | 0.0017
GEN-2022-238 | 04 SOUTHEAST | 515080 | LIMATAP2 | 69 | 6.2417 | 6.2568 | 0.0151
GEN-2022-238 | 04 SOUTHEAST | 515081 | CYPRESS2 | 69 | 3.2903 | 3.2952 | 0.0049
GEN-2022-238 | 04 SOUTHEAST | 515085 | EMAHAKA2 | 69 | 3.5719 | 3.5776 | 0.0057
GEN-2022-238 | 04 SOUTHEAST | 515086 | LETHA 2 | 69 | 4.364 | 4.3713 | 0.0073
GEN-2022-238 | 04 SOUTHEAST | 515087 | WEWOKAT2 | 69 | 4.491 | 4.5 | 0.009
GEN-2022-238 | 04 SOUTHEAST | 515088 | LTRIVER2 | 69 | 4.891 | 4.9028 | 0.0118
GEN-2022-238 | 04 SOUTHEAST | 515089 | WEWOKA 2 | 69 | 4.4919 | 4.5009 | 0.009
GEN-2022-238 | 04 SOUTHEAST | 515091 | KONOWAP2 | 69 | 4.1647 | 4.1717 | 0.007
GEN-2022-238 | 04 SOUTHEAST | 515093 | JUMPRCK2 | 69 | 4.0066 | 4.0115 | 0.0049
GEN-2022-238 | 04 SOUTHEAST | 515094 | SASAKWT2 | 69 | 4.1215 | 4.1257 | 0.0042
GEN-2022-238 | 04 SOUTHEAST | 515095 | SRVCEPL2 | 69 | 2.4378 | 2.4413 | 0.0035
GEN-2022-238 | 04 SOUTHEAST | 515097 | WLNUTCK4 | 138 | 10.0844 | 10.0875 | 0.0031
GEN-2022-238 | 04 SOUTHEAST | 515098 | AMOCOT 2 | 69 | 6.0929 | 6.0939 | 0.001
GEN-2022-238 | 04 SOUTHEAST | 515099 | PALIOGE2 | 69 | 9.1129 | 9.1152 | 0.0023
GEN-2022-238 | 04 SOUTHEAST | 515100 | PAOLI- 4 | 138 | 11.0216 | 11.0286 | 0.007
GEN-2022-238 | 04 SOUTHEAST | 515101 | PAULSVL2 | 69 | 6.1565 | 6.1576 | 0.0011
GEN-2022-238 | 04 SOUTHEAST | 515105 | WYNWOD 2 | 69 | 6.6062 | 6.6074 | 0.0012
GEN-2022-238 | 04 SOUTHEAST | 515110 | WNREF1T2 | 69 | 7.385 | 7.3865 | 0.0015
GEN-2022-238 | 04 SOUTHEAST | 515111 | DAVS 2 | 69 | 5.1559 | 5.1566 | 0.0007
GEN-2022-238 | 04 SOUTHEAST | 515113 | CHIGLEY2 | 69 | 7.3976 | 7.3991 | 0.0015
GEN-2022-238 | 04 SOUTHEAST | 515114 | CHIGLEY4 | 138 | 8.6871 | 8.6914 | 0.0043
GEN-2022-238 | 04 SOUTHEAST | 515116 | ARBUCKL2 | 69 | 6.4917 | 6.4928 | 0.0011
GEN-2022-238 | 04 SOUTHEAST | 515117 | ARBUCKL4 | 138 | 16.9443 | 16.9608 | 0.0165
GEN-2022-238 | 04 SOUTHEAST | 515118 | JOLLYVL4 | 138 | 9.5011 | 9.5047 | 0.0036
GEN-2022-238 | 04 SOUTHEAST | 515121 | MILLCKT4 | 138 | 12.1155 | 12.1197 | 0.0042
GEN-2022-238 | 04 SOUTHEAST | 515122 | SXMLCKT4 | 138 | 12.286 | 12.2901 | 0.0041
GEN-2022-238 | 04 SOUTHEAST | 515123 | OAKLAW-4 | 138 | 13.6505 | 13.6612 | 0.0107
GEN-2022-238 | 04 SOUTHEAST | 515124 | MAYSVIL4 | 138 | 6.5999 | 6.6017 | 0.0018
GEN-2022-238 | 04 SOUTHEAST | 515133 | BLUERIV4 | 138 | 11.0873 | 11.0977 | 0.0104
GEN-2022-238 | 04 SOUTHEAST | 515134 | PRARPNT4 | 138 | 5.9285 | 5.9294 | 0.0009
GEN-2022-238 | 04 SOUTHEAST | 515169 | AIRPRKT4 | 138 | 8.9457 | 8.9481 | 0.0024
GEN-2022-238 | 04 SOUTHEAST | 515173 | BERWYN 4 | 138 | 8.8592 | 8.8615 | 0.0023
GEN-2022-238 | 04 SOUTHEAST | 515174 | VANOSS 4 | 138 | 13.9063 | 13.9318 | 0.0255
GEN-2022-238 | 04 SOUTHEAST | 515175 | IDEAL 2 | 69 | 12.4042 | 12.4167 | 0.0125
GEN-2022-238 | 04 SOUTHEAST | 515177 | PARKLN 2 | 69 | 14.8386 | 14.8564 | 0.0178
GEN-2022-238 | 04 SOUTHEAST | 515178 | PARKLN 4 | 138 | 17.1716 | 17.2135 | 0.0419
GEN-2022-238 | 04 SOUTHEAST | 515179 | BYNGSPA2 | 69 | 4.9962 | 5.0004 | 0.0042
GEN-2022-238 | 04 SOUTHEAST | 515196 | MILLCRK4 | 138 | 9.869 | 9.8717 | 0.0027
GEN-2022-238 | 04 SOUTHEAST | 515224 | MUSKOGE7 | 345 | 28.7889 | 28.7923 | 0.0034
GEN-2022-238 | 04 SOUTHEAST | 515235 | PECANCK7 | 345 | 23.2658 | 23.2677 | 0.0019
GEN-2022-238 | 04 SOUTHEAST | 515286 | STRLGTP4 | 138 | 14.5345 | 14.6546 | 0.1201
GEN-2022-238 | 04 SOUTHEAST | 515302 | FTSMITH7 | 345 | 10.6073 | 10.6074 | 0.0001
GEN-2022-238 | 04 SOUTHEAST | 515318 | SOTHADA4 | 138 | 11.9544 | 11.9724 | 0.018
GEN-2022-238 | 04 SOUTHEAST | 515362 | HARDEN 4 | 138 | 8.4482 | 8.4545 | 0.0063
GEN-2022-238 | 04 SOUTHEAST | 515384 | ADAINDU2 | 69 | 9.3572 | 9.3637 | 0.0065
GEN-2022-238 | 04 SOUTHEAST | 515385 | YOUNGCT2 | 69 | 4.2894 | 4.2961 | 0.0067
GEN-2022-238 | 04 SOUTHEAST | 515386 | YOUNGCK2 | 69 | 3.5498 | 3.5544 | 0.0046
GEN-2022-238 | 04 SOUTHEAST | 515422 | C-RIVER7 | 345 | 11.8062 | 11.8094 | 0.0032
GEN-2022-238 | 04 SOUTHEAST | 515461 | RNDBARN4 | 138 | 41.1659 | 41.1792 | 0.0133
GEN-2022-238 | 04 SOUTHEAST | 515465 | LGARBER4 | 138 | 22.2007 | 22.206 | 0.0053
GEN-2022-238 | 04 SOUTHEAST | 515475 | PURCELL4 | 138 | 10.7876 | 10.7907 | 0.0031
GEN-2022-238 | 04 SOUTHEAST | 515492 | CRMWLTP2 | 69 | 4.2421 | 4.2457 | 0.0036
GEN-2022-238 | 04 SOUTHEAST | 515494 | EMHKATP2 | 69 | 3.575 | 3.5807 | 0.0057
GEN-2022-238 | 04 SOUTHEAST | 515496 | KNAWATP2 | 69 | 4.6074 | 4.616 | 0.0086
GEN-2022-238 | 04 SOUTHEAST | 515497 | MATHWSN7 | 345 | 35.0345 | 35.0446 | 0.0101
GEN-2022-238 | 04 SOUTHEAST | 515503 | LTRIVRT2 | 69 | 4.9044 | 4.9163 | 0.0119
GEN-2022-238 | 04 SOUTHEAST | 515513 | JMPRCKT2 | 69 | 4.0273 | 4.0323 | 0.005
GEN-2022-238 | 04 SOUTHEAST | 515515 | SUNOILT2 | 69 | 6.8041 | 6.8054 | 0.0013
GEN-2022-238 | 04 SOUTHEAST | 515531 | VANOSTP4 | 138 | 14.0405 | 14.0664 | 0.0259
GEN-2022-238 | 04 SOUTHEAST | 515559 | SULPHR 4 | 138 | 15.3548 | 15.368 | 0.0132
GEN-2022-238 | 04 SOUTHEAST | 515570 | MAYSVLT4 | 138 | 6.2218 | 6.2233 | 0.0015
GEN-2022-238 | 04 SOUTHEAST | 515636 | TRIBYTP2 | 69 | 2.6721 | 2.6763 | 0.0042
GEN-2022-238 | 04 SOUTHEAST | 515637 | SRVCPLT2 | 69 | 2.6765 | 2.6808 | 0.0043
GEN-2022-238 | 04 SOUTHEAST | 515933 | MLCLMRD4 | 138 | 9.2684 | 9.2695 | 0.0011
GEN-2022-238 | 04 SOUTHEAST | 515977 | LKKONWA4 | 138 | 41.1245 | 41.5153 | 0.3908
GEN-2022-238 | 04 SOUTHEAST | 516006 | DMNDSPG7 | 345 | 8.1784 | 8.1798 | 0.0014
GEN-2022-238 | 04 SOUTHEAST | 516009 | IRNHSTP2 | 69 | 8.6623 | 8.6796 | 0.0173
GEN-2022-238 | 04 SOUTHEAST | 516091 | OKTAHA 7 | 345 | 17.1448 | 17.1475 | 0.0027
GEN-2022-238 | 04 SOUTHEAST | 516092 | OKTAHA 5 | 161 | 10.9411 | 10.9416 | 0.0005
GEN-2022-238 | 04 SOUTHEAST | 516096 | NORMHLL7 | 345 | 28.1279 | 28.1509 | 0.023
GEN-2022-238 | 04 SOUTHEAST | 516097 | NORMHLL4 | 138 | 44.4173 | 44.4382 | 0.0209
GEN-2022-238 | 04 SOUTHEAST | 520422 | SEQUOYAHJ4 | 138 | 26.7675 | 26.7703 | 0.0028
GEN-2022-238 | 04 SOUTHEAST | 520445 | MAYSVLL4 | 138 | 6.1467 | 6.1482 | 0.0015
GEN-2022-238 | 04 SOUTHEAST | 520449 | STERLNG4 | 138 | 11.7937 | 11.8729 | 0.0792
GEN-2022-238 | 04 SOUTHEAST | 520472 | CHCKSHA4 | 138 | 8.8389 | 8.8399 | 0.001
GEN-2022-238 | 04 SOUTHEAST | 520473 | CKSHATP4 | 138 | 11.5133 | 11.5149 | 0.0016
GEN-2022-238 | 04 SOUTHEAST | 520510 | NAPLSTP4 | 138 | 9.0921 | 9.0936 | 0.0015
GEN-2022-238 | 04 SOUTHEAST | 520604 | NAPLES 4 | 138 | 6.4356 | 6.4364 | 0.0008
GEN-2022-238 | 04 SOUTHEAST | 520814 | ANADARK4 | 138 | 37.4694 | 37.4742 | 0.0048
GEN-2022-238 | 04 SOUTHEAST | 520867 | CORN TP4 | 138 | 14.6174 | 14.6216 | 0.0042
GEN-2022-238 | 04 SOUTHEAST | 520888 | PAYNESW4 | 138 | 9.5796 | 9.5812 | 0.0016
GEN-2022-238 | 04 SOUTHEAST | 521019 | OAKLAWN4 | 138 | 13.6505 | 13.6612 | 0.0107
GEN-2022-238 | 04 SOUTHEAST | 521089 | WASHITA4 | 138 | 31.3279 | 31.331 | 0.0031
GEN-2022-238 | 04 SOUTHEAST | 521157 | HUGO 7 | 345 | 11.8818 | 11.8828 | 0.001
GEN-2022-238 | 04 SOUTHEAST | 529307 | OMMARLO4 | 138 | 6.2248 | 6.2254 | 0.0006
GEN-2022-238 | 04 SOUTHEAST | 587794 | G16-097-TAP | 138 | 11.7141 | 11.7145 | 0.0004
GEN-2022-238 | 04 SOUTHEAST | 587820 | GEN-2016-102 | 138 | 10.1476 | 10.1562 | 0.0086
GEN-2022-238 | 04 SOUTHEAST | 588180 | GEN-2016-126 | 138 | 13.9274 | 13.9384 | 0.011
GEN-2022-238 | 04 SOUTHEAST | 588810 | GEN-2017-040 | 345 | 18.6332 | 18.6373 | 0.0041
GEN-2022-238 | 04 SOUTHEAST | 588838 | G17-092-SWYD | 345 | 19.0592 | 19.0634 | 0.0042
GEN-2022-238 | 04 SOUTHEAST | 588839 | FIREWHL-TAP | 345 | 19.0592 | 19.0634 | 0.0042
GEN-2022-238 | 04 SOUTHEAST | 589300 | GEN-2017-092 | 345 | 15.5182 | 15.521 | 0.0028
GEN-2022-238 | 04 SOUTHEAST | 760032 | GEN-2017-133 | 345 | 4.9609 | 4.9611 | 0.0002
GEN-2022-238 | 04 SOUTHEAST | 760830 | GEN-2017-149 | 345 | 3.9294 | 3.9297 | 0.0003
GEN-2022-238 | 04 SOUTHEAST | 762592 | GEN-2018-024 | 345 | 18.4762 | 18.4802 | 0.004
GEN-2022-238 | 04 SOUTHEAST | 763131 | GEN-2018-082 | 345 | 9.916 | 9.9188 | 0.0028
GEN-2022-238 | 04 SOUTHEAST | 764520 | G20-020-TAP | 345 | 10.5604 | 10.5606 | 0.0002
GEN-2022-238 | 04 SOUTHEAST | 765451 | G21-016-TAP | 345 | 11.7604 | 11.7632 | 0.0028
GEN-2022-238 | 04 SOUTHEAST | 771721 | GEN-2022-238 | 138 | 19.1595 | 19.9281 | 0.7686
GEN-2022-073 | 03 CENTRAL | 768441 | GEN-2022-073 | 161 | 22.2414 | 23.4933 | 1.2519
GEN-2022-073 | 03 CENTRAL | 768440 | G22-073-TAP | 161 | 27.2751 | 28.5145 | 1.2394
GEN-2022-073 | 03 CENTRAL | 541203 | NASHUA 5 | 161 | 28.6715 | 29.89 | 1.2185
GEN-2022-073 | 03 CENTRAL | 543028 | NASHUA-5 | 161 | 28.7958 | 30.0095 | 1.2137
GEN-2022-214 | 03 CENTRAL | 771261 | GEN-2022-214 | 138 | 13.1981 | 14.3186 | 1.1205
GEN-2022-214 | 03 CENTRAL | 771260 | G22-214-TAP | 138 | 13.3645 | 14.4839 | 1.1194
GEN-2022-073 | 03 CENTRAL | 543039 | FRSTCRK5 | 161 | 26.5683 | 27.5267 | 0.9584
GEN-2022-073 | 03 CENTRAL | 541144 | NASHUA_CAP5 | 161 | 24.4179 | 25.2964 | 0.8785
GEN-2022-142 | 03 CENTRAL | 769821 | GEN-2022-142 | 161 | 17.3054 | 18.1541 | 0.8487
GEN-2022-142 | 03 CENTRAL | 543029 | SHOLCRK5 | 161 | 17.3653 | 18.2139 | 0.8486
GEN-2022-144 | 03 CENTRAL | 769861 | GEN-2022-144 | 161 | 16.9567 | 17.8031 | 0.8464
GEN-2022-144 | 03 CENTRAL | 543004 | BLUMILS5 | 161 | 17.0142 | 17.8605 | 0.8463
GEN-2022-006 | 03 CENTRAL | 767101 | GEN-2022-006 | 161 | 17.8622 | 18.6386 | 0.7764
GEN-2022-006 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 21.9188 | 22.6894 | 0.7706
GEN-2022-007 | 03 CENTRAL | 767121 | GEN-2022-007 | 115 | 14.185 | 14.9265 | 0.7415
GEN-2022-007 | 03 CENTRAL | 767120 | G22-007-TAP | 115 | 14.2915 | 15.0327 | 0.7412
GEN-2022-007 | 03 CENTRAL | 533304 | LANG 3 | 115 | 15.0985 | 15.8275 | 0.729
GEN-2022-161 | 03 CENTRAL | 583850 | GEN-2014-001 | 345 | 6.3449 | 7.0166 | 0.6717
GEN-2022-161 | 03 CENTRAL | 562477 | GEN-2022-161 | 345 | 6.3449 | 7.0166 | 0.6717
GEN-2022-073 | 03 CENTRAL | 541204 | SMTHVL 5 | 161 | 21.2456 | 21.9148 | 0.6692
GEN-2022-214 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.3849 | 25.0372 | 0.6523
GEN-2022-161 | 03 CENTRAL | 583859 | GEN-2014-001 | 345 | 7.8581 | 8.497 | 0.6389
GEN-2022-161 | 03 CENTRAL | 532803 | BURNS 7 | 345 | 10.0734 | 10.685 | 0.6116
GEN-2022-013 | 03 CENTRAL | 767241 | GEN-2022-013 | 345 | 5.6032 | 6.1707 | 0.5675
GEN-2022-013 | 03 CENTRAL | 767240 | G22-013-TAP | 345 | 5.6048 | 6.1723 | 0.5675
GEN-2022-006 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 23.5073 | 24.0458 | 0.5385
GEN-2022-006 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 23.4701 | 24.0079 | 0.5378
GEN-2022-006 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 23.4017 | 23.9347 | 0.533
GEN-2022-015 | 03 CENTRAL | 767281 | GEN-2022-015 | 345 | 5.5869 | 6.1064 | 0.5195
GEN-2022-015 | 03 CENTRAL | 767280 | G22-015-TAP | 345 | 5.5888 | 6.1082 | 0.5194
GEN-2022-214 | 03 CENTRAL | 533047 | GILL 4 | 138 | 21.4814 | 21.9978 | 0.5164
GEN-2022-214 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 21.484 | 21.9988 | 0.5148
GEN-2022-214 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 21.4875 | 22.0023 | 0.5148
GEN-2022-214 | 03 CENTRAL | 533044 | GILL E 4 | 138 | 21.4245 | 21.9353 | 0.5108
GEN-2022-100 | 03 CENTRAL | 768981 | GEN-2022-100 | 161 | 7.0823 | 7.5786 | 0.4963
GEN-2022-100 | 03 CENTRAL | 768980 | G22-100-TAP | 161 | 7.1223 | 7.6184 | 0.4961
GEN-2022-013 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 15.0115 | 15.4985 | 0.487
GEN-2022-013 | 03 CENTRAL | 765350 | GEN-2021-006 | 345 | 14.9618 | 15.4455 | 0.4837
GEN-2022-142 | 03 CENTRAL | 543016 | GLADSTN5 | 161 | 18.1662 | 18.647 | 0.4808
GEN-2022-214 | 03 CENTRAL | 767061 | GEN-2022-004 | 138 | 20.4876 | 20.9548 | 0.4672
GEN-2022-144 | 03 CENTRAL | 548807 | BLUVLY-161 | 161 | 18.1387 | 18.6044 | 0.4657
GEN-2022-144 | 03 CENTRAL | 762669 | GEN-2018-031 | 161 | 18.1367 | 18.6023 | 0.4656
GEN-2022-144 | 03 CENTRAL | 548808 | ECKLES-161 | 161 | 25.1574 | 25.6133 | 0.4559
GEN-2022-142 | 03 CENTRAL | 543028 | NASHUA-5 | 161 | 29.569 | 30.0095 | 0.4405
GEN-2022-142 | 03 CENTRAL | 541203 | NASHUA 5 | 161 | 29.4546 | 29.89 | 0.4354
GEN-2022-073 | 03 CENTRAL | 541230 | RNRIDGE5 | 161 | 22.7592 | 23.1489 | 0.3897
GEN-2022-142 | 03 CENTRAL | 768440 | G22-073-TAP | 161 | 28.1252 | 28.5145 | 0.3893
GEN-2022-142 | 03 CENTRAL | 542946 | GLADSTN_CAP5 | 161 | 16.3598 | 16.7488 | 0.389
GEN-2022-102 | 03 CENTRAL | 541247 | LBRTYWT5 | 161 | 14.9387 | 15.3272 | 0.3885
GEN-2022-102 | 03 CENTRAL | 769021 | GEN-2022-102 | 161 | 14.7909 | 15.1793 | 0.3884
GEN-2022-054 | 03 CENTRAL | 768061 | GEN-2022-054 | 345 | 8.8503 | 9.2345 | 0.3842
GEN-2022-054 | 03 CENTRAL | 765200 | G20-090-TAP | 345 | 10.0011 | 10.3835 | 0.3824
GEN-2022-024 | 03 CENTRAL | 767240 | G22-013-TAP | 345 | 5.8029 | 6.1723 | 0.3694
GEN-2022-024 | 03 CENTRAL | 767241 | GEN-2022-013 | 345 | 5.8013 | 6.1707 | 0.3694
GEN-2022-065 | 03 CENTRAL | 768281 | GEN-2022-065 | 230 | 5.4431 | 5.8101 | 0.367
GEN-2022-214 | 03 CENTRAL | 533071 | WACO S 4 | 138 | 18.7297 | 19.0946 | 0.3649
GEN-2022-065 | 03 CENTRAL | 768280 | G22-065-TAP | 230 | 6.4055 | 6.769 | 0.3635
GEN-2022-214 | 03 CENTRAL | 533072 | WACO 4 | 138 | 18.6801 | 19.0426 | 0.3625
GEN-2022-214 | 03 CENTRAL | 533073 | WACO N 4 | 138 | 18.6311 | 18.9911 | 0.36
GEN-2022-144 | 03 CENTRAL | 542973 | HAWTHS5 | 161 | 58.0516 | 58.4089 | 0.3573
GEN-2022-144 | 03 CENTRAL | 543665 | HAWTHN5 | 161 | 58.7307 | 59.0854 | 0.3547
GEN-2022-214 | 03 CENTRAL | 533796 | GILL W 2 | 69 | 28.8378 | 29.1918 | 0.354
GEN-2022-214 | 03 CENTRAL | 533795 | GILL E 2 | 69 | 28.8304 | 29.184 | 0.3536
GEN-2022-142 | 03 CENTRAL | 543039 | FRSTCRK5 | 161 | 27.1758 | 27.5267 | 0.3509
GEN-2022-144 | 03 CENTRAL | 543129 | HAWTHS_G65 | 161 | 57.2005 | 57.5469 | 0.3464
GEN-2022-144 | 03 CENTRAL | 543130 | HAWTHS_XF5 | 161 | 57.1407 | 57.487 | 0.3463
GEN-2022-142 | 03 CENTRAL | 543022 | CLAYCM15 | 161 | 11.0806 | 11.4203 | 0.3397
GEN-2022-065 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.5609 | 6.8977 | 0.3368
GEN-2022-142 | 03 CENTRAL | 543015 | AVONDAL5 | 161 | 29.5327 | 29.8684 | 0.3357
GEN-2022-142 | 03 CENTRAL | 543665 | HAWTHN5 | 161 | 58.7564 | 59.0854 | 0.329
GEN-2022-065 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.4768 | 6.8048 | 0.328
GEN-2022-142 | 03 CENTRAL | 542973 | HAWTHS5 | 161 | 58.0915 | 58.4089 | 0.3174
GEN-2022-073 | 03 CENTRAL | 543665 | HAWTHN5 | 161 | 58.7724 | 59.0854 | 0.313
GEN-2022-142 | 03 CENTRAL | 541144 | NASHUA_CAP5 | 161 | 24.9838 | 25.2964 | 0.3126
GEN-2022-015 | 03 CENTRAL | 531429 | MINGO 3 | 115 | 12.1544 | 12.4663 | 0.3119
GEN-2022-024 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 15.1887 | 15.4985 | 0.3098
GEN-2022-142 | 03 CENTRAL | 543129 | HAWTHS_G65 | 161 | 57.2392 | 57.5469 | 0.3077
GEN-2022-024 | 03 CENTRAL | 765350 | GEN-2021-006 | 345 | 15.1379 | 15.4455 | 0.3076
GEN-2022-142 | 03 CENTRAL | 543130 | HAWTHS_XF5 | 161 | 57.1795 | 57.487 | 0.3075
GEN-2022-073 | 03 CENTRAL | 542973 | HAWTHS5 | 161 | 58.1057 | 58.4089 | 0.3032
GEN-2022-144 | 03 CENTRAL | 548814 | SUB M-161 | 161 | 20.5706 | 20.8737 | 0.3031
GEN-2022-073 | 03 CENTRAL | 541145 | RNRIDGE_CAP5 | 161 | 19.9935 | 20.2937 | 0.3002
GEN-2022-073 | 03 CENTRAL | 543129 | HAWTHS_G65 | 161 | 57.253 | 57.5469 | 0.2939
GEN-2022-073 | 03 CENTRAL | 543130 | HAWTHS_XF5 | 161 | 57.1932 | 57.487 | 0.2938
GEN-2022-015 | 03 CENTRAL | 531451 | MINGO 7 | 345 | 6.2282 | 6.5189 | 0.2907
GEN-2022-144 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 28.3658 | 28.6561 | 0.2903
GEN-2022-075 | 03 CENTRAL | 768481 | GEN-2022-075 | 345 | 6.7301 | 7.0182 | 0.2881
GEN-2022-075 | 03 CENTRAL | 768480 | G22-075-TAP | 345 | 7.6445 | 7.9316 | 0.2871
GEN-2022-054 | 03 CENTRAL | 765190 | GEN-2020-090 | 345 | 8.7217 | 9.0076 | 0.2859
GEN-2022-015 | 03 CENTRAL | 640325 | REDWILO3 | 345 | 6.1875 | 6.4726 | 0.2851
GEN-2022-142 | 03 CENTRAL | 543666 | NEASTN5 | 161 | 46.8919 | 47.1752 | 0.2833
GEN-2022-142 | 03 CENTRAL | 542985 | NEASTS5 | 161 | 46.4919 | 46.7641 | 0.2722
GEN-2022-144 | 03 CENTRAL | 542976 | LEVEE 5 | 161 | 52.2767 | 52.5451 | 0.2684
GEN-2022-013 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 22.4235 | 22.6894 | 0.2659
GEN-2022-142 | 03 CENTRAL | 542976 | LEVEE 5 | 161 | 52.2828 | 52.5451 | 0.2623
GEN-2022-013 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 23.786 | 24.0458 | 0.2598
GEN-2022-142 | 03 CENTRAL | 768441 | GEN-2022-073 | 161 | 23.2337 | 23.4933 | 0.2596
GEN-2022-073 | 03 CENTRAL | 541318 | NCONGRS5 | 161 | 18.4412 | 18.7006 | 0.2594
GEN-2022-013 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 23.7491 | 24.0079 | 0.2588
GEN-2022-073 | 03 CENTRAL | 543026 | TIFFANY5 | 161 | 19.7073 | 19.9658 | 0.2585
GEN-2022-013 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 23.6775 | 23.9347 | 0.2572
GEN-2022-073 | 03 CENTRAL | 543666 | NEASTN5 | 161 | 46.919 | 47.1752 | 0.2562
GEN-2022-102 | 03 CENTRAL | 541203 | NASHUA 5 | 161 | 29.6398 | 29.89 | 0.2502
GEN-2022-102 | 03 CENTRAL | 543028 | NASHUA-5 | 161 | 29.7602 | 30.0095 | 0.2493
GEN-2022-073 | 03 CENTRAL | 542976 | LEVEE 5 | 161 | 52.2966 | 52.5451 | 0.2485
GEN-2022-073 | 03 CENTRAL | 542985 | NEASTS5 | 161 | 46.5167 | 46.7641 | 0.2474
GEN-2022-214 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 31.14 | 31.3756 | 0.2356
GEN-2022-214 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 31.0656 | 31.3008 | 0.2352
GEN-2022-073 | 03 CENTRAL | 541349 | POPE | 161 | 12.6419 | 12.8761 | 0.2342
GEN-2022-214 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 30.9733 | 31.2062 | 0.2329
GEN-2022-073 | 03 CENTRAL | 543029 | SHOLCRK5 | 161 | 17.9825 | 18.2139 | 0.2314
GEN-2022-144 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 26.73 | 26.9609 | 0.2309
GEN-2022-007 | 03 CENTRAL | 533301 | EAST ST3 | 115 | 9.7502 | 9.9809 | 0.2307
GEN-2022-073 | 03 CENTRAL | 769821 | GEN-2022-142 | 161 | 17.9243 | 18.1541 | 0.2298
GEN-2022-142 | 03 CENTRAL | 543018 | NKANCTY5 | 161 | 33.7775 | 34.0069 | 0.2294
GEN-2022-100 | 03 CENTRAL | 345409 | 5OVERTON | 161 | 20.3876 | 20.6148 | 0.2272
GEN-2022-100 | 03 CENTRAL | 345411 | 5OVERTON 2 | 161 | 20.3876 | 20.6148 | 0.2272
GEN-2022-102 | 03 CENTRAL | 541215 | HLLMRK 5 | 161 | 13.386 | 13.6117 | 0.2257
GEN-2022-007 | 03 CENTRAL | 533307 | PRAIRIE3 | 115 | 9.8836 | 10.1079 | 0.2243
GEN-2022-161 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.0781 | 23.3018 | 0.2237
GEN-2022-102 | 03 CENTRAL | 768440 | G22-073-TAP | 161 | 28.291 | 28.5145 | 0.2235
GEN-2022-075 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 8.0024 | 8.2258 | 0.2234
GEN-2022-075 | 03 CENTRAL | 765990 | GEN-2021-076 | 345 | 8.0024 | 8.2258 | 0.2234
GEN-2022-006 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 22.5982 | 22.8204 | 0.2222
GEN-2022-006 | 03 CENTRAL | 533768 | NEOSHON2 | 69 | 22.5748 | 22.7966 | 0.2218
GEN-2022-007 | 03 CENTRAL | 533309 | WEMPORI3 | 115 | 10.8173 | 11.0372 | 0.2199
GEN-2022-073 | 03 CENTRAL | 541221 | PLTCTY 5 | 161 | 15.814 | 16.033 | 0.219
GEN-2022-015 | 03 CENTRAL | 531632 | GEN-2015-065 | 345 | 5.556 | 5.7747 | 0.2187
GEN-2022-073 | 03 CENTRAL | 301552 | 5PLATCTY | 161 | 15.7508 | 15.9679 | 0.2171
GEN-2022-214 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 13.9924 | 14.2081 | 0.2157
GEN-2022-142 | 03 CENTRAL | 541204 | SMTHVL 5 | 161 | 21.7033 | 21.9148 | 0.2115
GEN-2022-142 | 03 CENTRAL | 543027 | RANDLPH5 | 161 | 32.9922 | 33.2021 | 0.2099
GEN-2022-073 | 03 CENTRAL | 541247 | LBRTYWT5 | 161 | 15.119 | 15.3272 | 0.2082
GEN-2022-073 | 03 CENTRAL | 769021 | GEN-2022-102 | 161 | 14.9752 | 15.1793 | 0.2041
GEN-2022-142 | 03 CENTRAL | 542987 | GRAND 5 | 161 | 42.4176 | 42.62 | 0.2024
GEN-2022-073 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 22.5037 | 22.7056 | 0.2019
GEN-2022-214 | 03 CENTRAL | 533851 | VULCTP 2 | 69 | 21.8215 | 22.0218 | 0.2003
GEN-2022-073 | 03 CENTRAL | 543019 | BARRY 5 | 161 | 18.1903 | 18.3871 | 0.1968
GEN-2022-006 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 15.3018 | 15.4985 | 0.1967
GEN-2022-102 | 03 CENTRAL | 543039 | FRSTCRK5 | 161 | 27.3303 | 27.5267 | 0.1964
GEN-2022-006 | 03 CENTRAL | 765350 | GEN-2021-006 | 345 | 15.2501 | 15.4455 | 0.1954
GEN-2022-214 | 03 CENTRAL | 533029 | 59TH ST4 | 138 | 16.9093 | 17.1038 | 0.1945
GEN-2022-214 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 28.3001 | 28.494 | 0.1939
GEN-2022-065 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.7513 | 12.9439 | 0.1926
GEN-2022-100 | 03 CENTRAL | 541241 | SEDEAST5 | 161 | 7.5395 | 7.7294 | 0.1899
GEN-2022-214 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 13.9057 | 14.0939 | 0.1882
GEN-2022-214 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 24.0641 | 24.2519 | 0.1878
GEN-2022-015 | 03 CENTRAL | 531623 | EASTFORK3 | 115 | 9.4387 | 9.6258 | 0.1871
GEN-2022-214 | 03 CENTRAL | 533059 | ELPASOE4 | 138 | 24.0239 | 24.2108 | 0.1869
GEN-2022-015 | 03 CENTRAL | 640326 | REDWILO7 | 115 | 11.131 | 11.3151 | 0.1841
GEN-2022-065 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.4206 | 12.6026 | 0.182
GEN-2022-102 | 03 CENTRAL | 541144 | NASHUA_CAP5 | 161 | 25.1169 | 25.2964 | 0.1795
GEN-2022-073 | 03 CENTRAL | 541214 | TWA 5 | 161 | 15.0904 | 15.268 | 0.1776
GEN-2022-161 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.7775 | 16.9548 | 0.1773
GEN-2022-013 | 03 CENTRAL | 767101 | GEN-2022-006 | 161 | 18.4615 | 18.6386 | 0.1771
GEN-2022-161 | 03 CENTRAL | 532769 | LANG 7 | 345 | 16.5865 | 16.7596 | 0.1731
GEN-2022-013 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 10.6647 | 10.8378 | 0.1731
GEN-2022-075 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 11.4385 | 11.6072 | 0.1687
GEN-2022-024 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 22.5215 | 22.6894 | 0.1679
GEN-2022-073 | 03 CENTRAL | 543015 | AVONDAL5 | 161 | 29.7011 | 29.8684 | 0.1673
GEN-2022-214 | 03 CENTRAL | 533051 | INTERST4 | 138 | 15.3942 | 15.5611 | 0.1669
GEN-2022-100 | 03 CENTRAL | 541395 | NUCOR5 | 161 | 7.0601 | 7.2263 | 0.1662
GEN-2022-214 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.1367 | 23.3018 | 0.1651
GEN-2022-075 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 11.3325 | 11.4969 | 0.1644
GEN-2022-075 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 11.3325 | 11.4969 | 0.1644
GEN-2022-024 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 23.8818 | 24.0458 | 0.164
GEN-2022-004 | 03 CENTRAL | 533045 | GILL W 4 | 138 | 21.8384 | 22.0023 | 0.1639
GEN-2022-004 | 03 CENTRAL | 767061 | GEN-2022-004 | 138 | 20.7909 | 20.9548 | 0.1639
GEN-2022-024 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 23.8446 | 24.0079 | 0.1633
GEN-2022-004 | 03 CENTRAL | 533046 | GILL S 4 | 138 | 21.8355 | 21.9988 | 0.1633
GEN-2022-004 | 03 CENTRAL | 533047 | GILL 4 | 138 | 21.8345 | 21.9978 | 0.1633
GEN-2022-004 | 03 CENTRAL | 533044 | GILL E 4 | 138 | 21.7728 | 21.9353 | 0.1625
GEN-2022-024 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 23.7724 | 23.9347 | 0.1623
GEN-2022-073 | 03 CENTRAL | 543018 | NKANCTY5 | 161 | 33.8471 | 34.0069 | 0.1598
GEN-2022-073 | 03 CENTRAL | 542944 | BARRY_CAP 5 | 161 | 16.3793 | 16.5387 | 0.1594
GEN-2022-142 | 03 CENTRAL | 541230 | RNRIDGE5 | 161 | 22.9903 | 23.1489 | 0.1586
GEN-2022-144 | 03 CENTRAL | 543000 | BLUEVLY5 | 161 | 38.6159 | 38.7732 | 0.1573
GEN-2022-007 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.7988 | 16.9548 | 0.156
GEN-2022-214 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 29.6975 | 29.8534 | 0.1559
GEN-2022-007 | 03 CENTRAL | 532769 | LANG 7 | 345 | 16.6038 | 16.7596 | 0.1558
GEN-2022-214 | 03 CENTRAL | 533050 | HOOVERS4 | 138 | 16.7281 | 16.8815 | 0.1534
GEN-2022-054 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 15.2173 | 15.3689 | 0.1516
GEN-2022-073 | 03 CENTRAL | 543016 | GLADSTN5 | 161 | 18.4955 | 18.647 | 0.1515
GEN-2022-073 | 03 CENTRAL | 541213 | FRLVW 5 | 161 | 13.7358 | 13.8857 | 0.1499
GEN-2022-102 | 03 CENTRAL | 768441 | GEN-2022-073 | 161 | 23.3444 | 23.4933 | 0.1489
GEN-2022-013 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 9.9302 | 10.0789 | 0.1487
GEN-2022-142 | 03 CENTRAL | 543011 | CHOUTEU5 | 161 | 36.0924 | 36.2392 | 0.1468
GEN-2022-214 | 03 CENTRAL | 533850 | VULCAN 2 | 69 | 18.5662 | 18.7124 | 0.1462
GEN-2022-144 | 03 CENTRAL | 301563 | 5MOCITYB1 | 161 | 19.4112 | 19.5559 | 0.1447
GEN-2022-144 | 03 CENTRAL | 300098 | 5MOCITYB2 | 161 | 19.3839 | 19.5278 | 0.1439
GEN-2022-142 | 03 CENTRAL | 543000 | BLUEVLY5 | 161 | 38.6326 | 38.7732 | 0.1406
GEN-2022-214 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 11.7268 | 11.867 | 0.1402
GEN-2022-073 | 03 CENTRAL | 543027 | RANDLPH5 | 161 | 33.0626 | 33.2021 | 0.1395
GEN-2022-100 | 03 CENTRAL | 541209 | SEDALIA5 | 161 | 9.7362 | 9.8755 | 0.1393
GEN-2022-161 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.1522 | 20.2907 | 0.1385
GEN-2022-073 | 03 CENTRAL | 541212 | KCI 5 | 161 | 12.9239 | 13.0618 | 0.1379
GEN-2022-161 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.0454 | 20.1824 | 0.137
GEN-2022-073 | 03 CENTRAL | 543011 | CHOUTEU5 | 161 | 36.1035 | 36.2392 | 0.1357
GEN-2022-073 | 03 CENTRAL | 543000 | BLUEVLY5 | 161 | 38.639 | 38.7732 | 0.1342
GEN-2022-214 | 03 CENTRAL | 533798 | GILLJCT2 | 69 | 20.2623 | 20.395 | 0.1327
GEN-2022-013 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 15.2366 | 15.3689 | 0.1323
GEN-2022-144 | 03 CENTRAL | 548806 | BLUVLY | 69 | 22.9453 | 23.0772 | 0.1319
GEN-2022-214 | 03 CENTRAL | 533813 | MACARTH2 | 69 | 20.8926 | 21.0243 | 0.1317
GEN-2022-073 | 03 CENTRAL | 543017 | WETHRBY5 | 161 | 16.4516 | 16.5816 | 0.13
GEN-2022-065 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.5287 | 10.6579 | 0.1292
GEN-2022-214 | 03 CENTRAL | 533825 | OATVILL2 | 69 | 19.9849 | 20.1135 | 0.1286
GEN-2022-054 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.7414 | 18.8697 | 0.1283
GEN-2022-073 | 03 CENTRAL | 541215 | HLLMRK 5 | 161 | 13.4853 | 13.6117 | 0.1264
GEN-2022-100 | 03 CENTRAL | 541146 | SEDLIAW_CAP5 | 161 | 9.193 | 9.317 | 0.124
GEN-2022-073 | 03 CENTRAL | 542946 | GLADSTN_CAP5 | 161 | 16.6265 | 16.7488 | 0.1223
GEN-2022-142 | 03 CENTRAL | 541145 | RNRIDGE_CAP5 | 161 | 20.1717 | 20.2937 | 0.122
GEN-2022-073 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 22.8981 | 23.0196 | 0.1215
GEN-2022-214 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 27.0646 | 27.1852 | 0.1206
GEN-2022-161 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.9041 | 14.0247 | 0.1206
GEN-2022-102 | 03 CENTRAL | 541204 | SMTHVL 5 | 161 | 21.7943 | 21.9148 | 0.1205
GEN-2022-073 | 03 CENTRAL | 543025 | LINECRK5 | 161 | 16.8003 | 16.9206 | 0.1203
GEN-2022-214 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.2383 | 11.3557 | 0.1174
GEN-2022-007 | 03 CENTRAL | 533306 | READING3 | 115 | 6.9571 | 7.0744 | 0.1173
GEN-2022-006 | 03 CENTRAL | 533005 | NEPARSN4 | 138 | 12.3748 | 12.4898 | 0.115
GEN-2022-004 | 03 CENTRAL | 533071 | WACO S 4 | 138 | 18.9797 | 19.0946 | 0.1149
GEN-2022-214 | 03 CENTRAL | 533841 | SHERIDN2 | 69 | 20.9828 | 21.0973 | 0.1145
GEN-2022-004 | 03 CENTRAL | 533072 | WACO 4 | 138 | 18.9285 | 19.0426 | 0.1141
GEN-2022-004 | 03 CENTRAL | 533073 | WACO N 4 | 138 | 18.8777 | 18.9911 | 0.1134
GEN-2022-015 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 7.1926 | 7.3053 | 0.1127
GEN-2022-065 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 7.575 | 7.687 | 0.112
GEN-2022-015 | 03 CENTRAL | 640183 | GENTLMN3 | 345 | 14.35 | 14.4618 | 0.1118
GEN-2022-024 | 03 CENTRAL | 767101 | GEN-2022-006 | 161 | 18.5269 | 18.6386 | 0.1117
GEN-2022-065 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 7.5315 | 7.6422 | 0.1107
GEN-2022-214 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.4051 | 10.5153 | 0.1102
GEN-2022-065 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 15.0019 | 15.112 | 0.1101
GEN-2022-024 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 10.7283 | 10.8378 | 0.1095
GEN-2022-004 | 03 CENTRAL | 533796 | GILL W 2 | 69 | 29.0838 | 29.1918 | 0.108
GEN-2022-004 | 03 CENTRAL | 533795 | GILL E 2 | 69 | 29.0761 | 29.184 | 0.1079
GEN-2022-214 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.2372 | 12.3446 | 0.1074
GEN-2022-142 | 03 CENTRAL | 543026 | TIFFANY5 | 161 | 19.8589 | 19.9658 | 0.1069
GEN-2022-007 | 03 CENTRAL | 532776 | READWF 7 | 345 | 13.9185 | 14.0247 | 0.1062
GEN-2022-013 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 22.7144 | 22.8204 | 0.106
GEN-2022-013 | 03 CENTRAL | 533768 | NEOSHON2 | 69 | 22.6908 | 22.7966 | 0.1058
GEN-2022-214 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.1851 | 20.2907 | 0.1056
GEN-2022-214 | 03 CENTRAL | 760284 | GEN-2017-220 | 345 | 20.078 | 20.1824 | 0.1044
GEN-2022-144 | 03 CENTRAL | 543020 | BRMGHAM5 | 161 | 26.3883 | 26.4925 | 0.1042
GEN-2022-161 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 31.2721 | 31.3756 | 0.1035
GEN-2022-073 | 03 CENTRAL | 542982 | IATAN 7 | 345 | 30.1015 | 30.205 | 0.1035
GEN-2022-142 | 03 CENTRAL | 541318 | NCONGRS5 | 161 | 18.5972 | 18.7006 | 0.1034
GEN-2022-161 | 03 CENTRAL | 533041 | EVANS S4 | 138 | 31.1979 | 31.3008 | 0.1029
GEN-2022-144 | 03 CENTRAL | 543011 | CHOUTEU5 | 161 | 36.1365 | 36.2392 | 0.1027
GEN-2022-161 | 03 CENTRAL | 760641 | GEN-2017-226 | 138 | 31.104 | 31.2062 | 0.1022
GEN-2022-214 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 20.3338 | 20.4337 | 0.0999
GEN-2022-100 | 03 CENTRAL | 300117 | 5SEDALA | 161 | 9.0863 | 9.186 | 0.0997
GEN-2022-144 | 03 CENTRAL | 543027 | RANDLPH5 | 161 | 33.1025 | 33.2021 | 0.0996
GEN-2022-073 | 03 CENTRAL | 543021 | RIVRSID5 | 161 | 18.5613 | 18.6606 | 0.0993
GEN-2022-144 | 03 CENTRAL | 542997 | LEEDS 5 | 161 | 34.6057 | 34.7033 | 0.0976
GEN-2022-214 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 18.9112 | 19.0084 | 0.0972
GEN-2022-075 | 03 CENTRAL | 531469 | SPERVIL7 | 345 | 15.0159 | 15.112 | 0.0961
GEN-2022-102 | 03 CENTRAL | 543665 | HAWTHN5 | 161 | 58.9899 | 59.0854 | 0.0955
GEN-2022-065 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 14.2576 | 14.353 | 0.0954
GEN-2022-144 | 03 CENTRAL | 548815 | SUB M | 69 | 21.9729 | 22.0679 | 0.095
GEN-2022-142 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 22.611 | 22.7056 | 0.0946
GEN-2022-024 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 9.9849 | 10.0789 | 0.094
GEN-2022-073 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 28.5625 | 28.6561 | 0.0936
GEN-2022-073 | 03 CENTRAL | 542997 | LEEDS 5 | 161 | 34.611 | 34.7033 | 0.0923
GEN-2022-214 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.2384 | 18.3304 | 0.092
GEN-2022-073 | 03 CENTRAL | 543022 | CLAYCM15 | 161 | 11.3289 | 11.4203 | 0.0914
GEN-2022-142 | 03 CENTRAL | 542997 | LEEDS 5 | 161 | 34.6124 | 34.7033 | 0.0909
GEN-2022-015 | 03 CENTRAL | 640269 | MCCOOK 7 | 115 | 8.615 | 8.7046 | 0.0896
GEN-2022-142 | 03 CENTRAL | 543019 | BARRY 5 | 161 | 18.2988 | 18.3871 | 0.0883
GEN-2022-065 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 13.7255 | 13.8137 | 0.0882
GEN-2022-100 | 03 CENTRAL | 300082 | 5GEORGE | 161 | 8.2353 | 8.3228 | 0.0875
GEN-2022-214 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 11.0673 | 11.1546 | 0.0873
GEN-2022-214 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 9.9134 | 10.0003 | 0.0869
GEN-2022-007 | 03 CENTRAL | 533311 | WMBROSJ3 | 115 | 7.203 | 7.2897 | 0.0867
GEN-2022-075 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.6121 | 8.6982 | 0.0861
GEN-2022-144 | 03 CENTRAL | 548802 | SUB H | 69 | 21.4 | 21.4851 | 0.0851
GEN-2022-161 | 03 CENTRAL | 589060 | GEN-2017-068 | 138 | 28.4089 | 28.494 | 0.0851
GEN-2022-214 | 03 CENTRAL | 533042 | FARBER 4 | 138 | 16.2429 | 16.3278 | 0.0849
GEN-2022-007 | 03 CENTRAL | 533310 | WMBROS 3 | 115 | 7.1261 | 7.2109 | 0.0848
GEN-2022-054 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.3605 | 16.445 | 0.0845
GEN-2022-065 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 10.6708 | 10.7553 | 0.0845
GEN-2022-102 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 28.5717 | 28.6561 | 0.0844
GEN-2022-065 | 03 CENTRAL | 530601 | HEIZER 3 | 115 | 10.6309 | 10.715 | 0.0841
GEN-2022-024 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 15.2854 | 15.3689 | 0.0835
GEN-2022-075 | 03 CENTRAL | 539803 | IRONWOOD7 | 345 | 14.2698 | 14.353 | 0.0832
GEN-2022-214 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 18.9335 | 19.0165 | 0.083
GEN-2022-142 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 22.9377 | 23.0196 | 0.0819
GEN-2022-214 | 03 CENTRAL | 533839 | SENECA 2 | 69 | 17.3901 | 17.4717 | 0.0816
GEN-2022-102 | 03 CENTRAL | 541230 | RNRIDGE5 | 161 | 23.0684 | 23.1489 | 0.0805
GEN-2022-073 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 26.882 | 26.9609 | 0.0789
GEN-2022-144 | 03 CENTRAL | 541248 | LBRTYST5 | 161 | 18.9608 | 19.0379 | 0.0771
GEN-2022-142 | 03 CENTRAL | 541247 | LBRTYWT5 | 161 | 15.2502 | 15.3272 | 0.077
GEN-2022-075 | 03 CENTRAL | 579480 | GEN-2008-124 | 345 | 13.7368 | 13.8137 | 0.0769
GEN-2022-142 | 03 CENTRAL | 769021 | GEN-2022-102 | 161 | 15.1038 | 15.1793 | 0.0755
GEN-2022-065 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.668 | 12.7433 | 0.0753
GEN-2022-142 | 03 CENTRAL | 541221 | PLTCTY 5 | 161 | 15.9584 | 16.033 | 0.0746
GEN-2022-214 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 17.5285 | 17.6031 | 0.0746
GEN-2022-144 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 22.9457 | 23.0196 | 0.0739
GEN-2022-075 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 8.9981 | 9.0719 | 0.0738
GEN-2022-142 | 03 CENTRAL | 541349 | POPE | 161 | 12.8027 | 12.8761 | 0.0734
GEN-2022-073 | 03 CENTRAL | 761383 | G17-183-TAP | 345 | 17.0296 | 17.1028 | 0.0732
GEN-2022-006 | 03 CENTRAL | 764310 | G20-079-TAP | 161 | 17.8978 | 17.9708 | 0.073
GEN-2022-073 | 03 CENTRAL | 546669 | WOLCOTT5 | 161 | 17.8064 | 17.8791 | 0.0727
GEN-2022-142 | 03 CENTRAL | 542944 | BARRY_CAP 5 | 161 | 16.4673 | 16.5387 | 0.0714
GEN-2022-015 | 03 CENTRAL | 640184 | GENTLMN4 | 230 | 18.3488 | 18.4192 | 0.0704
GEN-2022-144 | 03 CENTRAL | 541235 | DUNCAN 5 | 161 | 19.2043 | 19.2742 | 0.0699
GEN-2022-006 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 10.7682 | 10.8378 | 0.0696
GEN-2022-015 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 11.025 | 11.0939 | 0.0689
GEN-2022-142 | 03 CENTRAL | 541214 | TWA 5 | 161 | 15.1992 | 15.268 | 0.0688
GEN-2022-102 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 26.8929 | 26.9609 | 0.068
GEN-2022-054 | 03 CENTRAL | 300949 | 7JASPER | 345 | 12.4584 | 12.5254 | 0.067
GEN-2022-024 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 22.7536 | 22.8204 | 0.0668
GEN-2022-024 | 03 CENTRAL | 533768 | NEOSHON2 | 69 | 22.73 | 22.7966 | 0.0666
GEN-2022-015 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 10.8938 | 10.9602 | 0.0664
GEN-2022-161 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.2641 | 18.3304 | 0.0663
GEN-2022-214 | 03 CENTRAL | 533804 | HAYSVJN2 | 69 | 13.4693 | 13.535 | 0.0657
GEN-2022-214 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 16.9162 | 16.9818 | 0.0656
GEN-2022-075 | 03 CENTRAL | 539815 | IRONWOOD WF7 | 345 | 12.6777 | 12.7433 | 0.0656
GEN-2022-214 | 03 CENTRAL | 533808 | HYDRJN2 | 69 | 15.4168 | 15.4813 | 0.0645
GEN-2022-065 | 03 CENTRAL | 765911 | G21-068-TAP | 345 | 13.4097 | 13.4738 | 0.0641
GEN-2022-144 | 03 CENTRAL | 543116 | BLUEMLS2 | 69 | 7.3315 | 7.3955 | 0.064
GEN-2022-144 | 03 CENTRAL | 548811 | SUB J | 69 | 17.742 | 17.8059 | 0.0639
GEN-2022-142 | 03 CENTRAL | 543021 | RIVRSID5 | 161 | 18.5969 | 18.6606 | 0.0637
GEN-2022-065 | 03 CENTRAL | 765910 | GEN-2021-068 | 345 | 13.3441 | 13.4076 | 0.0635
GEN-2022-065 | 03 CENTRAL | 765920 | GEN-2021-069 | 345 | 13.3441 | 13.4076 | 0.0635
GEN-2022-144 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 20.7937 | 20.8569 | 0.0632
GEN-2022-142 | 03 CENTRAL | 543025 | LINECRK5 | 161 | 16.8575 | 16.9206 | 0.0631
GEN-2022-102 | 03 CENTRAL | 541145 | RNRIDGE_CAP5 | 161 | 20.2318 | 20.2937 | 0.0619
GEN-2022-073 | 03 CENTRAL | 543020 | BRMGHAM5 | 161 | 26.4309 | 26.4925 | 0.0616
GEN-2022-073 | 03 CENTRAL | 548808 | ECKLES-161 | 161 | 25.552 | 25.6133 | 0.0613
GEN-2022-144 | 03 CENTRAL | 541205 | BLSPE 5 | 161 | 20.683 | 20.7442 | 0.0612
GEN-2022-004 | 03 CENTRAL | 533851 | VULCTP 2 | 69 | 21.9609 | 22.0218 | 0.0609
GEN-2022-144 | 03 CENTRAL | 548809 | SHRNKRD | 69 | 18.0575 | 18.1176 | 0.0601
GEN-2022-144 | 03 CENTRAL | 542996 | MIDTOWN5 | 161 | 34.7232 | 34.7832 | 0.06
GEN-2022-144 | 03 CENTRAL | 541244 | ORRICK 5 | 161 | 13.6286 | 13.6884 | 0.0598
GEN-2022-006 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 10.0191 | 10.0789 | 0.0598
GEN-2022-142 | 03 CENTRAL | 543020 | BRMGHAM5 | 161 | 26.4327 | 26.4925 | 0.0598
GEN-2022-004 | 03 CENTRAL | 533805 | HOOVERN2 | 69 | 30.021 | 30.0804 | 0.0594
GEN-2022-004 | 03 CENTRAL | 533806 | HOOVERS2 | 69 | 30.0442 | 30.1036 | 0.0594
GEN-2022-013 | 03 CENTRAL | 300949 | 7JASPER | 345 | 12.4663 | 12.5254 | 0.0591
GEN-2022-073 | 03 CENTRAL | 532772 | STRANGR7 | 345 | 26.8561 | 26.9146 | 0.0585
GEN-2022-144 | 03 CENTRAL | 548800 | SUB I | 69 | 18.3611 | 18.4193 | 0.0582
GEN-2022-006 | 03 CENTRAL | 547469 | RIV4525 | 161 | 24.037 | 24.0948 | 0.0578
GEN-2022-073 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 20.7992 | 20.8569 | 0.0577
GEN-2022-054 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.5481 | 13.6056 | 0.0575
GEN-2022-004 | 03 CENTRAL | 533029 | 59TH ST4 | 138 | 17.0467 | 17.1038 | 0.0571
GEN-2022-142 | 03 CENTRAL | 543017 | WETHRBY5 | 161 | 16.5249 | 16.5816 | 0.0567
GEN-2022-013 | 03 CENTRAL | 533005 | NEPARSN4 | 138 | 12.4337 | 12.4898 | 0.0561
GEN-2022-075 | 03 CENTRAL | 765911 | G21-068-TAP | 345 | 13.4179 | 13.4738 | 0.0559
GEN-2022-075 | 03 CENTRAL | 765920 | GEN-2021-069 | 345 | 13.3522 | 13.4076 | 0.0554
GEN-2022-075 | 03 CENTRAL | 765910 | GEN-2021-068 | 345 | 13.3522 | 13.4076 | 0.0554
GEN-2022-161 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 27.13 | 27.1852 | 0.0552
GEN-2022-006 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 23.5771 | 23.6323 | 0.0552
GEN-2022-015 | 03 CENTRAL | 531464 | SETAB 3 | 115 | 10.3377 | 10.3925 | 0.0548
GEN-2022-006 | 03 CENTRAL | 300739 | 7BLACKBERRY | 345 | 15.3141 | 15.3689 | 0.0548
GEN-2022-065 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.0794 | 6.1341 | 0.0547
GEN-2022-161 | 03 CENTRAL | 533074 | 45TH ST4 | 138 | 23.1168 | 23.1712 | 0.0544
GEN-2022-214 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 11.8139 | 11.8682 | 0.0543
GEN-2022-065 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 12.1092 | 12.1629 | 0.0537
GEN-2022-102 | 03 CENTRAL | 543026 | TIFFANY5 | 161 | 19.9122 | 19.9658 | 0.0536
GEN-2022-142 | 03 CENTRAL | 541250 | SIBLEYPL | 161 | 28.6026 | 28.6561 | 0.0535
GEN-2022-065 | 03 CENTRAL | 763857 | G19-054/068 | 230 | 6.0073 | 6.0606 | 0.0533
GEN-2022-015 | 03 CENTRAL | 530555 | COLBY 3 | 115 | 5.9058 | 5.9589 | 0.0531
GEN-2022-102 | 03 CENTRAL | 541318 | NCONGRS5 | 161 | 18.6477 | 18.7006 | 0.0529
GEN-2022-214 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 8.2493 | 8.3017 | 0.0524
GEN-2022-214 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 8.2493 | 8.3017 | 0.0524
GEN-2022-214 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 8.2493 | 8.3017 | 0.0524
GEN-2022-144 | 03 CENTRAL | 300320 | 5LEVASY | 161 | 10.1587 | 10.2109 | 0.0522
GEN-2022-065 | 03 CENTRAL | 765930 | GEN-2021-070 | 345 | 12.1299 | 12.1815 | 0.0516
GEN-2022-144 | 03 CENTRAL | 541203 | NASHUA 5 | 161 | 29.8388 | 29.89 | 0.0512
GEN-2022-073 | 03 CENTRAL | 541351 | WESTON 5 | 161 | 12.9314 | 12.9826 | 0.0512
GEN-2022-007 | 03 CENTRAL | 533171 | OSAGE J3 | 115 | 5.6264 | 5.6769 | 0.0505
GEN-2022-007 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 12.6315 | 12.6818 | 0.0503
GEN-2022-006 | 03 CENTRAL | 547501 | RIV453 5 | 161 | 22.6711 | 22.7211 | 0.05
GEN-2022-065 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.8307 | 13.8807 | 0.05
GEN-2022-144 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 18.5009 | 18.5509 | 0.05
GEN-2022-075 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.5979 | 10.6478 | 0.0499
GEN-2022-004 | 03 CENTRAL | 533051 | INTERST4 | 138 | 15.5113 | 15.5611 | 0.0498
GEN-2022-100 | 03 CENTRAL | 300500 | 5HUNTSDL | 161 | 10.3013 | 10.3503 | 0.049
GEN-2022-006 | 03 CENTRAL | 547502 | RIV167 5 | 161 | 22.2311 | 22.2801 | 0.049
GEN-2022-102 | 03 CENTRAL | 543029 | SHOLCRK5 | 161 | 18.165 | 18.2139 | 0.0489
GEN-2022-142 | 03 CENTRAL | 542982 | IATAN 7 | 345 | 30.1563 | 30.205 | 0.0487
GEN-2022-102 | 03 CENTRAL | 769821 | GEN-2022-142 | 161 | 18.1056 | 18.1541 | 0.0485
GEN-2022-142 | 03 CENTRAL | 541215 | HLLMRK 5 | 161 | 13.5633 | 13.6117 | 0.0484
GEN-2022-006 | 03 CENTRAL | 764300 | GEN-2020-079 | 161 | 14.8311 | 14.8793 | 0.0482
GEN-2022-054 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 15.4505 | 15.4985 | 0.048
GEN-2022-144 | 03 CENTRAL | 548827 | SUB P | 69 | 15.303 | 15.3509 | 0.0479
GEN-2022-073 | 03 CENTRAL | 541350 | IATAN5 | 161 | 14.9234 | 14.9713 | 0.0479
GEN-2022-102 | 03 CENTRAL | 542980 | NASHUA 7 | 345 | 22.6578 | 22.7056 | 0.0478
GEN-2022-065 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 12.151 | 12.1988 | 0.0478
GEN-2022-161 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 29.8057 | 29.8534 | 0.0477
GEN-2022-054 | 03 CENTRAL | 765350 | GEN-2021-006 | 345 | 15.3979 | 15.4455 | 0.0476
GEN-2022-004 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.1606 | 14.2081 | 0.0475
GEN-2022-100 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 12.5043 | 12.5516 | 0.0473
GEN-2022-004 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 24.2047 | 24.2519 | 0.0472
GEN-2022-161 | 03 CENTRAL | 532770 | MORRIS 7 | 345 | 12.6349 | 12.6818 | 0.0469
GEN-2022-004 | 03 CENTRAL | 533059 | ELPASOE4 | 138 | 24.1639 | 24.2108 | 0.0469
GEN-2022-065 | 03 CENTRAL | 539681 | N-GBEND3 | 115 | 8.0608 | 8.1076 | 0.0468
GEN-2022-075 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 12.1164 | 12.1629 | 0.0465
GEN-2022-102 | 03 CENTRAL | 548808 | ECKLES-161 | 161 | 25.5676 | 25.6133 | 0.0457
GEN-2022-073 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 18.5053 | 18.5509 | 0.0456
GEN-2022-142 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 26.9154 | 26.9609 | 0.0455
GEN-2022-075 | 03 CENTRAL | 765930 | GEN-2021-070 | 345 | 12.1365 | 12.1815 | 0.045
GEN-2022-214 | 03 CENTRAL | 533816 | MIDLAND2 | 69 | 11.7951 | 11.8396 | 0.0445
GEN-2022-004 | 03 CENTRAL | 533850 | VULCAN 2 | 69 | 18.6679 | 18.7124 | 0.0445
GEN-2022-075 | 03 CENTRAL | 530676 | GMEC 3 | 115 | 10.0075 | 10.0516 | 0.0441
GEN-2022-004 | 03 CENTRAL | 533050 | HOOVERS4 | 138 | 16.8376 | 16.8815 | 0.0439
GEN-2022-214 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 11.7789 | 11.8227 | 0.0438
GEN-2022-100 | 03 CENTRAL | 345071 | 5MCBAIN T | 161 | 13.8211 | 13.8649 | 0.0438
GEN-2022-004 | 03 CENTRAL | 533049 | HOOVERN4 | 138 | 16.841 | 16.8848 | 0.0438
GEN-2022-073 | 03 CENTRAL | 541199 | ST JOE 7 | 345 | 19.8563 | 19.9 | 0.0437
GEN-2022-013 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 25.8334 | 25.8771 | 0.0437
GEN-2022-144 | 03 CENTRAL | 548810 | SUB B | 69 | 14.27 | 14.3131 | 0.0431
GEN-2022-214 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.6337 | 11.6765 | 0.0428
GEN-2022-075 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.838 | 13.8807 | 0.0427
GEN-2022-144 | 03 CENTRAL | 541211 | BLSPS 5 | 161 | 19.4144 | 19.4571 | 0.0427
GEN-2022-102 | 03 CENTRAL | 543015 | AVONDAL5 | 161 | 29.8265 | 29.8684 | 0.0419
GEN-2022-075 | 03 CENTRAL | 539695 | SPEARVL6 | 230 | 12.902 | 12.9439 | 0.0419
GEN-2022-102 | 03 CENTRAL | 541349 | POPE | 161 | 12.8343 | 12.8761 | 0.0418
GEN-2022-004 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 24.9955 | 25.0372 | 0.0417
GEN-2022-013 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 25.1657 | 25.2072 | 0.0415
GEN-2022-013 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 25.1657 | 25.2072 | 0.0415
GEN-2022-214 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 10.4051 | 10.4465 | 0.0414
GEN-2022-102 | 03 CENTRAL | 543019 | BARRY 5 | 161 | 18.3457 | 18.3871 | 0.0414
GEN-2022-007 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.3668 | 16.4081 | 0.0413
GEN-2022-075 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 12.1575 | 12.1988 | 0.0413
GEN-2022-054 | 03 CENTRAL | 766141 | G21-096-TAP | 345 | 12.3849 | 12.426 | 0.0411
GEN-2022-102 | 03 CENTRAL | 541221 | PLTCTY 5 | 161 | 15.9919 | 16.033 | 0.0411
GEN-2022-054 | 03 CENTRAL | 766140 | GEN-2021-096 | 345 | 12.3778 | 12.4189 | 0.0411
GEN-2022-013 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 25.0218 | 25.0628 | 0.041
GEN-2022-144 | 03 CENTRAL | 543009 | WINJT N5 | 161 | 23.2864 | 23.3273 | 0.0409
GEN-2022-075 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 13.5177 | 13.5585 | 0.0408
GEN-2022-102 | 03 CENTRAL | 301552 | 5PLATCTY | 161 | 15.9271 | 15.9679 | 0.0408
GEN-2022-065 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.8816 | 9.9223 | 0.0407
GEN-2022-007 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.2495 | 21.2899 | 0.0404
GEN-2022-007 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 13.689 | 13.7294 | 0.0404
GEN-2022-015 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.1671 | 21.2073 | 0.0402
GEN-2022-075 | 03 CENTRAL | 530581 | N HAYS3 | 115 | 9.4618 | 9.5019 | 0.0401
GEN-2022-007 | 03 CENTRAL | 533305 | MORRIS 3 | 115 | 12.4629 | 12.503 | 0.0401
GEN-2022-161 | 03 CENTRAL | 533054 | MAIZE 4 | 138 | 20.394 | 20.4337 | 0.0397
GEN-2022-075 | 03 CENTRAL | 539117 | SPRVILL-EHVB | 230 | 12.563 | 12.6026 | 0.0396
GEN-2022-161 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.3685 | 16.4081 | 0.0396
GEN-2022-004 | 03 CENTRAL | 533798 | GILLJCT2 | 69 | 20.3561 | 20.395 | 0.0389
GEN-2022-004 | 03 CENTRAL | 533813 | MACARTH2 | 69 | 20.9861 | 21.0243 | 0.0382
GEN-2022-065 | 03 CENTRAL | 539666 | GBENDTP3 | 115 | 7.5436 | 7.5816 | 0.038
GEN-2022-004 | 03 CENTRAL | 533825 | OATVILL2 | 69 | 20.0758 | 20.1135 | 0.0377
GEN-2022-065 | 03 CENTRAL | 530609 | HZRNGPL3 | 115 | 7.1158 | 7.1535 | 0.0377
GEN-2022-142 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 20.8193 | 20.8569 | 0.0376
GEN-2022-161 | 03 CENTRAL | 533065 | SG12COL4 | 138 | 18.9791 | 19.0165 | 0.0374
GEN-2022-015 | 03 CENTRAL | 640287 | N.PLATT7 | 115 | 17.8852 | 17.9226 | 0.0374
GEN-2022-161 | 03 CENTRAL | 533075 | VIOLA 4 | 138 | 25 | 25.0372 | 0.0372
GEN-2022-024 | 03 CENTRAL | 300949 | 7JASPER | 345 | 12.4882 | 12.5254 | 0.0372
GEN-2022-100 | 03 CENTRAL | 301489 | 5MCBAINB2 | 161 | 13.2876 | 13.3248 | 0.0372
GEN-2022-100 | 03 CENTRAL | 300501 | 5MCBAINB1 | 161 | 13.2794 | 13.3165 | 0.0371
GEN-2022-073 | 03 CENTRAL | 541400 | EASTOWN7 | 345 | 18.3228 | 18.3598 | 0.037
GEN-2022-100 | 03 CENTRAL | 343004 | 5PERCHE | 161 | 9.1816 | 9.2185 | 0.0369
GEN-2022-144 | 03 CENTRAL | 548801 | SUB K | 69 | 12.9807 | 13.0176 | 0.0369
GEN-2022-161 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 17.5662 | 17.6031 | 0.0369
GEN-2022-004 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 29.8168 | 29.8534 | 0.0366
GEN-2022-144 | 03 CENTRAL | 548830 | SUB R | 69 | 13.5101 | 13.5467 | 0.0366
GEN-2022-100 | 03 CENTRAL | 541337 | WAFBE_SW5 | 161 | 6.5336 | 6.5702 | 0.0366
GEN-2022-013 | 03 CENTRAL | 765571 | G21-029-TAP | 345 | 24.1995 | 24.2359 | 0.0364
GEN-2022-102 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 22.9832 | 23.0196 | 0.0364
GEN-2022-144 | 03 CENTRAL | 548825 | SUB C | 69 | 15.6626 | 15.6988 | 0.0362
GEN-2022-065 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 11.6422 | 11.6783 | 0.0361
GEN-2022-007 | 03 CENTRAL | 533170 | OSAGE 3 | 115 | 4.7524 | 4.7884 | 0.036
GEN-2022-073 | 03 CENTRAL | 548814 | SUB M-161 | 161 | 20.8379 | 20.8737 | 0.0358
GEN-2022-144 | 03 CENTRAL | 543010 | WINJT S5 | 161 | 22.9453 | 22.9811 | 0.0358
GEN-2022-161 | 03 CENTRAL | 533035 | CHISHLM4 | 138 | 20.8798 | 20.9152 | 0.0354
GEN-2022-100 | 03 CENTRAL | 541335 | WAFBW_SW5 | 161 | 6.504 | 6.5394 | 0.0354
GEN-2022-100 | 03 CENTRAL | 300044 | 7MCCRED | 345 | 17.3944 | 17.4298 | 0.0354
GEN-2022-024 | 03 CENTRAL | 533005 | NEPARSN4 | 138 | 12.4545 | 12.4898 | 0.0353
GEN-2022-015 | 03 CENTRAL | 531433 | SCOTCTY3 | 115 | 8.7855 | 8.8207 | 0.0352
GEN-2022-161 | 03 CENTRAL | 533304 | LANG 3 | 115 | 15.7928 | 15.8275 | 0.0347
GEN-2022-065 | 03 CENTRAL | 530582 | S HAYS6 | 230 | 9.0373 | 9.0719 | 0.0346
GEN-2022-065 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.8274 | 9.862 | 0.0346
GEN-2022-100 | 03 CENTRAL | 300541 | 2SEDALI | 69 | 9.9887 | 10.0233 | 0.0346
GEN-2022-065 | 03 CENTRAL | 539661 | 24-FREY3 | 115 | 7.0438 | 7.0781 | 0.0343
GEN-2022-065 | 03 CENTRAL | 539689 | 2ND-KS 3 | 115 | 7.0843 | 7.1186 | 0.0343
GEN-2022-013 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.145 | 9.1793 | 0.0343
GEN-2022-142 | 03 CENTRAL | 761383 | G17-183-TAP | 345 | 17.0685 | 17.1028 | 0.0343
GEN-2022-065 | 03 CENTRAL | 530584 | POSTROCK6 | 230 | 11.573 | 11.6072 | 0.0342
GEN-2022-161 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 24.218 | 24.2519 | 0.0339
GEN-2022-214 | 03 CENTRAL | 533812 | LIN 2 | 69 | 9.2677 | 9.3015 | 0.0338
GEN-2022-015 | 03 CENTRAL | 640286 | N.PLATT4 | 230 | 12.627 | 12.6607 | 0.0337
GEN-2022-073 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 21.9874 | 22.0211 | 0.0337
GEN-2022-102 | 03 CENTRAL | 543016 | GLADSTN5 | 161 | 18.6134 | 18.647 | 0.0336
GEN-2022-161 | 03 CENTRAL | 533047 | GILL 4 | 138 | 21.9642 | 21.9978 | 0.0336
GEN-2022-065 | 03 CENTRAL | 530558 | KNOLL N 6 | 230 | 11.4635 | 11.4969 | 0.0334
GEN-2022-065 | 03 CENTRAL | 530720 | KNOLL S 6 | 230 | 11.4635 | 11.4969 | 0.0334
GEN-2022-004 | 03 CENTRAL | 533038 | COWSKIN4 | 138 | 17.0792 | 17.1124 | 0.0332
GEN-2022-214 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.7528 | 6.786 | 0.0332
GEN-2022-013 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 22.503 | 22.5361 | 0.0331
GEN-2022-075 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.5479 | 8.5808 | 0.0329
GEN-2022-015 | 03 CENTRAL | 530713 | GEM_SW 3 | 115 | 4.8036 | 4.8365 | 0.0329
GEN-2022-004 | 03 CENTRAL | 533034 | CENTENN4 | 138 | 14.4756 | 14.5084 | 0.0328
GEN-2022-073 | 03 CENTRAL | 533283 | 87TH 3 | 115 | 39.2519 | 39.2847 | 0.0328
GEN-2022-075 | 03 CENTRAL | 530695 | CHETOLAH3 | 115 | 8.4991 | 8.5316 | 0.0325
GEN-2022-004 | 03 CENTRAL | 533841 | SHERIDN2 | 69 | 21.0648 | 21.0973 | 0.0325
GEN-2022-142 | 03 CENTRAL | 548814 | SUB M-161 | 161 | 20.8412 | 20.8737 | 0.0325
GEN-2022-013 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 8.894 | 8.9264 | 0.0324
GEN-2022-006 | 03 CENTRAL | 547498 | STL439 5 | 161 | 23.6638 | 23.696 | 0.0322
GEN-2022-161 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.2578 | 21.2899 | 0.0321
GEN-2022-214 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 10.3902 | 10.4221 | 0.0319
GEN-2022-004 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 16.8865 | 16.9182 | 0.0317
GEN-2022-075 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 11.6468 | 11.6783 | 0.0315
GEN-2022-073 | 03 CENTRAL | 532775 | 87TH 7 | 345 | 21.1206 | 21.152 | 0.0314
GEN-2022-073 | 03 CENTRAL | 541248 | LBRTYST5 | 161 | 19.0067 | 19.0379 | 0.0312
GEN-2022-161 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 19.7241 | 19.7552 | 0.0311
GEN-2022-004 | 03 CENTRAL | 771260 | G22-214-TAP | 138 | 14.4529 | 14.4839 | 0.031
GEN-2022-007 | 03 CENTRAL | 533173 | SCRANTN3 | 115 | 5.5125 | 5.5434 | 0.0309
GEN-2022-161 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.063 | 14.0939 | 0.0309
GEN-2022-161 | 03 CENTRAL | 767120 | G22-007-TAP | 115 | 15.0019 | 15.0327 | 0.0308
GEN-2022-004 | 03 CENTRAL | 533856 | WATER2 2 | 69 | 22.7888 | 22.8196 | 0.0308
GEN-2022-100 | 03 CENTRAL | 764355 | G20-072-TAP | 161 | 8.7298 | 8.7603 | 0.0305
GEN-2022-075 | 03 CENTRAL | 587310 | GEN-2016-046 | 345 | 10.5418 | 10.5722 | 0.0304
GEN-2022-100 | 03 CENTRAL | 301443 | 5THMHLB4 | 161 | 29.9606 | 29.9909 | 0.0303
GEN-2022-100 | 03 CENTRAL | 300120 | 5THMHILB1 | 161 | 30.1969 | 30.2272 | 0.0303
GEN-2022-161 | 03 CENTRAL | 767121 | GEN-2022-007 | 115 | 14.8962 | 14.9265 | 0.0303
GEN-2022-073 | 03 CENTRAL | 533268 | STRANGR3 | 115 | 36.2468 | 36.2771 | 0.0303
GEN-2022-004 | 03 CENTRAL | 771261 | GEN-2022-214 | 138 | 14.2884 | 14.3186 | 0.0302
GEN-2022-100 | 03 CENTRAL | 541338 | WAFBE5 | 161 | 5.9353 | 5.9655 | 0.0302
GEN-2022-013 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 9.7466 | 9.7767 | 0.0301
GEN-2022-075 | 03 CENTRAL | 763670 | GEN-2019-030 | 345 | 9.8321 | 9.862 | 0.0299
GEN-2022-142 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 18.5211 | 18.5509 | 0.0298
GEN-2022-100 | 03 CENTRAL | 764345 | GEN-2020-072 | 161 | 8.6501 | 8.6799 | 0.0298
GEN-2022-100 | 03 CENTRAL | 541217 | WINDSR 5 | 161 | 8.7264 | 8.7561 | 0.0297
GEN-2022-214 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.1924 | 16.222 | 0.0296
GEN-2022-142 | 03 CENTRAL | 532772 | STRANGR7 | 345 | 26.885 | 26.9146 | 0.0296
GEN-2022-006 | 03 CENTRAL | 533703 | ORDNJCT2 | 69 | 8.3114 | 8.3409 | 0.0295
GEN-2022-100 | 03 CENTRAL | 541336 | WAFBW5 | 161 | 5.9073 | 5.9366 | 0.0293
GEN-2022-144 | 03 CENTRAL | 300110 | 5PITTSV | 161 | 8.4475 | 8.4768 | 0.0293
GEN-2022-075 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.4184 | 6.4475 | 0.0291
GEN-2022-144 | 03 CENTRAL | 541237 | BLSPW 5 | 161 | 15.0522 | 15.0813 | 0.0291
GEN-2022-100 | 03 CENTRAL | 44888 | J1490_POI | 345 | 17.6099 | 17.6387 | 0.0288
GEN-2022-075 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.3984 | 11.4271 | 0.0287
GEN-2022-161 | 03 CENTRAL | 762922 | GEN-2018-057 | 138 | 16.9531 | 16.9818 | 0.0287
GEN-2022-214 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 11.8506 | 11.8793 | 0.0287
GEN-2022-065 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.0384 | 13.067 | 0.0286
GEN-2022-075 | 03 CENTRAL | 539132 | SPRVILL-EHV2 | 230 | 10.6298 | 10.6579 | 0.0281
GEN-2022-161 | 03 CENTRAL | 533060 | NOEASTE4 | 138 | 19.9373 | 19.9653 | 0.028
GEN-2022-075 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.6005 | 11.6283 | 0.0278
GEN-2022-024 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 25.8496 | 25.8771 | 0.0275
GEN-2022-142 | 03 CENTRAL | 541248 | LBRTYST5 | 161 | 19.0105 | 19.0379 | 0.0274
GEN-2022-161 | 03 CENTRAL | 533038 | COWSKIN4 | 138 | 17.0851 | 17.1124 | 0.0273
GEN-2022-161 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 21.4932 | 21.5205 | 0.0273
GEN-2022-015 | 03 CENTRAL | 640304 | OGALALANPPD7 | 115 | 14.031 | 14.0582 | 0.0272
GEN-2022-013 | 03 CENTRAL | 765200 | G20-090-TAP | 345 | 10.3563 | 10.3835 | 0.0272
GEN-2022-054 | 03 CENTRAL | 532937 | NEOSHO 5 | 161 | 22.6623 | 22.6894 | 0.0271
GEN-2022-015 | 03 CENTRAL | 640253 | KEYSTON7 | 115 | 13.7471 | 13.7742 | 0.0271
GEN-2022-065 | 03 CENTRAL | 530563 | HEIZER 2 | 69 | 8.2376 | 8.2647 | 0.0271
GEN-2022-102 | 03 CENTRAL | 542946 | GLADSTN_CAP5 | 161 | 16.7217 | 16.7488 | 0.0271
GEN-2022-161 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.195 | 16.222 | 0.027
GEN-2022-161 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.195 | 16.222 | 0.027
GEN-2022-144 | 03 CENTRAL | 541215 | HLLMRK 5 | 161 | 13.5847 | 13.6117 | 0.027
GEN-2022-144 | 03 CENTRAL | 543023 | CLAYCM25 | 161 | 13.4378 | 13.4648 | 0.027
GEN-2022-100 | 03 CENTRAL | 300061 | 5BOONE | 161 | 13.8043 | 13.8312 | 0.0269
GEN-2022-015 | 03 CENTRAL | 531501 | BUCKNER7 | 345 | 11.6514 | 11.6783 | 0.0269
GEN-2022-006 | 03 CENTRAL | 547459 | WWR477 | 161 | 21.6162 | 21.643 | 0.0268
GEN-2022-013 | 03 CENTRAL | 764310 | G20-079-TAP | 161 | 17.944 | 17.9708 | 0.0268
GEN-2022-004 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.275 | 23.3018 | 0.0268
GEN-2022-144 | 03 CENTRAL | 543085 | COURTNY2 | 69 | 12.6218 | 12.6485 | 0.0267
GEN-2022-102 | 03 CENTRAL | 541212 | KCI 5 | 161 | 13.0351 | 13.0618 | 0.0267
GEN-2022-054 | 03 CENTRAL | 533021 | NEOSHO 4 | 138 | 24.0192 | 24.0458 | 0.0266
GEN-2022-161 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.2435 | 22.2701 | 0.0266
GEN-2022-054 | 03 CENTRAL | 533020 | NEOSHOS4 | 138 | 23.9814 | 24.0079 | 0.0265
GEN-2022-015 | 03 CENTRAL | 530559 | PH RUN 3 | 115 | 4.4854 | 4.5118 | 0.0264
GEN-2022-006 | 03 CENTRAL | 547467 | ORO110 5 | 161 | 19.3024 | 19.3288 | 0.0264
GEN-2022-100 | 03 CENTRAL | 300043 | 7KINGDM | 345 | 14.8469 | 14.8732 | 0.0263
GEN-2022-144 | 03 CENTRAL | 541226 | GRAINVL5 | 161 | 13.5809 | 13.6072 | 0.0263
GEN-2022-054 | 03 CENTRAL | 533022 | NEOSHON4 | 138 | 23.9084 | 23.9347 | 0.0263
GEN-2022-161 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.0334 | 19.0597 | 0.0263
GEN-2022-073 | 03 CENTRAL | 541235 | DUNCAN 5 | 161 | 19.2479 | 19.2742 | 0.0263
GEN-2022-161 | 03 CENTRAL | 533053 | LAKERDG4 | 138 | 16.892 | 16.9182 | 0.0262
GEN-2022-024 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 25.1811 | 25.2072 | 0.0261
GEN-2022-024 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 25.1811 | 25.2072 | 0.0261
GEN-2022-013 | 03 CENTRAL | 765580 | GEN-2021-030 | 345 | 20.4822 | 20.5083 | 0.0261
GEN-2022-013 | 03 CENTRAL | 765570 | GEN-2021-029 | 345 | 20.4822 | 20.5083 | 0.0261
GEN-2022-144 | 03 CENTRAL | 543165 | SUGRCK_TP_E2 | 69 | 13.6526 | 13.6786 | 0.026
GEN-2022-054 | 03 CENTRAL | 709500 | GI-95_POI | 345 | 11.3778 | 11.4037 | 0.0259
GEN-2022-054 | 03 CENTRAL | 709501 | GI-95_HV | 345 | 11.3778 | 11.4037 | 0.0259
GEN-2022-144 | 03 CENTRAL | 543164 | SUGRCK_TP_W2 | 69 | 13.6879 | 13.7138 | 0.0259
GEN-2022-214 | 03 CENTRAL | 533803 | HAYSV 2 | 69 | 8.5514 | 8.5772 | 0.0258
GEN-2022-024 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 25.037 | 25.0628 | 0.0258
GEN-2022-214 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.5673 | 5.593 | 0.0257
GEN-2022-144 | 03 CENTRAL | 541247 | LBRTYWT5 | 161 | 15.3016 | 15.3272 | 0.0256
GEN-2022-004 | 03 CENTRAL | 533784 | CANALS 2 | 69 | 19.7811 | 19.8065 | 0.0254
GEN-2022-161 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.0913 | 11.1166 | 0.0253
GEN-2022-015 | 03 CENTRAL | 640252 | KEYSTON3 | 345 | 7.0505 | 7.0758 | 0.0253
GEN-2022-006 | 03 CENTRAL | 767241 | GEN-2022-013 | 345 | 6.1454 | 6.1707 | 0.0253
GEN-2022-006 | 03 CENTRAL | 767240 | G22-013-TAP | 345 | 6.147 | 6.1723 | 0.0253
GEN-2022-100 | 03 CENTRAL | 541228 | WBURGE 5 | 161 | 6.3994 | 6.4246 | 0.0252
GEN-2022-006 | 03 CENTRAL | 300949 | 7JASPER | 345 | 12.5003 | 12.5254 | 0.0251
GEN-2022-144 | 03 CENTRAL | 769021 | GEN-2022-102 | 161 | 15.1542 | 15.1793 | 0.0251
GEN-2022-006 | 03 CENTRAL | 588664 | G17-022-TAP | 138 | 8.8161 | 8.8411 | 0.025
GEN-2022-013 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 17.5783 | 17.6031 | 0.0248
GEN-2022-102 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 20.8323 | 20.8569 | 0.0246
GEN-2022-054 | 03 CENTRAL | 300950 | 5JASPER | 161 | 12.4985 | 12.5231 | 0.0246
GEN-2022-006 | 03 CENTRAL | 533001 | ALTOONA4 | 138 | 8.8518 | 8.8764 | 0.0246
GEN-2022-161 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 18.419 | 18.4436 | 0.0246
GEN-2022-161 | 03 CENTRAL | 532863 | MORRIS 6 | 230 | 13.705 | 13.7294 | 0.0244
GEN-2022-144 | 03 CENTRAL | 543089 | SUGRCRK_N2 | 69 | 13.2631 | 13.2875 | 0.0244
GEN-2022-144 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 18.3649 | 18.3892 | 0.0243
GEN-2022-004 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 18.9842 | 19.0084 | 0.0242
GEN-2022-100 | 03 CENTRAL | 300531 | 2GEORGE | 69 | 7.7906 | 7.8147 | 0.0241
GEN-2022-102 | 03 CENTRAL | 542982 | IATAN 7 | 345 | 30.1809 | 30.205 | 0.0241
GEN-2022-015 | 03 CENTRAL | 640082 | BEVERLY7 | 115 | 4.6916 | 4.7156 | 0.024
GEN-2022-073 | 03 CENTRAL | 541225 | PHILL 5 | 161 | 33.8824 | 33.9063 | 0.0239
GEN-2022-007 | 03 CENTRAL | 533158 | 4CORNER3 | 115 | 5.9271 | 5.951 | 0.0239
GEN-2022-214 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 8.9303 | 8.9541 | 0.0238
GEN-2022-161 | 03 CENTRAL | 533049 | HOOVERN4 | 138 | 16.8611 | 16.8848 | 0.0237
GEN-2022-144 | 03 CENTRAL | 543087 | LAKCTYJ2 | 69 | 10.2628 | 10.2865 | 0.0237
GEN-2022-073 | 03 CENTRAL | 548820 | SUB N-161 | 161 | 16.4711 | 16.4948 | 0.0237
GEN-2022-161 | 03 CENTRAL | 533037 | COMOTAR4 | 138 | 18.1428 | 18.1664 | 0.0236
GEN-2022-013 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 8.6656 | 8.6892 | 0.0236
GEN-2022-013 | 03 CENTRAL | 709501 | GI-95_HV | 345 | 11.3802 | 11.4037 | 0.0235
GEN-2022-013 | 03 CENTRAL | 709500 | GI-95_POI | 345 | 11.3802 | 11.4037 | 0.0235
GEN-2022-004 | 03 CENTRAL | 533839 | SENECA 2 | 69 | 17.4484 | 17.4717 | 0.0233
GEN-2022-004 | 03 CENTRAL | 533827 | OSAGE 2 | 69 | 18.7493 | 18.7725 | 0.0232
GEN-2022-100 | 03 CENTRAL | 541271 | SEDN 2 | 69 | 7.1671 | 7.1903 | 0.0232
GEN-2022-100 | 03 CENTRAL | 300530 | 2GEOGT2 | 69 | 7.703 | 7.7262 | 0.0232
GEN-2022-006 | 03 CENTRAL | 588660 | GEN-2017-022 | 138 | 8.4682 | 8.4914 | 0.0232
GEN-2022-004 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 21.4974 | 21.5205 | 0.0231
GEN-2022-024 | 03 CENTRAL | 765571 | G21-029-TAP | 345 | 24.213 | 24.2359 | 0.0229
GEN-2022-073 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 18.3664 | 18.3892 | 0.0228
GEN-2022-013 | 03 CENTRAL | 547469 | RIV4525 | 161 | 24.072 | 24.0948 | 0.0228
GEN-2022-013 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.8469 | 18.8697 | 0.0228
GEN-2022-054 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 25.8545 | 25.8771 | 0.0226
GEN-2022-015 | 03 CENTRAL | 523118 | BUFF_DUNES 7 | 345 | 6.8067 | 6.8291 | 0.0224
GEN-2022-161 | 03 CENTRAL | 533064 | 17TH 4 | 138 | 17.2092 | 17.2316 | 0.0224
GEN-2022-144 | 03 CENTRAL | 543110 | MILCKJT2 | 69 | 11.7138 | 11.7361 | 0.0223
GEN-2022-214 | 03 CENTRAL | 533802 | HAYSVJS2 | 69 | 7.9425 | 7.9648 | 0.0223
GEN-2022-054 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 25.0406 | 25.0628 | 0.0222
GEN-2022-214 | 03 CENTRAL | 539668 | HARPER 4 | 138 | 7.1884 | 7.2106 | 0.0222
GEN-2022-013 | 03 CENTRAL | 300950 | 5JASPER | 161 | 12.501 | 12.5231 | 0.0221
GEN-2022-100 | 03 CENTRAL | 345221 | 5MOBERLY | 161 | 15.1619 | 15.1839 | 0.022
GEN-2022-100 | 03 CENTRAL | 344233 | 5CALIF UE 1 | 161 | 10.2952 | 10.3172 | 0.022
GEN-2022-100 | 03 CENTRAL | 300126 | 5MOBTAP | 161 | 15.1716 | 15.1936 | 0.022
GEN-2022-100 | 03 CENTRAL | 344234 | 5CALIF UE 2 | 161 | 10.2952 | 10.3172 | 0.022
GEN-2022-161 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 18.9865 | 19.0084 | 0.0219
GEN-2022-142 | 03 CENTRAL | 300098 | 5MOCITYB2 | 161 | 19.5059 | 19.5278 | 0.0219
GEN-2022-013 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 23.6105 | 23.6323 | 0.0218
GEN-2022-007 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 23.6724 | 23.6941 | 0.0217
GEN-2022-024 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.1577 | 9.1793 | 0.0216
GEN-2022-015 | 03 CENTRAL | 765911 | G21-068-TAP | 345 | 13.4522 | 13.4738 | 0.0216
GEN-2022-065 | 03 CENTRAL | 765990 | GEN-2021-076 | 345 | 8.2043 | 8.2258 | 0.0215
GEN-2022-214 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 13.7267 | 13.7482 | 0.0215
GEN-2022-065 | 03 CENTRAL | 530583 | POSTROCK7 | 345 | 8.2043 | 8.2258 | 0.0215
GEN-2022-006 | 03 CENTRAL | 547470 | JOP145 5 | 161 | 18.4825 | 18.5039 | 0.0214
GEN-2022-054 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 25.1858 | 25.2072 | 0.0214
GEN-2022-073 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.1933 | 20.2147 | 0.0214
GEN-2022-054 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 25.1858 | 25.2072 | 0.0214
GEN-2022-013 | 03 CENTRAL | 768061 | GEN-2022-054 | 345 | 9.2131 | 9.2345 | 0.0214
GEN-2022-004 | 03 CENTRAL | 533847 | TYLER 2 | 69 | 18.0772 | 18.0985 | 0.0213
GEN-2022-065 | 03 CENTRAL | 768480 | G22-075-TAP | 345 | 7.9104 | 7.9316 | 0.0212
GEN-2022-004 | 03 CENTRAL | 533058 | 47TH ST4 | 138 | 16.85 | 16.8712 | 0.0212
GEN-2022-007 | 03 CENTRAL | 533195 | CARB-KW 3 | 115 | 6.5113 | 6.5324 | 0.0211
GEN-2022-100 | 03 CENTRAL | 541273 | KELHYS 2 | 69 | 6.7974 | 6.8183 | 0.0209
GEN-2022-024 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 22.5153 | 22.5361 | 0.0208
GEN-2022-100 | 03 CENTRAL | 344026 | 5APCH TP | 161 | 10.3678 | 10.3885 | 0.0207
GEN-2022-075 | 03 CENTRAL | 539759 | SPRVL 3 | 115 | 13.0464 | 13.067 | 0.0206
GEN-2022-161 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 23.6735 | 23.6941 | 0.0206
GEN-2022-006 | 03 CENTRAL | 547494 | OAK432 5 | 161 | 17.4724 | 17.493 | 0.0206
GEN-2022-142 | 03 CENTRAL | 541199 | ST JOE 7 | 345 | 19.8794 | 19.9 | 0.0206
GEN-2022-075 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 8.6814 | 8.7019 | 0.0205
GEN-2022-015 | 03 CENTRAL | 530682 | SEGNTP 3 | 115 | 4.2656 | 4.2861 | 0.0205
GEN-2022-100 | 03 CENTRAL | 343052 | 2PERCHE2 | 69 | 14.6705 | 14.6909 | 0.0204
GEN-2022-100 | 03 CENTRAL | 343005 | 2PERCHE | 69 | 14.6705 | 14.6909 | 0.0204
GEN-2022-024 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 8.906 | 8.9264 | 0.0204
GEN-2022-075 | 03 CENTRAL | 764431 | G20-011-SS1 | 345 | 8.6572 | 8.6776 | 0.0204
GEN-2022-075 | 03 CENTRAL | 764420 | GEN-2020-011 | 345 | 8.6662 | 8.6866 | 0.0204
GEN-2022-006 | 03 CENTRAL | 533008 | TV1MNDV4 | 138 | 6.9341 | 6.9544 | 0.0203
GEN-2022-144 | 03 CENTRAL | 543663 | HAWT11_2 | 69 | 13.2833 | 13.3035 | 0.0202
GEN-2022-144 | 03 CENTRAL | 543664 | HAWT12_2 | 69 | 13.2833 | 13.3035 | 0.0202
GEN-2022-013 | 03 CENTRAL | 765190 | GEN-2020-090 | 345 | 8.9874 | 9.0076 | 0.0202
GEN-2022-100 | 03 CENTRAL | 300063 | 5CALIF | 161 | 9.8569 | 9.8771 | 0.0202
GEN-2022-075 | 03 CENTRAL | 764433 | G20-011-SS3 | 345 | 8.5911 | 8.6112 | 0.0201
GEN-2022-075 | 03 CENTRAL | 587350 | GEN-2016-050 | 345 | 5.3231 | 5.3431 | 0.02
GEN-2022-100 | 03 CENTRAL | 541272 | SEDS 2 | 69 | 6.3787 | 6.3987 | 0.02
GEN-2022-100 | 03 CENTRAL | 300529 | 2GEOGT1 | 69 | 7.1302 | 7.1502 | 0.02
GEN-2022-100 | 03 CENTRAL | 301567 | 5NORTONTP | 161 | 6.0441 | 6.0641 | 0.02
GEN-2022-142 | 03 CENTRAL | 532775 | 87TH 7 | 345 | 21.1321 | 21.152 | 0.0199
GEN-2022-214 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.3299 | 5.3498 | 0.0199
GEN-2022-144 | 03 CENTRAL | 344558 | 5MAURER 2 | 161 | 8.0195 | 8.0394 | 0.0199
GEN-2022-144 | 03 CENTRAL | 344557 | 5MAURER 1 | 161 | 8.0195 | 8.0394 | 0.0199
GEN-2022-214 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 15.2816 | 15.3013 | 0.0197
GEN-2022-004 | 03 CENTRAL | 533804 | HAYSVJN2 | 69 | 13.5154 | 13.535 | 0.0196
GEN-2022-015 | 03 CENTRAL | 530717 | ANGELUS | 115 | 4.0161 | 4.0357 | 0.0196
GEN-2022-102 | 03 CENTRAL | 541235 | DUNCAN 5 | 161 | 19.2547 | 19.2742 | 0.0195
GEN-2022-102 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 18.5315 | 18.5509 | 0.0194
GEN-2022-073 | 03 CENTRAL | 541244 | ORRICK 5 | 161 | 13.669 | 13.6884 | 0.0194
GEN-2022-004 | 03 CENTRAL | 533042 | FARBER 4 | 138 | 16.3084 | 16.3278 | 0.0194
GEN-2022-006 | 03 CENTRAL | 547483 | JOP389 5 | 161 | 19.4012 | 19.4205 | 0.0193
GEN-2022-015 | 03 CENTRAL | 530683 | SEGUIN 3 | 115 | 4.0536 | 4.0728 | 0.0192
GEN-2022-100 | 03 CENTRAL | 541274 | PITTCRN2 | 69 | 6.3211 | 6.3403 | 0.0192
GEN-2022-102 | 03 CENTRAL | 543022 | CLAYCM15 | 161 | 11.4011 | 11.4203 | 0.0192
GEN-2022-100 | 03 CENTRAL | 541275 | SEDPLT 2 | 69 | 6.4892 | 6.5083 | 0.0191
GEN-2022-004 | 03 CENTRAL | 533030 | BOEINGE4 | 138 | 16.4784 | 16.4975 | 0.0191
GEN-2022-214 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.2511 | 22.2701 | 0.019
GEN-2022-024 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 9.7578 | 9.7767 | 0.0189
GEN-2022-075 | 03 CENTRAL | 539855 | G-2011-008-2 | 345 | 9.7472 | 9.7661 | 0.0189
GEN-2022-054 | 03 CENTRAL | 765571 | G21-029-TAP | 345 | 24.2171 | 24.2359 | 0.0188
GEN-2022-075 | 03 CENTRAL | 539841 | G-2011-008-1 | 345 | 9.6623 | 9.6811 | 0.0188
GEN-2022-054 | 03 CENTRAL | 532777 | G17-009-TAP | 345 | 10.819 | 10.8378 | 0.0188
GEN-2022-142 | 03 CENTRAL | 541351 | WESTON 5 | 161 | 12.9639 | 12.9826 | 0.0187
GEN-2022-075 | 03 CENTRAL | 539679 | GRTBEND6 | 230 | 7.6683 | 7.687 | 0.0187
GEN-2022-144 | 03 CENTRAL | 541263 | SIBLEY 2 | 69 | 11.3625 | 11.3811 | 0.0186
GEN-2022-007 | 03 CENTRAL | 532803 | BURNS 7 | 345 | 10.6664 | 10.685 | 0.0186
GEN-2022-075 | 03 CENTRAL | 530680 | HEIZER 6 | 230 | 7.6237 | 7.6422 | 0.0185
GEN-2022-065 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.4466 | 18.4651 | 0.0185
GEN-2022-006 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 25.8586 | 25.8771 | 0.0185
GEN-2022-073 | 03 CENTRAL | 541253 | ST JOE 5 | 161 | 20.1936 | 20.212 | 0.0184
GEN-2022-100 | 03 CENTRAL | 300105 | 5NORTON | 161 | 6.5154 | 6.5338 | 0.0184
GEN-2022-004 | 03 CENTRAL | 533808 | HYDRJN2 | 69 | 15.463 | 15.4813 | 0.0183
GEN-2022-075 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 9.049 | 9.0672 | 0.0182
GEN-2022-015 | 03 CENTRAL | 530716 | COLBY_PUMP3 | 115 | 3.5794 | 3.5976 | 0.0182
GEN-2022-100 | 03 CENTRAL | 543064 | NORTON 5 | 161 | 6.5373 | 6.5555 | 0.0182
GEN-2022-142 | 03 CENTRAL | 541350 | IATAN5 | 161 | 14.9531 | 14.9713 | 0.0182
GEN-2022-054 | 03 CENTRAL | 767101 | GEN-2022-006 | 161 | 18.6206 | 18.6386 | 0.018
GEN-2022-102 | 03 CENTRAL | 301563 | 5MOCITYB1 | 161 | 19.538 | 19.5559 | 0.0179
GEN-2022-054 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 22.5182 | 22.5361 | 0.0179
GEN-2022-161 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.3268 | 12.3446 | 0.0178
GEN-2022-102 | 03 CENTRAL | 300098 | 5MOCITYB2 | 161 | 19.51 | 19.5278 | 0.0178
GEN-2022-007 | 03 CENTRAL | 533308 | VAUGHN 3 | 115 | 4.2801 | 4.2979 | 0.0178
GEN-2022-144 | 03 CENTRAL | 543095 | LIBRTYS2 | 69 | 11.93 | 11.9478 | 0.0178
GEN-2022-075 | 03 CENTRAL | 587311 | G16-046XFMR1 | 115 | 15.1255 | 15.1432 | 0.0177
GEN-2022-144 | 03 CENTRAL | 543114 | PLUMRRD2 | 69 | 12.1728 | 12.1905 | 0.0177
GEN-2022-015 | 03 CENTRAL | 763410 | G18-125-TAP | 345 | 7.169 | 7.1867 | 0.0177
GEN-2022-013 | 03 CENTRAL | 764300 | GEN-2020-079 | 161 | 14.8616 | 14.8793 | 0.0177
GEN-2022-006 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 25.1896 | 25.2072 | 0.0176
GEN-2022-006 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 25.1896 | 25.2072 | 0.0176
GEN-2022-075 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 8.7229 | 8.7405 | 0.0176
GEN-2022-065 | 03 CENTRAL | 533416 | RENO 3 | 115 | 22.2525 | 22.2701 | 0.0176
GEN-2022-065 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 17.9322 | 17.9497 | 0.0175
GEN-2022-015 | 03 CENTRAL | 640374 | SWEET W3 | 345 | 9.5487 | 9.5662 | 0.0175
GEN-2022-142 | 03 CENTRAL | 541400 | EASTOWN7 | 345 | 18.3423 | 18.3598 | 0.0175
GEN-2022-065 | 03 CENTRAL | 530702 | BUCKEYE_230 | 230 | 8.6808 | 8.6982 | 0.0174
GEN-2022-006 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 25.0454 | 25.0628 | 0.0174
GEN-2022-102 | 03 CENTRAL | 541205 | BLSPE 5 | 161 | 20.7269 | 20.7442 | 0.0173
GEN-2022-102 | 03 CENTRAL | 761383 | G17-183-TAP | 345 | 17.0855 | 17.1028 | 0.0173
GEN-2022-006 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.4509 | 8.4681 | 0.0172
GEN-2022-006 | 03 CENTRAL | 532934 | MARMTNE5 | 161 | 8.4558 | 8.473 | 0.0172
GEN-2022-013 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.4278 | 16.445 | 0.0172
GEN-2022-102 | 03 CENTRAL | 541244 | ORRICK 5 | 161 | 13.6712 | 13.6884 | 0.0172
GEN-2022-054 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 17.5859 | 17.6031 | 0.0172
GEN-2022-024 | 03 CENTRAL | 765200 | G20-090-TAP | 345 | 10.3664 | 10.3835 | 0.0171
GEN-2022-144 | 03 CENTRAL | 543092 | LAKCTY 2 | 69 | 8.9054 | 8.9225 | 0.0171
GEN-2022-006 | 03 CENTRAL | 547729 | BAX488 5 | 161 | 14.6947 | 14.7118 | 0.0171
GEN-2022-214 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.0997 | 11.1166 | 0.0169
GEN-2022-024 | 03 CENTRAL | 764310 | G20-079-TAP | 161 | 17.954 | 17.9708 | 0.0168
GEN-2022-054 | 03 CENTRAL | 300045 | 7MORGAN | 345 | 13.2163 | 13.2329 | 0.0166
GEN-2022-006 | 03 CENTRAL | 533758 | CRAWFOR2 | 69 | 7.1931 | 7.2097 | 0.0166
GEN-2022-065 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.4612 | 9.4778 | 0.0166
GEN-2022-015 | 03 CENTRAL | 640365 | STOCKVL7 | 115 | 4.4656 | 4.4821 | 0.0165
GEN-2022-065 | 03 CENTRAL | 768481 | GEN-2022-075 | 345 | 7.0018 | 7.0182 | 0.0164
GEN-2022-004 | 03 CENTRAL | 533824 | OAKLAWN2 | 69 | 15.195 | 15.2114 | 0.0164
GEN-2022-065 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 9.3995 | 9.4159 | 0.0164
GEN-2022-024 | 03 CENTRAL | 765580 | GEN-2021-030 | 345 | 20.4919 | 20.5083 | 0.0164
GEN-2022-024 | 03 CENTRAL | 765570 | GEN-2021-029 | 345 | 20.4919 | 20.5083 | 0.0164
GEN-2022-065 | 03 CENTRAL | 530568 | GB NTH 2 | 69 | 6.4365 | 6.4528 | 0.0163
GEN-2022-100 | 03 CENTRAL | 344041 | 5LOYMART 2 | 161 | 10.1607 | 10.1769 | 0.0162
GEN-2022-054 | 03 CENTRAL | 532778 | GEN-2017-009 | 345 | 10.0627 | 10.0789 | 0.0162
GEN-2022-100 | 03 CENTRAL | 344040 | 5LOYMART 1 | 161 | 10.1607 | 10.1769 | 0.0162
GEN-2022-015 | 03 CENTRAL | 531412 | GRINNEL3 | 115 | 3.6776 | 3.6937 | 0.0161
GEN-2022-065 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.2432 | 17.2593 | 0.0161
GEN-2022-015 | 03 CENTRAL | 531485 | CNTRLPL3 | 115 | 5.9338 | 5.9498 | 0.016
GEN-2022-015 | 03 CENTRAL | 763406 | GEN-2018-125 | 345 | 6.8174 | 6.8334 | 0.016
GEN-2022-073 | 03 CENTRAL | 543023 | CLAYCM25 | 161 | 13.4488 | 13.4648 | 0.016
GEN-2022-100 | 03 CENTRAL | 762383 | ASG-2018-007 | 161 | 11.5335 | 11.5494 | 0.0159
GEN-2022-004 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 17.5872 | 17.6031 | 0.0159
GEN-2022-100 | 03 CENTRAL | 543062 | SALSBRY5 | 161 | 11.5443 | 11.5601 | 0.0158
GEN-2022-075 | 03 CENTRAL | 539857 | G-2011-008-3 | 345 | 8.8654 | 8.8812 | 0.0158
GEN-2022-142 | 03 CENTRAL | 533268 | STRANGR3 | 115 | 36.2613 | 36.2771 | 0.0158
GEN-2022-142 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 18.3735 | 18.3892 | 0.0157
GEN-2022-065 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.6119 | 8.6276 | 0.0157
GEN-2022-054 | 03 CENTRAL | 533062 | ROSEHIL4 | 138 | 29.8378 | 29.8534 | 0.0156
GEN-2022-015 | 03 CENTRAL | 531504 | CIMWD2 7 | 345 | 9.0516 | 9.0672 | 0.0156
GEN-2022-013 | 03 CENTRAL | 300045 | 7MORGAN | 345 | 13.2173 | 13.2329 | 0.0156
GEN-2022-024 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 17.5875 | 17.6031 | 0.0156
GEN-2022-102 | 03 CENTRAL | 543004 | BLUMILS5 | 161 | 17.8449 | 17.8605 | 0.0156
GEN-2022-102 | 03 CENTRAL | 769861 | GEN-2022-144 | 161 | 17.7876 | 17.8031 | 0.0155
GEN-2022-142 | 03 CENTRAL | 543023 | CLAYCM25 | 161 | 13.4493 | 13.4648 | 0.0155
GEN-2022-161 | 03 CENTRAL | 533413 | CIRCLE 3 | 115 | 18.4496 | 18.4651 | 0.0155
GEN-2022-006 | 03 CENTRAL | 765571 | G21-029-TAP | 345 | 24.2205 | 24.2359 | 0.0154
GEN-2022-006 | 03 CENTRAL | 547466 | ATL109 5 | 161 | 15.9068 | 15.9222 | 0.0154
GEN-2022-073 | 03 CENTRAL | 761376 | GEN-2017-183 | 345 | 8.5558 | 8.5711 | 0.0153
GEN-2022-006 | 03 CENTRAL | 533696 | LABETTS2 | 69 | 6.0714 | 6.0867 | 0.0153
GEN-2022-161 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.613 | 27.6283 | 0.0153
GEN-2022-006 | 03 CENTRAL | 533003 | LIBERTY4 | 138 | 7.2764 | 7.2916 | 0.0152
GEN-2022-161 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.5372 | 27.5524 | 0.0152
GEN-2022-161 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 27.4567 | 27.4719 | 0.0152
GEN-2022-015 | 03 CENTRAL | 531351 | BREWSTR3 | 115 | 3.0799 | 3.0951 | 0.0152
GEN-2022-006 | 03 CENTRAL | 533702 | ORDNCE 2 | 69 | 6.0088 | 6.0239 | 0.0151
GEN-2022-054 | 03 CENTRAL | 532791 | BENTON 7 | 345 | 18.3154 | 18.3304 | 0.015
GEN-2022-015 | 03 CENTRAL | 531502 | CIMRRN 7 | 345 | 8.7255 | 8.7405 | 0.015
GEN-2022-024 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 8.6743 | 8.6892 | 0.0149
GEN-2022-214 | 03 CENTRAL | 539002 | BLF-CRK4 | 138 | 4.6862 | 4.7011 | 0.0149
GEN-2022-075 | 03 CENTRAL | 539678 | GRTBEND3 | 115 | 10.7404 | 10.7553 | 0.0149
GEN-2022-006 | 03 CENTRAL | 547490 | FIR417 5 | 161 | 14.0448 | 14.0596 | 0.0148
GEN-2022-161 | 03 CENTRAL | 533786 | CHISHLM2 | 69 | 19.5317 | 19.5465 | 0.0148
GEN-2022-004 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.0791 | 14.0939 | 0.0148
GEN-2022-007 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.6135 | 27.6283 | 0.0148
GEN-2022-024 | 03 CENTRAL | 709500 | GI-95_POI | 345 | 11.389 | 11.4037 | 0.0147
GEN-2022-024 | 03 CENTRAL | 709501 | GI-95_HV | 345 | 11.389 | 11.4037 | 0.0147
GEN-2022-161 | 03 CENTRAL | 533421 | HEC GT 3 | 115 | 17.935 | 17.9497 | 0.0147
GEN-2022-161 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 9.783 | 9.7976 | 0.0146
GEN-2022-073 | 03 CENTRAL | 541147 | ST JOE_CAP5 | 161 | 17.9874 | 18.002 | 0.0146
GEN-2022-161 | 03 CENTRAL | 763417 | GEN-2018-128 | 345 | 11.1401 | 11.1546 | 0.0145
GEN-2022-024 | 03 CENTRAL | 547469 | RIV4525 | 161 | 24.0804 | 24.0948 | 0.0144
GEN-2022-214 | 03 CENTRAL | 533573 | CRESWLS2 | 69 | 12.9363 | 12.9506 | 0.0143
GEN-2022-214 | 03 CENTRAL | 533543 | CRESWLN2 | 69 | 12.9399 | 12.9542 | 0.0143
GEN-2022-024 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.8554 | 18.8697 | 0.0143
GEN-2022-144 | 03 CENTRAL | 541236 | RICHMND5 | 161 | 7.7444 | 7.7586 | 0.0142
GEN-2022-013 | 03 CENTRAL | 533703 | ORDNJCT2 | 69 | 8.3267 | 8.3409 | 0.0142
GEN-2022-015 | 03 CENTRAL | 640265 | MALONEY7 | 115 | 10.9981 | 11.0122 | 0.0141
GEN-2022-006 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.1652 | 9.1793 | 0.0141
GEN-2022-065 | 03 CENTRAL | 530561 | KNOLL 3 | 115 | 10.6337 | 10.6478 | 0.0141
GEN-2022-006 | 03 CENTRAL | 766260 | GEN-2020-007 | 345 | 22.5221 | 22.5361 | 0.014
GEN-2022-006 | 03 CENTRAL | 533002 | DEARING4 | 138 | 9.1832 | 9.1972 | 0.014
GEN-2022-015 | 03 CENTRAL | 640270 | MCCOOK 8 | 69 | 4.4192 | 4.4332 | 0.014
GEN-2022-102 | 03 CENTRAL | 532772 | STRANGR7 | 345 | 26.9006 | 26.9146 | 0.014
GEN-2022-073 | 03 CENTRAL | 533244 | JARBALO3 | 115 | 26.6853 | 26.6992 | 0.0139
GEN-2022-024 | 03 CENTRAL | 300950 | 5JASPER | 161 | 12.5092 | 12.5231 | 0.0139
GEN-2022-161 | 03 CENTRAL | 533309 | WEMPORI3 | 115 | 11.0234 | 11.0372 | 0.0138
GEN-2022-214 | 03 CENTRAL | 539001 | ANTHONY4 | 138 | 5.005 | 5.0188 | 0.0138
GEN-2022-013 | 03 CENTRAL | 547498 | STL439 5 | 161 | 23.6823 | 23.696 | 0.0137
GEN-2022-073 | 03 CENTRAL | 541401 | EASTOWN5 | 161 | 17.2623 | 17.276 | 0.0137
GEN-2022-024 | 03 CENTRAL | 547503 | RIV452T 5 | 161 | 23.6186 | 23.6323 | 0.0137
GEN-2022-015 | 03 CENTRAL | 531445 | GRDNCTY3 | 115 | 12.5537 | 12.5674 | 0.0137
GEN-2022-161 | 03 CENTRAL | 533419 | HEC 3 | 115 | 17.2457 | 17.2593 | 0.0136
GEN-2022-102 | 03 CENTRAL | 548807 | BLUVLY-161 | 161 | 18.5909 | 18.6044 | 0.0135
GEN-2022-054 | 03 CENTRAL | 765580 | GEN-2021-030 | 345 | 20.4948 | 20.5083 | 0.0135
GEN-2022-054 | 03 CENTRAL | 765570 | GEN-2021-029 | 345 | 20.4948 | 20.5083 | 0.0135
GEN-2022-161 | 03 CENTRAL | 533036 | CLEARWT4 | 138 | 14.1947 | 14.2081 | 0.0134
GEN-2022-024 | 03 CENTRAL | 768061 | GEN-2022-054 | 345 | 9.2211 | 9.2345 | 0.0134
GEN-2022-144 | 03 CENTRAL | 543088 | BLUSPRG2 | 69 | 8.0194 | 8.0327 | 0.0133
GEN-2022-006 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 8.9131 | 8.9264 | 0.0133
GEN-2022-004 | 03 CENTRAL | 533032 | BU11PON4 | 138 | 14.7376 | 14.7509 | 0.0133
GEN-2022-007 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.2886 | 23.3018 | 0.0132
GEN-2022-214 | 03 CENTRAL | 533830 | PECK 2 | 69 | 6.3303 | 6.3434 | 0.0131
GEN-2022-100 | 03 CENTRAL | 345088 | 7MCCREDIE | 345 | 6.5486 | 6.5616 | 0.013
GEN-2022-073 | 03 CENTRAL | 541258 | WOODBIN5 | 161 | 16.9227 | 16.9357 | 0.013
GEN-2022-065 | 03 CENTRAL | 539692 | SEWARD 3 | 115 | 5.3237 | 5.3367 | 0.013
GEN-2022-004 | 03 CENTRAL | 533816 | MIDLAND2 | 69 | 11.8266 | 11.8396 | 0.013
GEN-2022-024 | 03 CENTRAL | 765190 | GEN-2020-090 | 345 | 8.9949 | 9.0076 | 0.0127
GEN-2022-013 | 03 CENTRAL | 588664 | G17-022-TAP | 138 | 8.8284 | 8.8411 | 0.0127
GEN-2022-065 | 03 CENTRAL | 530587 | WSPRTTP2 | 69 | 5.7012 | 5.7139 | 0.0127
GEN-2022-006 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 9.7642 | 9.7767 | 0.0125
GEN-2022-004 | 03 CENTRAL | 533810 | HYDRJS2 | 69 | 12.5326 | 12.5451 | 0.0125
GEN-2022-161 | 03 CENTRAL | 533301 | EAST ST3 | 115 | 9.9684 | 9.9809 | 0.0125
GEN-2022-006 | 03 CENTRAL | 547472 | TIP292 5 | 161 | 17.0916 | 17.1041 | 0.0125
GEN-2022-161 | 03 CENTRAL | 533307 | PRAIRIE3 | 115 | 10.0954 | 10.1079 | 0.0125
GEN-2022-214 | 03 CENTRAL | 532803 | BURNS 7 | 345 | 10.6726 | 10.685 | 0.0124
GEN-2022-075 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.238 | 5.2504 | 0.0124
GEN-2022-006 | 03 CENTRAL | 533766 | LITCH S2 | 69 | 12.5239 | 12.5362 | 0.0123
GEN-2022-075 | 03 CENTRAL | 763850 | G19-055-TAP | 230 | 6.8854 | 6.8977 | 0.0123
GEN-2022-161 | 03 CENTRAL | 532852 | JEC 6 | 230 | 24.7204 | 24.7327 | 0.0123
GEN-2022-161 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2052 | 7.2174 | 0.0122
GEN-2022-161 | 03 CENTRAL | 771260 | G22-214-TAP | 138 | 14.4717 | 14.4839 | 0.0122
GEN-2022-102 | 03 CENTRAL | 541211 | BLSPS 5 | 161 | 19.4449 | 19.4571 | 0.0122
GEN-2022-100 | 03 CENTRAL | 300049 | 7THOMHL | 345 | 14.2739 | 14.286 | 0.0121
GEN-2022-015 | 03 CENTRAL | 531432 | PILE 3 | 115 | 6.3841 | 6.3962 | 0.0121
GEN-2022-004 | 03 CENTRAL | 533807 | HYDRA N2 | 69 | 12.2195 | 12.2315 | 0.012
GEN-2022-006 | 03 CENTRAL | 547487 | HOC404 5 | 161 | 13.0549 | 13.0669 | 0.012
GEN-2022-075 | 03 CENTRAL | 768280 | G22-065-TAP | 230 | 6.757 | 6.769 | 0.012
GEN-2022-075 | 03 CENTRAL | 763846 | G19-053/055 | 230 | 6.7928 | 6.8048 | 0.012
GEN-2022-100 | 03 CENTRAL | 301494 | 5HIGBEEB2 | 161 | 12.2451 | 12.257 | 0.0119
GEN-2022-161 | 03 CENTRAL | 771261 | GEN-2022-214 | 138 | 14.3067 | 14.3186 | 0.0119
GEN-2022-015 | 03 CENTRAL | 640083 | BEVERLY8 | 69 | 4.271 | 4.2829 | 0.0119
GEN-2022-075 | 03 CENTRAL | 588630 | GEN-2017-018 | 345 | 16.2102 | 16.222 | 0.0118
GEN-2022-075 | 03 CENTRAL | 531449 | HOLCOMB7 | 345 | 11.0821 | 11.0939 | 0.0118
GEN-2022-075 | 03 CENTRAL | 539801 | THISTLE7 | 345 | 16.2102 | 16.222 | 0.0118
GEN-2022-065 | 03 CENTRAL | 530553 | S HAYS 3 | 115 | 8.569 | 8.5808 | 0.0118
GEN-2022-214 | 03 CENTRAL | 532981 | CRESWLN4 | 138 | 8.4705 | 8.4822 | 0.0117
GEN-2022-161 | 03 CENTRAL | 533182 | TECHILE3 | 115 | 24.5165 | 24.5282 | 0.0117
GEN-2022-013 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.5939 | 13.6056 | 0.0117
GEN-2022-015 | 03 CENTRAL | 640302 | OGALALA4 | 230 | 7.4841 | 7.4958 | 0.0117
GEN-2022-006 | 03 CENTRAL | 547477 | CJ 366 5 | 161 | 12.178 | 12.1896 | 0.0116
GEN-2022-161 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 17.2594 | 17.271 | 0.0116
GEN-2022-214 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.3226 | 6.3341 | 0.0115
GEN-2022-006 | 03 CENTRAL | 765200 | G20-090-TAP | 345 | 10.3721 | 10.3835 | 0.0114
GEN-2022-013 | 03 CENTRAL | 547467 | ORO110 5 | 161 | 19.3174 | 19.3288 | 0.0114
GEN-2022-075 | 03 CENTRAL | 523853 | FINNEY 7 | 345 | 10.9489 | 10.9602 | 0.0113
GEN-2022-161 | 03 CENTRAL | 533305 | MORRIS 3 | 115 | 12.4917 | 12.503 | 0.0113
GEN-2022-144 | 03 CENTRAL | 543093 | LAKCTYK2 | 69 | 7.4855 | 7.4967 | 0.0112
GEN-2022-073 | 03 CENTRAL | 541254 | EAST 5 | 161 | 15.6707 | 15.6819 | 0.0112
GEN-2022-161 | 03 CENTRAL | 532773 | SUMMIT 7 | 345 | 10.9116 | 10.9228 | 0.0112
GEN-2022-006 | 03 CENTRAL | 532794 | ROSEHIL7 | 345 | 17.5919 | 17.6031 | 0.0112
GEN-2022-006 | 03 CENTRAL | 547539 | JOP145 2 | 69 | 20.3631 | 20.3742 | 0.0111
GEN-2022-054 | 03 CENTRAL | 532986 | BENTON 4 | 138 | 27.1741 | 27.1852 | 0.0111
GEN-2022-007 | 03 CENTRAL | 583859 | GEN-2014-001 | 345 | 8.4859 | 8.497 | 0.0111
GEN-2022-161 | 03 CENTRAL | 533015 | BENTLEY4 | 138 | 10.569 | 10.5801 | 0.0111
GEN-2022-006 | 03 CENTRAL | 765580 | GEN-2021-030 | 345 | 20.4972 | 20.5083 | 0.0111
GEN-2022-006 | 03 CENTRAL | 765570 | GEN-2021-029 | 345 | 20.4972 | 20.5083 | 0.0111
GEN-2022-024 | 03 CENTRAL | 764300 | GEN-2020-079 | 161 | 14.8682 | 14.8793 | 0.0111
GEN-2022-100 | 03 CENTRAL | 344677 | 5GUTHRIE 1 | 161 | 10.6919 | 10.7029 | 0.011
GEN-2022-054 | 03 CENTRAL | 533778 | NEOSHOS2 | 69 | 22.8095 | 22.8204 | 0.0109
GEN-2022-024 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.4341 | 16.445 | 0.0109
GEN-2022-006 | 03 CENTRAL | 533876 | FRANKLIN2 | 69 | 10.9453 | 10.9562 | 0.0109
GEN-2022-065 | 03 CENTRAL | 530693 | VINETAP3 | 115 | 8.5752 | 8.5861 | 0.0109
GEN-2022-065 | 03 CENTRAL | 530695 | CHETOLAH3 | 115 | 8.5207 | 8.5316 | 0.0109
GEN-2022-015 | 03 CENTRAL | 531362 | MANNGT 3 | 115 | 4.9873 | 4.9982 | 0.0109
GEN-2022-054 | 03 CENTRAL | 533768 | NEOSHON2 | 69 | 22.7857 | 22.7966 | 0.0109
GEN-2022-144 | 03 CENTRAL | 541232 | LEX161 5 | 161 | 7.5052 | 7.516 | 0.0108
GEN-2022-006 | 03 CENTRAL | 510422 | COFFEYT4 | 138 | 9.76 | 9.7708 | 0.0108
GEN-2022-015 | 03 CENTRAL | 531379 | JONES3 | 115 | 10.5988 | 10.6095 | 0.0107
GEN-2022-161 | 03 CENTRAL | 765340 | GEN-2021-005 | 345 | 10.6841 | 10.6948 | 0.0107
GEN-2022-013 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.1834 | 25.1941 | 0.0107
GEN-2022-013 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 23.7168 | 23.7273 | 0.0105
GEN-2022-102 | 03 CENTRAL | 541199 | ST JOE 7 | 345 | 19.8895 | 19.9 | 0.0105
GEN-2022-144 | 03 CENTRAL | 541262 | LIBERTY2 | 69 | 9.6557 | 9.6662 | 0.0105
GEN-2022-006 | 03 CENTRAL | 709501 | GI-95_HV | 345 | 11.3933 | 11.4037 | 0.0104
GEN-2022-006 | 03 CENTRAL | 709500 | GI-95_POI | 345 | 11.3933 | 11.4037 | 0.0104
GEN-2022-075 | 03 CENTRAL | 539694 | SPEARVL3 | 115 | 9.9119 | 9.9223 | 0.0104
GEN-2022-065 | 03 CENTRAL | 530679 | SEWRDMW3 | 115 | 4.7436 | 4.754 | 0.0104
GEN-2022-073 | 03 CENTRAL | 541256 | IND PRK5 | 161 | 15.1537 | 15.1641 | 0.0104
GEN-2022-006 | 03 CENTRAL | 533004 | MONTGOM4 | 138 | 6.9295 | 6.9398 | 0.0103
GEN-2022-006 | 03 CENTRAL | 532932 | LITCH 5 | 161 | 8.8272 | 8.8375 | 0.0103
GEN-2022-054 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 23.7171 | 23.7273 | 0.0102
GEN-2022-100 | 03 CENTRAL | 541202 | SIBLEY 5 | 161 | 26.9508 | 26.9609 | 0.0101
GEN-2022-013 | 03 CENTRAL | 512650 | GRDA1 7 | 345 | 26.0506 | 26.0607 | 0.0101
GEN-2022-004 | 03 CENTRAL | 533812 | LIN 2 | 69 | 9.2914 | 9.3015 | 0.0101
GEN-2022-073 | 03 CENTRAL | 300039 | 7FAIRPT | 345 | 12.3322 | 12.3423 | 0.0101
GEN-2022-102 | 03 CENTRAL | 541351 | WESTON 5 | 161 | 12.9726 | 12.9826 | 0.01
GEN-2022-006 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.8597 | 18.8697 | 0.01
GEN-2022-015 | 03 CENTRAL | 640255 | KINGSLY7 | 115 | 8.6802 | 8.6902 | 0.01
GEN-2022-214 | 03 CENTRAL | 532985 | TCROCK 4 | 138 | 5.8705 | 5.8804 | 0.0099
GEN-2022-013 | 03 CENTRAL | 533008 | TV1MNDV4 | 138 | 6.9445 | 6.9544 | 0.0099
GEN-2022-006 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 8.6794 | 8.6892 | 0.0098
GEN-2022-013 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.6185 | 27.6283 | 0.0098
GEN-2022-024 | 03 CENTRAL | 300045 | 7MORGAN | 345 | 13.2231 | 13.2329 | 0.0098
GEN-2022-075 | 03 CENTRAL | 640066 | AXTELL 7 | 115 | 13.9237 | 13.9335 | 0.0098
GEN-2022-006 | 03 CENTRAL | 300950 | 5JASPER | 161 | 12.5134 | 12.5231 | 0.0097
GEN-2022-013 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 27.4622 | 27.4719 | 0.0097
GEN-2022-100 | 03 CENTRAL | 541201 | SIBLEY 7 | 345 | 20.8472 | 20.8569 | 0.0097
GEN-2022-013 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.5427 | 27.5524 | 0.0097
GEN-2022-015 | 03 CENTRAL | 531353 | GOODLND3 | 115 | 2.6386 | 2.6483 | 0.0097
GEN-2022-006 | 03 CENTRAL | 533704 | PARSONS2 | 69 | 4.8336 | 4.8433 | 0.0097
GEN-2022-102 | 03 CENTRAL | 541350 | IATAN5 | 161 | 14.9616 | 14.9713 | 0.0097
GEN-2022-161 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.1964 | 13.206 | 0.0096
GEN-2022-015 | 03 CENTRAL | 530554 | ATWOOD 3 | 115 | 2.978 | 2.9876 | 0.0096
GEN-2022-006 | 03 CENTRAL | 533772 | SE1GREE2 | 69 | 6.0043 | 6.0139 | 0.0096
GEN-2022-161 | 03 CENTRAL | 533151 | AUBURN 3 | 115 | 21.051 | 21.0606 | 0.0096
GEN-2022-006 | 03 CENTRAL | 547541 | RIV167 2 | 69 | 17.2157 | 17.2253 | 0.0096
GEN-2022-054 | 03 CENTRAL | 512650 | GRDA1 7 | 345 | 26.0512 | 26.0607 | 0.0095
GEN-2022-015 | 03 CENTRAL | 531443 | GODLNDT3 | 115 | 2.6248 | 2.6343 | 0.0095
GEN-2022-006 | 03 CENTRAL | 547462 | SVRCK469 5 | 161 | 13.8654 | 13.8749 | 0.0095
GEN-2022-075 | 03 CENTRAL | 763862 | G19-054-TAP | 230 | 6.1246 | 6.1341 | 0.0095
GEN-2022-161 | 03 CENTRAL | 515543 | RENFROW7 | 345 | 11.8588 | 11.8682 | 0.0094
GEN-2022-144 | 03 CENTRAL | 300091 | 5LATHRP | 161 | 8.6183 | 8.6277 | 0.0094
GEN-2022-065 | 03 CENTRAL | 530722 | VINEDE_S | 115 | 7.8701 | 7.8795 | 0.0094
GEN-2022-161 | 03 CENTRAL | 560053 | G15052_T | 345 | 11.2954 | 11.3048 | 0.0094
GEN-2022-144 | 03 CENTRAL | 300124 | 5HOLDENB2 | 161 | 7.5119 | 7.5212 | 0.0093
GEN-2022-161 | 03 CENTRAL | 562900 | G15052_1 | 345 | 11.2495 | 11.2588 | 0.0093
GEN-2022-102 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 18.3799 | 18.3892 | 0.0093
GEN-2022-006 | 03 CENTRAL | 547525 | JOP 59 2 | 69 | 19.1124 | 19.1217 | 0.0093
GEN-2022-144 | 03 CENTRAL | 301561 | 5HOLDENB1 | 161 | 7.5081 | 7.5174 | 0.0093
GEN-2022-214 | 03 CENTRAL | 532783 | KINGMAN7 | 345 | 7.2081 | 7.2174 | 0.0093
GEN-2022-161 | 03 CENTRAL | 533335 | MCDOWEL3 | 115 | 18.4803 | 18.4895 | 0.0092
GEN-2022-054 | 03 CENTRAL | 301622 | 5MORGANXF2 | 161 | 18.59 | 18.5992 | 0.0092
GEN-2022-075 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 4.1646 | 4.1738 | 0.0092
GEN-2022-075 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.743 | 6.7521 | 0.0091
GEN-2022-006 | 03 CENTRAL | 532938 | FRANKLIN5 | 161 | 7.7083 | 7.7174 | 0.0091
GEN-2022-006 | 03 CENTRAL | 547526 | JOP 64 2 | 69 | 18.7639 | 18.773 | 0.0091
GEN-2022-004 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 11.858 | 11.867 | 0.009
GEN-2022-161 | 03 CENTRAL | 539638 | FLATRDG4 | 138 | 15.2923 | 15.3013 | 0.009
GEN-2022-006 | 03 CENTRAL | 768061 | GEN-2022-054 | 345 | 9.2255 | 9.2345 | 0.009
GEN-2022-015 | 03 CENTRAL | 530644 | COLBY 2 | 69 | 3.4786 | 3.4875 | 0.0089
GEN-2022-006 | 03 CENTRAL | 588504 | G17-005-TAP | 161 | 6.8858 | 6.8947 | 0.0089
GEN-2022-024 | 03 CENTRAL | 533703 | ORDNJCT2 | 69 | 8.332 | 8.3409 | 0.0089
GEN-2022-102 | 03 CENTRAL | 541400 | EASTOWN7 | 345 | 18.3509 | 18.3598 | 0.0089
GEN-2022-214 | 03 CENTRAL | 533558 | TIMBJCT2 | 69 | 8.6713 | 8.6801 | 0.0088
GEN-2022-075 | 03 CENTRAL | 530551 | SALINE 3 | 115 | 4.8314 | 4.8402 | 0.0088
GEN-2022-013 | 03 CENTRAL | 512865 | GREC TAP5 | 345 | 24.8829 | 24.8917 | 0.0088
GEN-2022-015 | 03 CENTRAL | 640200 | GR ISLD4 | 230 | 15.6655 | 15.6743 | 0.0088
GEN-2022-214 | 03 CENTRAL | 587884 | G16-111-TAP | 345 | 9.7889 | 9.7976 | 0.0087
GEN-2022-075 | 03 CENTRAL | 768281 | GEN-2022-065 | 230 | 5.8014 | 5.8101 | 0.0087
GEN-2022-144 | 03 CENTRAL | 300304 | 2MOCITY | 69 | 9.2113 | 9.22 | 0.0087
GEN-2022-015 | 03 CENTRAL | 659800 | GRANTNB_-TS7 | 115 | 6.1464 | 6.1551 | 0.0087
GEN-2022-142 | 03 CENTRAL | 541253 | ST JOE 5 | 161 | 20.2033 | 20.212 | 0.0087
GEN-2022-013 | 03 CENTRAL | 766141 | G21-096-TAP | 345 | 12.4173 | 12.426 | 0.0087
GEN-2022-073 | 03 CENTRAL | 541257 | COOK 5 | 161 | 14.0294 | 14.038 | 0.0086
GEN-2022-006 | 03 CENTRAL | 588500 | GEN-2017-005 | 161 | 6.8001 | 6.8087 | 0.0086
GEN-2022-024 | 03 CENTRAL | 547498 | STL439 5 | 161 | 23.6874 | 23.696 | 0.0086
GEN-2022-161 | 03 CENTRAL | 588360 | GEN-2016-153 | 345 | 8.2932 | 8.3017 | 0.0085
GEN-2022-015 | 03 CENTRAL | 640100 | CAMBRIG7 | 115 | 4.1247 | 4.1332 | 0.0085
GEN-2022-161 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 8.2932 | 8.3017 | 0.0085
GEN-2022-161 | 03 CENTRAL | 589240 | GEN-2017-086 | 345 | 8.2932 | 8.3017 | 0.0085
GEN-2022-006 | 03 CENTRAL | 533697 | LIBERT-2 | 69 | 8.3172 | 8.3257 | 0.0085
GEN-2022-004 | 03 CENTRAL | 763421 | G18-128-TAP | 345 | 12.3361 | 12.3446 | 0.0085
GEN-2022-006 | 03 CENTRAL | 765190 | GEN-2020-090 | 345 | 8.9991 | 9.0076 | 0.0085
GEN-2022-161 | 03 CENTRAL | 533336 | GEARY 3 | 115 | 19.1122 | 19.1207 | 0.0085
GEN-2022-161 | 03 CENTRAL | 766240 | GEN-2021-107 | 345 | 15.0544 | 15.0628 | 0.0084
GEN-2022-161 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 13.709 | 13.7174 | 0.0084
GEN-2022-102 | 03 CENTRAL | 541237 | BLSPW 5 | 161 | 15.0729 | 15.0813 | 0.0084
GEN-2022-100 | 03 CENTRAL | 541535 | LAMONTETP | 69 | 4.8731 | 4.8815 | 0.0084
GEN-2022-013 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.5 | 40.5083 | 0.0083
GEN-2022-006 | 03 CENTRAL | 547574 | JOP341 2 | 69 | 17.6265 | 17.6348 | 0.0083
GEN-2022-161 | 03 CENTRAL | 539008 | MILAN_GOAB | 138 | 11.8587 | 11.867 | 0.0083
GEN-2022-054 | 03 CENTRAL | 512865 | GREC TAP5 | 345 | 24.8835 | 24.8917 | 0.0082
GEN-2022-100 | 03 CENTRAL | 300057 | 5BARNET | 161 | 9.2418 | 9.2499 | 0.0081
GEN-2022-144 | 03 CENTRAL | 300036 | 5MPLTAP | 161 | 8.594 | 8.6021 | 0.0081
GEN-2022-161 | 03 CENTRAL | 532851 | AUBURN 6 | 230 | 13.2357 | 13.2438 | 0.0081
GEN-2022-100 | 03 CENTRAL | 344028 | 5APCH FLT | 161 | 8.187 | 8.195 | 0.008
GEN-2022-015 | 03 CENTRAL | 531428 | LEOTI 3 | 115 | 4.2268 | 4.2348 | 0.008
GEN-2022-006 | 03 CENTRAL | 547534 | ORO110 2 | 69 | 17.4712 | 17.4792 | 0.008
GEN-2022-015 | 03 CENTRAL | 653571 | GR ISLD3 | 345 | 11.3839 | 11.3919 | 0.008
GEN-2022-013 | 03 CENTRAL | 512656 | GRDA1 5 | 161 | 42.4176 | 42.4256 | 0.008
GEN-2022-006 | 03 CENTRAL | 543650 | DAKOTA_5 | 161 | 7.6588 | 7.6668 | 0.008
GEN-2022-024 | 03 CENTRAL | 588664 | G17-022-TAP | 138 | 8.8331 | 8.8411 | 0.008
GEN-2022-100 | 03 CENTRAL | 541536 | LAMONTE | 69 | 4.724 | 4.7319 | 0.0079
GEN-2022-013 | 03 CENTRAL | 533758 | CRAWFOR2 | 69 | 7.2018 | 7.2097 | 0.0079
GEN-2022-015 | 03 CENTRAL | 764420 | GEN-2020-011 | 345 | 8.6787 | 8.6866 | 0.0079
GEN-2022-015 | 03 CENTRAL | 640065 | AXTELL 3 | 345 | 8.694 | 8.7019 | 0.0079
GEN-2022-054 | 03 CENTRAL | 532796 | WICHITA7 | 345 | 23.2939 | 23.3018 | 0.0079
GEN-2022-075 | 03 CENTRAL | 640374 | SWEET W3 | 345 | 9.5584 | 9.5662 | 0.0078
GEN-2022-161 | 03 CENTRAL | 532784 | NINN1WF7 | 345 | 5.9842 | 5.992 | 0.0078
GEN-2022-015 | 03 CENTRAL | 653871 | GR ISLD-LNX3 | 345 | 11.2726 | 11.2804 | 0.0078
GEN-2022-214 | 03 CENTRAL | 766141 | G21-096-TAP | 345 | 12.4182 | 12.426 | 0.0078
GEN-2022-144 | 03 CENTRAL | 344923 | 5LATHROP | 161 | 8.42 | 8.4278 | 0.0078
GEN-2022-004 | 03 CENTRAL | 533803 | HAYSV 2 | 69 | 8.5695 | 8.5772 | 0.0077
GEN-2022-100 | 03 CENTRAL | 541414 | SIB REA1 | 345 | 18.5432 | 18.5509 | 0.0077
GEN-2022-065 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.6035 | 6.6112 | 0.0077
GEN-2022-013 | 03 CENTRAL | 300741 | 5SPORTSMAN | 161 | 39.1489 | 39.1566 | 0.0077
GEN-2022-161 | 03 CENTRAL | 532797 | WOLFCRK7 | 345 | 18.8621 | 18.8697 | 0.0076
GEN-2022-004 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.3481 | 11.3557 | 0.0076
GEN-2022-075 | 03 CENTRAL | 530599 | SMKYP2 6 | 230 | 6.2366 | 6.2442 | 0.0076
GEN-2022-006 | 03 CENTRAL | 547602 | RIV406 2 | 69 | 15.2712 | 15.2788 | 0.0076
GEN-2022-006 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.4374 | 16.445 | 0.0076
GEN-2022-054 | 03 CENTRAL | 533039 | ELPASO 4 | 138 | 24.2444 | 24.2519 | 0.0075
GEN-2022-013 | 03 CENTRAL | 533003 | LIBERTY4 | 138 | 7.2841 | 7.2916 | 0.0075
GEN-2022-102 | 03 CENTRAL | 541226 | GRAINVL5 | 161 | 13.5998 | 13.6072 | 0.0074
GEN-2022-073 | 03 CENTRAL | 640139 | COOPER 3 | 345 | 26.0776 | 26.085 | 0.0074
GEN-2022-054 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 9.7693 | 9.7767 | 0.0074
GEN-2022-006 | 03 CENTRAL | 300045 | 7MORGAN | 345 | 13.2255 | 13.2329 | 0.0074
GEN-2022-013 | 03 CENTRAL | 533696 | LABETTS2 | 69 | 6.0793 | 6.0867 | 0.0074
GEN-2022-013 | 03 CENTRAL | 533702 | ORDNCE 2 | 69 | 6.0165 | 6.0239 | 0.0074
GEN-2022-024 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.5982 | 13.6056 | 0.0074
GEN-2022-054 | 03 CENTRAL | 533059 | ELPASOE4 | 138 | 24.2034 | 24.2108 | 0.0074
GEN-2022-161 | 03 CENTRAL | 539009 | CONWAY | 138 | 11.3484 | 11.3557 | 0.0073
GEN-2022-161 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 10.781 | 10.7883 | 0.0073
GEN-2022-004 | 03 CENTRAL | 533793 | ELPASO 2 | 69 | 11.6077 | 11.615 | 0.0073
GEN-2022-214 | 03 CENTRAL | 583859 | GEN-2014-001 | 345 | 8.4897 | 8.497 | 0.0073
GEN-2022-161 | 03 CENTRAL | 515646 | GRNTWD 7 | 345 | 10.4393 | 10.4465 | 0.0072
GEN-2022-142 | 03 CENTRAL | 761376 | GEN-2017-183 | 345 | 8.5639 | 8.5711 | 0.0072
GEN-2022-024 | 03 CENTRAL | 547467 | ORO110 5 | 161 | 19.3216 | 19.3288 | 0.0072
GEN-2022-065 | 03 CENTRAL | 530602 | LAXTAP 3 | 115 | 3.9737 | 3.9809 | 0.0072
GEN-2022-054 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.1721 | 9.1793 | 0.0072
GEN-2022-054 | 03 CENTRAL | 300741 | 5SPORTSMAN | 161 | 39.1494 | 39.1566 | 0.0072
GEN-2022-100 | 03 CENTRAL | 300550 | 2CALIF | 69 | 8.3839 | 8.391 | 0.0071
GEN-2022-161 | 03 CENTRAL | 764375 | GEN-2020-058 | 345 | 22.1584 | 22.1655 | 0.0071
GEN-2022-161 | 03 CENTRAL | 542940 | ATLNTIC7 | 345 | 22.2055 | 22.2126 | 0.0071
GEN-2022-161 | 03 CENTRAL | 765115 | GEN-2020-057 | 345 | 22.1586 | 22.1656 | 0.007
GEN-2022-161 | 03 CENTRAL | 532987 | BUTLER 4 | 138 | 10.7317 | 10.7387 | 0.007
GEN-2022-004 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.5083 | 10.5153 | 0.007
GEN-2022-065 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.3514 | 6.3584 | 0.007
GEN-2022-054 | 03 CENTRAL | 300794 | 5LAMAR | 161 | 8.531 | 8.538 | 0.007
GEN-2022-015 | 03 CENTRAL | 531364 | ATWODSW3 | 115 | 2.6473 | 2.6543 | 0.007
GEN-2022-065 | 03 CENTRAL | 532872 | EMCPHER6 | 230 | 7.8267 | 7.8337 | 0.007
GEN-2022-013 | 03 CENTRAL | 547729 | BAX488 5 | 161 | 14.7048 | 14.7118 | 0.007
GEN-2022-161 | 03 CENTRAL | 532800 | LATHAMS7 | 345 | 9.7698 | 9.7767 | 0.0069
GEN-2022-015 | 03 CENTRAL | 640167 | ENDERS 7 | 115 | 3.6946 | 3.7015 | 0.0069
GEN-2022-214 | 03 CENTRAL | 514804 | MIDLTNT4 | 138 | 8.0461 | 8.053 | 0.0069
GEN-2022-144 | 03 CENTRAL | 543091 | DUNCNRD2 | 69 | 6.364 | 6.3709 | 0.0069
GEN-2022-015 | 03 CENTRAL | 531411 | GOVE 3 | 115 | 2.739 | 2.7458 | 0.0068
GEN-2022-054 | 03 CENTRAL | 532781 | CANEYWF7 | 345 | 8.9196 | 8.9264 | 0.0068
GEN-2022-065 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.1992 | 13.206 | 0.0068
GEN-2022-004 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.6697 | 11.6765 | 0.0068
GEN-2022-054 | 03 CENTRAL | 532991 | WEAVER 4 | 138 | 21.5137 | 21.5205 | 0.0068
GEN-2022-073 | 03 CENTRAL | 301559 | 5FAIRPTXF3 | 161 | 16.5736 | 16.5803 | 0.0067
GEN-2022-004 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 11.816 | 11.8227 | 0.0067
GEN-2022-013 | 03 CENTRAL | 532934 | MARMTNE5 | 161 | 8.4663 | 8.473 | 0.0067
GEN-2022-013 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.4614 | 8.4681 | 0.0067
GEN-2022-015 | 03 CENTRAL | 640066 | AXTELL 7 | 115 | 13.9268 | 13.9335 | 0.0067
GEN-2022-214 | 03 CENTRAL | 539000 | RAGO 4 | 138 | 3.9396 | 3.9463 | 0.0067
GEN-2022-075 | 03 CENTRAL | 539771 | NFTDODG3 | 115 | 9.4711 | 9.4778 | 0.0067
GEN-2022-013 | 03 CENTRAL | 301348 | 5CHOTEAU2 | 161 | 40.6563 | 40.663 | 0.0067
GEN-2022-024 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.1874 | 25.1941 | 0.0067
GEN-2022-161 | 03 CENTRAL | 532767 | GEARY 7 | 345 | 10.0753 | 10.0819 | 0.0066
GEN-2022-065 | 03 CENTRAL | 533417 | EMCPHER3 | 115 | 11.2906 | 11.2972 | 0.0066
GEN-2022-073 | 03 CENTRAL | 541263 | SIBLEY 2 | 69 | 11.3745 | 11.3811 | 0.0066
GEN-2022-013 | 03 CENTRAL | 300794 | 5LAMAR | 161 | 8.5314 | 8.538 | 0.0066
GEN-2022-075 | 03 CENTRAL | 539671 | FTDODGE3 | 115 | 9.4093 | 9.4159 | 0.0066
GEN-2022-006 | 03 CENTRAL | 533639 | MARMATN2 | 69 | 8.7219 | 8.7285 | 0.0066
GEN-2022-006 | 03 CENTRAL | 533672 | ALTAMNS2 | 69 | 3.9973 | 4.0039 | 0.0066
GEN-2022-006 | 03 CENTRAL | 533695 | LABETTE2 | 69 | 4.0094 | 4.016 | 0.0066
GEN-2022-075 | 03 CENTRAL | 530593 | SMKYP1 6 | 230 | 5.8863 | 5.8929 | 0.0066
GEN-2022-024 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 23.7207 | 23.7273 | 0.0066
GEN-2022-161 | 03 CENTRAL | 533250 | LWRNCHL3 | 115 | 27.8968 | 27.9033 | 0.0065
GEN-2022-161 | 03 CENTRAL | 539676 | MILAN 4 | 138 | 10.5088 | 10.5153 | 0.0065
GEN-2022-004 | 03 CENTRAL | 533802 | HAYSVJS2 | 69 | 7.9583 | 7.9648 | 0.0065
GEN-2022-161 | 03 CENTRAL | 533279 | ATLNTIC3 | 115 | 37.5025 | 37.5089 | 0.0064
GEN-2022-142 | 03 CENTRAL | 541401 | EASTOWN5 | 161 | 17.2696 | 17.276 | 0.0064
GEN-2022-054 | 03 CENTRAL | 512656 | GRDA1 5 | 161 | 42.4192 | 42.4256 | 0.0064
GEN-2022-024 | 03 CENTRAL | 512650 | GRDA1 7 | 345 | 26.0543 | 26.0607 | 0.0064
GEN-2022-161 | 03 CENTRAL | 533016 | WWUPLNT4 | 138 | 8.0167 | 8.0231 | 0.0064
GEN-2022-100 | 03 CENTRAL | 300545 | 2SYLVAN | 69 | 4.7312 | 4.7376 | 0.0064
GEN-2022-015 | 03 CENTRAL | 640194 | GOSPER 7 | 115 | 4.3075 | 4.3139 | 0.0064
GEN-2022-015 | 03 CENTRAL | 523823 | CARPENTER 7 | 345 | 7.1306 | 7.137 | 0.0064
GEN-2022-161 | 03 CENTRAL | 532857 | TECHILL6 | 230 | 10.6662 | 10.6726 | 0.0064
GEN-2022-161 | 03 CENTRAL | 533011 | HALSTD 4 | 138 | 8.1736 | 8.18 | 0.0064
GEN-2022-054 | 03 CENTRAL | 533040 | EVANS N4 | 138 | 31.3692 | 31.3756 | 0.0064
GEN-2022-015 | 03 CENTRAL | 531488 | BVERVLLY | 115 | 2.3849 | 2.3912 | 0.0063
GEN-2022-073 | 03 CENTRAL | 533259 | NW LEAV3 | 115 | 16.8837 | 16.89 | 0.0063
GEN-2022-006 | 03 CENTRAL | 547556 | OAK280 2 | 69 | 15.4668 | 15.473 | 0.0062
GEN-2022-161 | 03 CENTRAL | 532765 | HOYT 7 | 345 | 15.9745 | 15.9807 | 0.0062
GEN-2022-214 | 03 CENTRAL | 533559 | UDALL 2 | 69 | 7.3522 | 7.3584 | 0.0062
GEN-2022-024 | 03 CENTRAL | 533008 | TV1MNDV4 | 138 | 6.9482 | 6.9544 | 0.0062
GEN-2022-054 | 03 CENTRAL | 512648 | MAID 5 | 161 | 42.8575 | 42.8637 | 0.0062
GEN-2022-024 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 27.4658 | 27.4719 | 0.0061
GEN-2022-024 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.5463 | 27.5524 | 0.0061
GEN-2022-073 | 03 CENTRAL | 532765 | HOYT 7 | 345 | 15.9746 | 15.9807 | 0.0061
GEN-2022-054 | 03 CENTRAL | 767240 | G22-013-TAP | 345 | 6.1662 | 6.1723 | 0.0061
GEN-2022-161 | 03 CENTRAL | 533597 | MIDIANW2 | 69 | 13.9371 | 13.9432 | 0.0061
GEN-2022-161 | 03 CENTRAL | 587880 | GEN-2016-111 | 345 | 6.502 | 6.5081 | 0.0061
GEN-2022-006 | 03 CENTRAL | 533688 | DEARING2 | 69 | 7.892 | 7.8981 | 0.0061
GEN-2022-075 | 03 CENTRAL | 640312 | PAULINE3 | 345 | 7.5163 | 7.5224 | 0.0061
GEN-2022-054 | 03 CENTRAL | 767241 | GEN-2022-013 | 345 | 6.1646 | 6.1707 | 0.0061
GEN-2022-054 | 03 CENTRAL | 300069 | 5CHOTEAU1 | 161 | 40.6569 | 40.663 | 0.0061
GEN-2022-054 | 03 CENTRAL | 301348 | 5CHOTEAU2 | 161 | 40.6569 | 40.663 | 0.0061
GEN-2022-054 | 03 CENTRAL | 549984 | BROOKLINE 7 | 345 | 11.4482 | 11.4543 | 0.0061
GEN-2022-024 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.6222 | 27.6283 | 0.0061
GEN-2022-065 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 9.6749 | 9.6809 | 0.006
GEN-2022-161 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.1881 | 25.1941 | 0.006
GEN-2022-006 | 03 CENTRAL | 512656 | GRDA1 5 | 161 | 42.4196 | 42.4256 | 0.006
GEN-2022-144 | 03 CENTRAL | 301310 | 5REX | 161 | 9.1568 | 9.1628 | 0.006
GEN-2022-006 | 03 CENTRAL | 512650 | GRDA1 7 | 345 | 26.0548 | 26.0607 | 0.0059
GEN-2022-065 | 03 CENTRAL | 539684 | OTISSUB3 | 115 | 2.8216 | 2.8275 | 0.0059
GEN-2022-054 | 03 CENTRAL | 533005 | NEPARSN4 | 138 | 12.4839 | 12.4898 | 0.0059
GEN-2022-075 | 03 CENTRAL | 532873 | SUMMIT 6 | 230 | 13.2001 | 13.206 | 0.0059
GEN-2022-015 | 03 CENTRAL | 640500 | THEDFRD3 | 345 | 4.791 | 4.7969 | 0.0059
GEN-2022-054 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 8.6834 | 8.6892 | 0.0058
GEN-2022-100 | 03 CENTRAL | 541534 | KNOSTERTP | 69 | 4.7463 | 4.7521 | 0.0058
GEN-2022-065 | 03 CENTRAL | 530608 | NEKOMA 3 | 115 | 3.8598 | 3.8656 | 0.0058
GEN-2022-015 | 03 CENTRAL | 587680 | GEN-2016-074 | 345 | 5.4816 | 5.4874 | 0.0058
GEN-2022-214 | 03 CENTRAL | 533541 | AKRON 2 | 69 | 7.0771 | 7.0829 | 0.0058
GEN-2022-065 | 03 CENTRAL | 539696 | ST-JOHN3 | 115 | 4.9136 | 4.9194 | 0.0058
GEN-2022-006 | 03 CENTRAL | 547608 | JOP430 2 | 69 | 15.3881 | 15.3939 | 0.0058
GEN-2022-006 | 03 CENTRAL | 300740 | 7SPORTSMAN | 345 | 23.7215 | 23.7273 | 0.0058
GEN-2022-006 | 03 CENTRAL | 533762 | GIR JCT2 | 69 | 6.3711 | 6.3768 | 0.0057
GEN-2022-102 | 03 CENTRAL | 543023 | CLAYCM25 | 161 | 13.4591 | 13.4648 | 0.0057
GEN-2022-161 | 03 CENTRAL | 542981 | LACYGNE7 | 345 | 25.8714 | 25.8771 | 0.0057
GEN-2022-161 | 03 CENTRAL | 766141 | G21-096-TAP | 345 | 12.4204 | 12.426 | 0.0056
GEN-2022-161 | 03 CENTRAL | 766140 | GEN-2021-096 | 345 | 12.4133 | 12.4189 | 0.0056
GEN-2022-161 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 9.9947 | 10.0003 | 0.0056
GEN-2022-004 | 03 CENTRAL | 539675 | MILANTP4 | 138 | 9.9947 | 10.0003 | 0.0056
GEN-2022-075 | 03 CENTRAL | 531448 | HOLCOMB3 | 115 | 21.2017 | 21.2073 | 0.0056
GEN-2022-054 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.1885 | 25.1941 | 0.0056
GEN-2022-024 | 03 CENTRAL | 766141 | G21-096-TAP | 345 | 12.4205 | 12.426 | 0.0055
GEN-2022-161 | 03 CENTRAL | 532801 | ELKRVR17 | 345 | 8.6837 | 8.6892 | 0.0055
GEN-2022-015 | 03 CENTRAL | 640381 | THEDFRD7 | 115 | 8.4397 | 8.4452 | 0.0055
GEN-2022-006 | 03 CENTRAL | 533680 | CHRYJCT2 | 69 | 6.747 | 6.7525 | 0.0055
GEN-2022-073 | 03 CENTRAL | 533272 | THORNTN3 | 115 | 15.858 | 15.8635 | 0.0055
GEN-2022-024 | 03 CENTRAL | 512865 | GREC TAP5 | 345 | 24.8862 | 24.8917 | 0.0055
GEN-2022-073 | 03 CENTRAL | 541262 | LIBERTY2 | 69 | 9.6607 | 9.6662 | 0.0055
GEN-2022-161 | 03 CENTRAL | 543629 | LACYGNE11_7 | 345 | 25.2018 | 25.2072 | 0.0054
GEN-2022-161 | 03 CENTRAL | 532799 | WAVERLY7 | 345 | 16.4396 | 16.445 | 0.0054
GEN-2022-075 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.2853 | 20.2907 | 0.0054
GEN-2022-161 | 03 CENTRAL | 543632 | LACYGNE22_7 | 345 | 25.2018 | 25.2072 | 0.0054
GEN-2022-161 | 03 CENTRAL | 533163 | HOYT 3 | 115 | 22.535 | 22.5404 | 0.0054
GEN-2022-100 | 03 CENTRAL | 992003 | VSC2_3 | 345 | 6.7916 | 6.797 | 0.0054
GEN-2022-065 | 03 CENTRAL | 530603 | LACROS 3 | 115 | 3.4613 | 3.4667 | 0.0054
GEN-2022-161 | 03 CENTRAL | 532792 | FR2EAST7 | 345 | 6.7806 | 6.786 | 0.0054
GEN-2022-161 | 03 CENTRAL | 766261 | G20-007-TAP | 345 | 25.0574 | 25.0628 | 0.0054
GEN-2022-161 | 03 CENTRAL | 532984 | SUMNER 4 | 138 | 11.8174 | 11.8227 | 0.0053
GEN-2022-015 | 03 CENTRAL | 640366 | STOCKVL8 | 69 | 3.2492 | 3.2545 | 0.0053
GEN-2022-015 | 03 CENTRAL | 640093 | C.CREEK4 | 230 | 6.9255 | 6.9308 | 0.0053
GEN-2022-007 | 03 CENTRAL | 533302 | EEUREKA3 | 115 | 4.1244 | 4.1297 | 0.0053
GEN-2022-161 | 03 CENTRAL | 515476 | HUNTERS7 | 345 | 11.874 | 11.8793 | 0.0053
GEN-2022-161 | 03 CENTRAL | 532780 | CANEYRV7 | 345 | 9.174 | 9.1793 | 0.0053
GEN-2022-102 | 03 CENTRAL | 300320 | 5LEVASY | 161 | 10.2056 | 10.2109 | 0.0053
GEN-2022-054 | 03 CENTRAL | 533024 | 29TH 4 | 138 | 19.0544 | 19.0597 | 0.0053
GEN-2022-161 | 03 CENTRAL | 533306 | READING3 | 115 | 7.0691 | 7.0744 | 0.0053
GEN-2022-161 | 03 CENTRAL | 533063 | SC10BEL4 | 138 | 11.6712 | 11.6765 | 0.0053
GEN-2022-024 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.5031 | 40.5083 | 0.0052
GEN-2022-075 | 03 CENTRAL | 539804 | THISTLE4 | 138 | 17.2658 | 17.271 | 0.0052
GEN-2022-214 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.9496 | 16.9548 | 0.0052
GEN-2022-006 | 03 CENTRAL | 532802 | WAVERTX7 | 345 | 13.6004 | 13.6056 | 0.0052
GEN-2022-075 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.4215 | 3.4267 | 0.0052
GEN-2022-100 | 03 CENTRAL | 542972 | HAWTH 7 | 345 | 23.0144 | 23.0196 | 0.0052
GEN-2022-054 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.5473 | 27.5524 | 0.0051
GEN-2022-006 | 03 CENTRAL | 512865 | GREC TAP5 | 345 | 24.8866 | 24.8917 | 0.0051
GEN-2022-161 | 03 CENTRAL | 539800 | CLARKCOUNTY7 | 345 | 13.8756 | 13.8807 | 0.0051
GEN-2022-006 | 03 CENTRAL | 547592 | JOP389 2 | 69 | 14.896 | 14.9011 | 0.0051
GEN-2022-102 | 03 CENTRAL | 541263 | SIBLEY 2 | 69 | 11.376 | 11.3811 | 0.0051
GEN-2022-161 | 03 CENTRAL | 532785 | PRATTWF7 | 345 | 4.9592 | 4.9643 | 0.0051
GEN-2022-075 | 03 CENTRAL | 640313 | PAULINE7 | 115 | 15.7198 | 15.7249 | 0.0051
GEN-2022-006 | 03 CENTRAL | 533647 | UN1ELSM2 | 69 | 7.8232 | 7.8283 | 0.0051
GEN-2022-006 | 03 CENTRAL | 542968 | STILWEL7 | 345 | 25.189 | 25.1941 | 0.0051
GEN-2022-054 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.6232 | 27.6283 | 0.0051
GEN-2022-004 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 10.4171 | 10.4221 | 0.005
GEN-2022-024 | 03 CENTRAL | 533758 | CRAWFOR2 | 69 | 7.2047 | 7.2097 | 0.005
GEN-2022-054 | 03 CENTRAL | 532988 | BELAIRE4 | 138 | 18.4386 | 18.4436 | 0.005
GEN-2022-161 | 03 CENTRAL | 765571 | G21-029-TAP | 345 | 24.2309 | 24.2359 | 0.005
GEN-2022-024 | 03 CENTRAL | 512656 | GRDA1 5 | 161 | 42.4206 | 42.4256 | 0.005
GEN-2022-161 | 03 CENTRAL | 533429 | MOUNDRG3 | 115 | 8.4093 | 8.4142 | 0.0049
GEN-2022-024 | 03 CENTRAL | 300741 | 5SPORTSMAN | 161 | 39.1517 | 39.1566 | 0.0049
GEN-2022-054 | 03 CENTRAL | 533068 | STEARMN4 | 138 | 19.0035 | 19.0084 | 0.0049
GEN-2022-013 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.2098 | 20.2147 | 0.0049
GEN-2022-054 | 03 CENTRAL | 532782 | BUFFALO7 | 345 | 20.2858 | 20.2907 | 0.0049
GEN-2022-142 | 03 CENTRAL | 300039 | 7FAIRPT | 345 | 12.3374 | 12.3423 | 0.0049
GEN-2022-214 | 03 CENTRAL | 533070 | SLATECRK4 | 138 | 5.7036 | 5.7085 | 0.0049
GEN-2022-161 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.5035 | 40.5083 | 0.0048
GEN-2022-161 | 03 CENTRAL | 532874 | UNIONRG6 | 230 | 8.0719 | 8.0767 | 0.0048
GEN-2022-007 | 03 CENTRAL | 533366 | FLORENC3 | 115 | 3.3372 | 3.342 | 0.0048
GEN-2022-161 | 03 CENTRAL | 532772 | STRANGR7 | 345 | 26.9098 | 26.9146 | 0.0048
GEN-2022-161 | 03 CENTRAL | 763890 | GEN-2019-058 | 345 | 13.5537 | 13.5585 | 0.0048
GEN-2022-006 | 03 CENTRAL | 542969 | STILWEL5 | 161 | 40.5036 | 40.5083 | 0.0047
GEN-2022-006 | 03 CENTRAL | 547728 | GAL278T | 69 | 13.0209 | 13.0256 | 0.0047
GEN-2022-054 | 03 CENTRAL | 513596 | IGLOOV 7 | 345 | 19.7172 | 19.7219 | 0.0047
GEN-2022-161 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 11.0713 | 11.076 | 0.0047
GEN-2022-024 | 03 CENTRAL | 533003 | LIBERTY4 | 138 | 7.2869 | 7.2916 | 0.0047
GEN-2022-024 | 03 CENTRAL | 533696 | LABETTS2 | 69 | 6.082 | 6.0867 | 0.0047
GEN-2022-013 | 03 CENTRAL | 533704 | PARSONS2 | 69 | 4.8386 | 4.8433 | 0.0047
GEN-2022-006 | 03 CENTRAL | 532926 | BAKER 2 | 69 | 4.8832 | 4.8879 | 0.0047
GEN-2022-006 | 03 CENTRAL | 547551 | GAT258 2 | 69 | 14.0287 | 14.0334 | 0.0047
GEN-2022-006 | 03 CENTRAL | 762279 | GEN-2017-195 | 345 | 27.5478 | 27.5524 | 0.0046
GEN-2022-006 | 03 CENTRAL | 762300 | GEN-2017-196 | 345 | 27.4673 | 27.4719 | 0.0046
GEN-2022-054 | 03 CENTRAL | 533052 | PARKCTY4 | 138 | 19.7506 | 19.7552 | 0.0046
GEN-2022-015 | 03 CENTRAL | 531420 | FLETCHR3 | 115 | 6.7649 | 6.7695 | 0.0046
GEN-2022-161 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 6.8765 | 6.8811 | 0.0046
GEN-2022-024 | 03 CENTRAL | 533702 | ORDNCE 2 | 69 | 6.0193 | 6.0239 | 0.0046
GEN-2022-006 | 03 CENTRAL | 543651 | PRQN_WIND5 | 161 | 6.4186 | 6.4232 | 0.0046
GEN-2022-006 | 03 CENTRAL | 542965 | W.GRDNR7 | 345 | 27.6237 | 27.6283 | 0.0046
GEN-2022-142 | 03 CENTRAL | 543095 | LIBRTYS2 | 69 | 11.9432 | 11.9478 | 0.0046
GEN-2022-006 | 03 CENTRAL | 300741 | 5SPORTSMAN | 161 | 39.152 | 39.1566 | 0.0046
GEN-2022-054 | 03 CENTRAL | 533026 | ANDOVER4 | 138 | 17.409 | 17.4135 | 0.0045
GEN-2022-013 | 03 CENTRAL | 533772 | SE1GREE2 | 69 | 6.0094 | 6.0139 | 0.0045
GEN-2022-214 | 03 CENTRAL | 533561 | WINFLD 2 | 69 | 8.0012 | 8.0057 | 0.0045
GEN-2022-065 | 03 CENTRAL | 539642 | ELLSWTP3 | 115 | 3.8436 | 3.8481 | 0.0045
GEN-2022-161 | 03 CENTRAL | 532871 | CIRCLE 6 | 230 | 8.6231 | 8.6276 | 0.0045
GEN-2022-161 | 03 CENTRAL | 532853 | LAWHILL6 | 230 | 13.9496 | 13.9541 | 0.0045
GEN-2022-161 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 22.0166 | 22.0211 | 0.0045
GEN-2022-161 | 03 CENTRAL | 532854 | LEC U5 6 | 230 | 13.8103 | 13.8147 | 0.0044
GEN-2022-006 | 03 CENTRAL | 533670 | SUNFLRS2 | 69 | 6.3939 | 6.3983 | 0.0044
GEN-2022-006 | 03 CENTRAL | 533773 | SOPITT 2 | 69 | 5.4759 | 5.4803 | 0.0044
GEN-2022-065 | 03 CENTRAL | 530586 | ALBERT 2 | 69 | 3.539 | 3.5434 | 0.0044
GEN-2022-065 | 03 CENTRAL | 530714 | ANGUS 3 | 115 | 5.246 | 5.2504 | 0.0044
GEN-2022-024 | 03 CENTRAL | 547729 | BAX488 5 | 161 | 14.7074 | 14.7118 | 0.0044
GEN-2022-161 | 03 CENTRAL | 515375 | WWRDEHV7 | 345 | 17.5334 | 17.5378 | 0.0044
GEN-2022-065 | 03 CENTRAL | 530610 | SHAYS_230 | 230 | 4.1695 | 4.1738 | 0.0043
GEN-2022-054 | 03 CENTRAL | 562900 | G15052_1 | 345 | 11.2545 | 11.2588 | 0.0043
GEN-2022-054 | 03 CENTRAL | 560053 | G15052_T | 345 | 11.3005 | 11.3048 | 0.0043
GEN-2022-024 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.4639 | 8.4681 | 0.0042
GEN-2022-024 | 03 CENTRAL | 532934 | MARMTNE5 | 161 | 8.4688 | 8.473 | 0.0042
GEN-2022-015 | 03 CENTRAL | 641244 | ATHEY 7 | 115 | 3.0171 | 3.0213 | 0.0042
GEN-2022-161 | 03 CENTRAL | 532862 | MCDOWEL6 | 230 | 6.9667 | 6.9709 | 0.0042
GEN-2022-024 | 03 CENTRAL | 301348 | 5CHOTEAU2 | 161 | 40.6588 | 40.663 | 0.0042
GEN-2022-100 | 03 CENTRAL | 541200 | PHILL 7 | 345 | 18.3851 | 18.3892 | 0.0041
GEN-2022-006 | 03 CENTRAL | 547690 | GLF339 2 | 69 | 11.5843 | 11.5884 | 0.0041
GEN-2022-024 | 03 CENTRAL | 300794 | 5LAMAR | 161 | 8.5339 | 8.538 | 0.0041
GEN-2022-015 | 03 CENTRAL | 531393 | PLYMELL3 | 115 | 7.6907 | 7.6948 | 0.0041
GEN-2022-004 | 03 CENTRAL | 588364 | G16-153-TAP | 345 | 8.2976 | 8.3017 | 0.0041
GEN-2022-161 | 03 CENTRAL | 533412 | ARKVALJ3 | 115 | 9.6768 | 9.6809 | 0.0041
GEN-2022-161 | 03 CENTRAL | 533013 | MOUND 4 | 138 | 6.8096 | 6.8137 | 0.0041
GEN-2022-100 | 03 CENTRAL | 300534 | 2LINCLN | 69 | 4.7553 | 4.7594 | 0.0041
GEN-2022-013 | 03 CENTRAL | 764375 | GEN-2020-058 | 345 | 22.1614 | 22.1655 | 0.0041
GEN-2022-006 | 03 CENTRAL | 301348 | 5CHOTEAU2 | 161 | 40.6589 | 40.663 | 0.0041
GEN-2022-015 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.4435 | 6.4475 | 0.004
GEN-2022-013 | 03 CENTRAL | 765115 | GEN-2020-057 | 345 | 22.1616 | 22.1656 | 0.004
GEN-2022-013 | 03 CENTRAL | 542940 | ATLNTIC7 | 345 | 22.2086 | 22.2126 | 0.004
GEN-2022-006 | 03 CENTRAL | 512631 | MIAMI 5 | 161 | 9.3037 | 9.3077 | 0.004
GEN-2022-013 | 03 CENTRAL | 547541 | RIV167 2 | 69 | 17.2213 | 17.2253 | 0.004
GEN-2022-102 | 03 CENTRAL | 541236 | RICHMND5 | 161 | 7.7546 | 7.7586 | 0.004
GEN-2022-075 | 03 CENTRAL | 531465 | SETAB 7 | 345 | 7.3013 | 7.3053 | 0.004
GEN-2022-161 | 03 CENTRAL | 515544 | RENFROW4 | 138 | 13.7443 | 13.7482 | 0.0039
GEN-2022-073 | 03 CENTRAL | 541260 | RNRDGE 2 | 69 | 5.1729 | 5.1768 | 0.0039
GEN-2022-161 | 03 CENTRAL | 532982 | OXFORD 4 | 138 | 10.4182 | 10.4221 | 0.0039
GEN-2022-161 | 03 CENTRAL | 533438 | WMCPHER3 | 115 | 10.9991 | 11.003 | 0.0039
GEN-2022-006 | 03 CENTRAL | 766141 | G21-096-TAP | 345 | 12.4221 | 12.426 | 0.0039
GEN-2022-065 | 03 CENTRAL | 530623 | RICE 3 | 115 | 6.8303 | 6.8342 | 0.0039
GEN-2022-004 | 03 CENTRAL | 533873 | SG8CRAG2 | 69 | 5.9479 | 5.9517 | 0.0038
GEN-2022-015 | 03 CENTRAL | 640267 | MAXWELS7 | 115 | 6.4827 | 6.4865 | 0.0038
GEN-2022-065 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.1242 | 5.128 | 0.0038
GEN-2022-004 | 03 CENTRAL | 533830 | PECK 2 | 69 | 6.3396 | 6.3434 | 0.0038
GEN-2022-075 | 03 CENTRAL | 640250 | KEARNEY7 | 115 | 11.886 | 11.8897 | 0.0037
GEN-2022-075 | 03 CENTRAL | 530605 | REDLIN 3 | 115 | 3.7326 | 3.7363 | 0.0037
GEN-2022-075 | 03 CENTRAL | 515852 | DGRASSE7 | 345 | 13.7137 | 13.7174 | 0.0037
GEN-2022-075 | 03 CENTRAL | 640183 | GENTLMN3 | 345 | 14.4581 | 14.4618 | 0.0037
GEN-2022-161 | 03 CENTRAL | 533428 | MCPHER 3 | 115 | 10.614 | 10.6176 | 0.0036
GEN-2022-004 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 8.9505 | 8.9541 | 0.0036
GEN-2022-102 | 03 CENTRAL | 761376 | GEN-2017-183 | 345 | 8.5675 | 8.5711 | 0.0036
GEN-2022-013 | 03 CENTRAL | 588504 | G17-005-TAP | 161 | 6.8911 | 6.8947 | 0.0036
GEN-2022-142 | 03 CENTRAL | 640139 | COOPER 3 | 345 | 26.0814 | 26.085 | 0.0036
GEN-2022-054 | 03 CENTRAL | 547469 | RIV4525 | 161 | 24.0912 | 24.0948 | 0.0036
GEN-2022-073 | 03 CENTRAL | 532766 | JEC N 7 | 345 | 23.6905 | 23.6941 | 0.0036
GEN-2022-161 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 29.71 | 29.7135 | 0.0035
GEN-2022-065 | 03 CENTRAL | 539643 | ROLLHLS3 | 115 | 3.5427 | 3.5462 | 0.0035
GEN-2022-054 | 03 CENTRAL | 533030 | BOEINGE4 | 138 | 16.494 | 16.4975 | 0.0035
GEN-2022-073 | 03 CENTRAL | 533163 | HOYT 3 | 115 | 22.537 | 22.5404 | 0.0034
GEN-2022-015 | 03 CENTRAL | 599950 | LAMAR7 | 345 | 2.4482 | 2.4516 | 0.0034
GEN-2022-161 | 03 CENTRAL | 532855 | MIDLAND6 | 230 | 12.3799 | 12.3833 | 0.0034
GEN-2022-161 | 03 CENTRAL | 539813 | TRANSFORMER | 345 | 11.4237 | 11.4271 | 0.0034
GEN-2022-075 | 03 CENTRAL | 539645 | DCBEEF3 | 115 | 6.7956 | 6.799 | 0.0034
GEN-2022-054 | 03 CENTRAL | 764310 | G20-079-TAP | 161 | 17.9674 | 17.9708 | 0.0034
GEN-2022-065 | 03 CENTRAL | 530686 | RICE 6 | 230 | 4.6587 | 4.662 | 0.0033
GEN-2022-144 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 7.7498 | 7.7531 | 0.0033
GEN-2022-073 | 03 CENTRAL | 541261 | STALEY 2 | 69 | 5.6094 | 5.6127 | 0.0033
GEN-2022-161 | 03 CENTRAL | 532795 | FR2WEST7 | 345 | 5.3465 | 5.3498 | 0.0033
GEN-2022-161 | 03 CENTRAL | 533415 | DAVIS 3 | 115 | 8.0468 | 8.0501 | 0.0033
GEN-2022-075 | 03 CENTRAL | 653571 | GR ISLD3 | 345 | 11.3886 | 11.3919 | 0.0033
GEN-2022-161 | 03 CENTRAL | 539840 | GEN-2011-008 | 345 | 11.625 | 11.6283 | 0.0033
GEN-2022-144 | 03 CENTRAL | 300302 | 2LATHRP | 69 | 8.1086 | 8.1119 | 0.0033
GEN-2022-073 | 03 CENTRAL | 541394 | AVENUECTY 5 | 161 | 9.4756 | 9.4789 | 0.0033
GEN-2022-144 | 03 CENTRAL | 301627 | 2LATHRPLD | 69 | 8.0574 | 8.0606 | 0.0032
GEN-2022-144 | 03 CENTRAL | 300310 | 2SMITHV | 69 | 7.1494 | 7.1526 | 0.0032
GEN-2022-142 | 03 CENTRAL | 532765 | HOYT 7 | 345 | 15.9775 | 15.9807 | 0.0032
GEN-2022-144 | 03 CENTRAL | 300526 | 2LMV | 69 | 6.3302 | 6.3334 | 0.0032
GEN-2022-065 | 03 CENTRAL | 765010 | GEN-2020-056 | 115 | 3.368 | 3.3712 | 0.0032
GEN-2022-065 | 03 CENTRAL | 539701 | RUSSELL3 | 115 | 3.3825 | 3.3857 | 0.0032
GEN-2022-013 | 03 CENTRAL | 543650 | DAKOTA_5 | 161 | 7.6636 | 7.6668 | 0.0032
GEN-2022-161 | 03 CENTRAL | 560080 | G16-046-TAP | 345 | 12.1956 | 12.1988 | 0.0032
GEN-2022-054 | 03 CENTRAL | 300042 | 7HUBEN | 345 | 10.0726 | 10.0758 | 0.0032
GEN-2022-161 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 28.7586 | 28.7617 | 0.0031
GEN-2022-024 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.2116 | 20.2147 | 0.0031
GEN-2022-006 | 03 CENTRAL | 533763 | HUDSON-2 | 69 | 4.5779 | 4.581 | 0.0031
GEN-2022-073 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 7.75 | 7.7531 | 0.0031
GEN-2022-006 | 03 CENTRAL | 300794 | 5LAMAR | 161 | 8.5349 | 8.538 | 0.0031
GEN-2022-075 | 03 CENTRAL | 539688 | S-DODGE3 | 115 | 6.6081 | 6.6112 | 0.0031
GEN-2022-161 | 03 CENTRAL | 533414 | CITIES 3 | 115 | 7.8674 | 7.8704 | 0.003
GEN-2022-013 | 03 CENTRAL | 533279 | ATLNTIC3 | 115 | 37.5059 | 37.5089 | 0.003
GEN-2022-102 | 03 CENTRAL | 541232 | LEX161 5 | 161 | 7.513 | 7.516 | 0.003
GEN-2022-073 | 03 CENTRAL | 645458 | S3458 3 | 345 | 28.4035 | 28.4065 | 0.003
GEN-2022-054 | 03 CENTRAL | 533032 | BU11PON4 | 138 | 14.7479 | 14.7509 | 0.003
GEN-2022-024 | 03 CENTRAL | 533704 | PARSONS2 | 69 | 4.8403 | 4.8433 | 0.003
GEN-2022-102 | 03 CENTRAL | 300110 | 5PITTSV | 161 | 8.4738 | 8.4768 | 0.003
GEN-2022-015 | 03 CENTRAL | 640312 | PAULINE3 | 345 | 7.5194 | 7.5224 | 0.003
GEN-2022-015 | 03 CENTRAL | 640238 | JEFFREY7 | 115 | 5.9115 | 5.9145 | 0.003
GEN-2022-065 | 03 CENTRAL | 530592 | SMOKYHL6 | 230 | 6.7491 | 6.7521 | 0.003
GEN-2022-161 | 03 CENTRAL | 532861 | EMANHAT6 | 230 | 10.0478 | 10.0507 | 0.0029
GEN-2022-075 | 03 CENTRAL | 530677 | OGALATP3 | 115 | 2.5546 | 2.5575 | 0.0029
GEN-2022-100 | 03 CENTRAL | 346117 | 2OVERTON | 69 | 3.5122 | 3.5151 | 0.0029
GEN-2022-144 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 12.5487 | 12.5516 | 0.0029
GEN-2022-054 | 03 CENTRAL | 533067 | SPRNGDL4 | 138 | 14.1494 | 14.1523 | 0.0029
GEN-2022-065 | 03 CENTRAL | 560082 | G16-050-TAP | 345 | 6.4446 | 6.4475 | 0.0029
GEN-2022-100 | 03 CENTRAL | 543061 | BRUNSWK5 | 161 | 5.6871 | 5.69 | 0.0029
GEN-2022-144 | 03 CENTRAL | 300311 | 2SMRSET | 69 | 6.6166 | 6.6195 | 0.0029
GEN-2022-015 | 03 CENTRAL | 640271 | MCCOOL 3 | 345 | 9.9258 | 9.9286 | 0.0028
GEN-2022-161 | 03 CENTRAL | 761838 | GEN-2017-121 | 138 | 8.9513 | 8.9541 | 0.0028
GEN-2022-161 | 03 CENTRAL | 515853 | DGRASSE4 | 138 | 14.0979 | 14.1007 | 0.0028
GEN-2022-161 | 03 CENTRAL | 533430 | MNDRGCT3 | 115 | 6.4833 | 6.4861 | 0.0028
GEN-2022-015 | 03 CENTRAL | 640510 | HOLT.CO3 | 345 | 6.1952 | 6.198 | 0.0028
GEN-2022-075 | 03 CENTRAL | 763758 | GEN-2019-044 | 115 | 6.3556 | 6.3584 | 0.0028
GEN-2022-102 | 03 CENTRAL | 543114 | PLUMRRD2 | 69 | 12.1877 | 12.1905 | 0.0028
GEN-2022-024 | 03 CENTRAL | 533772 | SE1GREE2 | 69 | 6.0111 | 6.0139 | 0.0028
GEN-2022-161 | 03 CENTRAL | 763677 | G19-030-TAP | 345 | 12.1601 | 12.1629 | 0.0028
GEN-2022-054 | 03 CENTRAL | 533029 | 59TH ST4 | 138 | 17.101 | 17.1038 | 0.0028
GEN-2022-161 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 30.0666 | 30.0693 | 0.0027
GEN-2022-013 | 03 CENTRAL | 533639 | MARMATN2 | 69 | 8.7258 | 8.7285 | 0.0027
GEN-2022-161 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.212 | 20.2147 | 0.0027
GEN-2022-013 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 29.7108 | 29.7135 | 0.0027
GEN-2022-015 | 03 CENTRAL | 640168 | ENDERS 8 | 69 | 3.0028 | 3.0055 | 0.0027
GEN-2022-054 | 03 CENTRAL | 300070 | 5CLARK | 161 | 7.8258 | 7.8285 | 0.0027
GEN-2022-006 | 03 CENTRAL | 543065 | CNTRVIL5 | 161 | 6.2715 | 6.2742 | 0.0027
GEN-2022-015 | 03 CENTRAL | 584650 | GEN-2015-023 | 345 | 6.15 | 6.1527 | 0.0027
GEN-2022-161 | 03 CENTRAL | 588494 | G17-004-TAP | 345 | 6.3177 | 6.3203 | 0.0026
GEN-2022-015 | 03 CENTRAL | 760767 | GEN-2017-144 | 345 | 5.9727 | 5.9753 | 0.0026
GEN-2022-075 | 03 CENTRAL | 587680 | GEN-2016-074 | 345 | 5.4848 | 5.4874 | 0.0026
GEN-2022-144 | 03 CENTRAL | 541261 | STALEY 2 | 69 | 5.6101 | 5.6127 | 0.0026
GEN-2022-024 | 03 CENTRAL | 764375 | GEN-2020-058 | 345 | 22.1629 | 22.1655 | 0.0026
GEN-2022-013 | 03 CENTRAL | 512750 | TONECE7 | 345 | 14.903 | 14.9055 | 0.0025
GEN-2022-006 | 03 CENTRAL | 547554 | BAX271 2 | 69 | 9.2689 | 9.2714 | 0.0025
GEN-2022-054 | 03 CENTRAL | 512742 | WMAIN ST5 | 161 | 26.9261 | 26.9286 | 0.0025
GEN-2022-024 | 03 CENTRAL | 547541 | RIV167 2 | 69 | 17.2228 | 17.2253 | 0.0025
GEN-2022-024 | 03 CENTRAL | 765115 | GEN-2020-057 | 345 | 22.1631 | 22.1656 | 0.0025
GEN-2022-024 | 03 CENTRAL | 542940 | ATLNTIC7 | 345 | 22.2101 | 22.2126 | 0.0025
GEN-2022-006 | 03 CENTRAL | 547601 | HOC404 2 | 69 | 9.3824 | 9.3849 | 0.0025
GEN-2022-161 | 03 CENTRAL | 532793 | NEOSHO 7 | 345 | 15.496 | 15.4985 | 0.0025
GEN-2022-013 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 28.7593 | 28.7617 | 0.0024
GEN-2022-006 | 03 CENTRAL | 541198 | PECULR 7 | 345 | 20.2123 | 20.2147 | 0.0024
GEN-2022-006 | 03 CENTRAL | 533654 | ZILAJCT2 | 69 | 6.1887 | 6.1911 | 0.0024
GEN-2022-073 | 03 CENTRAL | 541501 | OSBORN7 | 345 | 6.9078 | 6.9102 | 0.0024
GEN-2022-144 | 03 CENTRAL | 300331 | 2PITTSV | 69 | 4.293 | 4.2954 | 0.0024
GEN-2022-144 | 03 CENTRAL | 300301 | 2KEARNY | 69 | 5.6538 | 5.6562 | 0.0024
GEN-2022-024 | 03 CENTRAL | 588504 | G17-005-TAP | 161 | 6.8924 | 6.8947 | 0.0023
GEN-2022-144 | 03 CENTRAL | 300329 | 2OAKGVNW | 69 | 4.2868 | 4.2891 | 0.0023
GEN-2022-075 | 03 CENTRAL | 763410 | G18-125-TAP | 345 | 7.1844 | 7.1867 | 0.0023
GEN-2022-144 | 03 CENTRAL | 300297 | 2HOLT | 69 | 6.1287 | 6.131 | 0.0023
GEN-2022-006 | 03 CENTRAL | 533621 | ALLEN 2 | 69 | 6.5959 | 6.5982 | 0.0023
GEN-2022-013 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 22.0188 | 22.0211 | 0.0023
GEN-2022-073 | 03 CENTRAL | 635017 | ATCHSN 3 | 345 | 16.7399 | 16.7422 | 0.0023
GEN-2022-054 | 03 CENTRAL | 764300 | GEN-2020-079 | 161 | 14.877 | 14.8793 | 0.0023
GEN-2022-102 | 03 CENTRAL | 541262 | LIBERTY2 | 69 | 9.664 | 9.6662 | 0.0022
GEN-2022-073 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 12.5494 | 12.5516 | 0.0022
GEN-2022-054 | 03 CENTRAL | 300651 | 2LAMR | 69 | 9.672 | 9.6742 | 0.0022
GEN-2022-013 | 03 CENTRAL | 532926 | BAKER 2 | 69 | 4.8857 | 4.8879 | 0.0022
GEN-2022-161 | 03 CENTRAL | 533426 | MANVILE3 | 115 | 8.3627 | 8.3649 | 0.0022
GEN-2022-054 | 03 CENTRAL | 506935 | FLINTCR7 | 345 | 15.1317 | 15.1339 | 0.0022
GEN-2022-006 | 03 CENTRAL | 547527 | WEB436 2 | 69 | 9.2603 | 9.2624 | 0.0021
GEN-2022-054 | 03 CENTRAL | 514825 | KAYWIND7 | 345 | 11.0475 | 11.0496 | 0.0021
GEN-2022-100 | 03 CENTRAL | 345222 | 2MOBERLY | 69 | 7.6527 | 7.6548 | 0.0021
GEN-2022-013 | 03 CENTRAL | 533647 | UN1ELSM2 | 69 | 7.8262 | 7.8283 | 0.0021
GEN-2022-054 | 03 CENTRAL | 515621 | OPENSKY7 | 345 | 11.0739 | 11.076 | 0.0021
GEN-2022-054 | 03 CENTRAL | 512750 | TONECE7 | 345 | 14.9034 | 14.9055 | 0.0021
GEN-2022-065 | 03 CENTRAL | 539660 | EHALLTP3 | 115 | 3.2421 | 3.2442 | 0.0021
GEN-2022-054 | 03 CENTRAL | 542940 | ATLNTIC7 | 345 | 22.2105 | 22.2126 | 0.0021
GEN-2022-075 | 03 CENTRAL | 640525 | TOBIAS 3 | 345 | 10.0232 | 10.0253 | 0.0021
GEN-2022-006 | 03 CENTRAL | 764375 | GEN-2020-058 | 345 | 22.1635 | 22.1655 | 0.002
GEN-2022-006 | 03 CENTRAL | 547486 | HOC404 4 | 138 | 6.4584 | 6.4604 | 0.002
GEN-2022-142 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 7.7511 | 7.7531 | 0.002
GEN-2022-024 | 03 CENTRAL | 543650 | DAKOTA_5 | 161 | 7.6648 | 7.6668 | 0.002
GEN-2022-013 | 03 CENTRAL | 533773 | SOPITT 2 | 69 | 5.4783 | 5.4803 | 0.002
GEN-2022-075 | 03 CENTRAL | 762834 | GEN-2018-049 | 345 | 6.8791 | 6.8811 | 0.002
GEN-2022-024 | 03 CENTRAL | 533279 | ATLNTIC3 | 115 | 37.507 | 37.5089 | 0.0019
GEN-2022-142 | 03 CENTRAL | 541260 | RNRDGE 2 | 69 | 5.1749 | 5.1768 | 0.0019
GEN-2022-065 | 03 CENTRAL | 530725 | PFEIFER 3 | 115 | 3.4248 | 3.4267 | 0.0019
GEN-2022-006 | 03 CENTRAL | 765115 | GEN-2020-057 | 345 | 22.1637 | 22.1656 | 0.0019
GEN-2022-006 | 03 CENTRAL | 542940 | ATLNTIC7 | 345 | 22.2107 | 22.2126 | 0.0019
GEN-2022-013 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 30.0674 | 30.0693 | 0.0019
GEN-2022-004 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.3323 | 6.3341 | 0.0018
GEN-2022-054 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 5.9502 | 5.952 | 0.0018
GEN-2022-075 | 03 CENTRAL | 640275 | MINDEN 7 | 115 | 7.0296 | 7.0314 | 0.0018
GEN-2022-073 | 03 CENTRAL | 345409 | 5OVERTON | 161 | 20.613 | 20.6148 | 0.0018
GEN-2022-006 | 03 CENTRAL | 512750 | TONECE7 | 345 | 14.9038 | 14.9055 | 0.0017
GEN-2022-024 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 29.7118 | 29.7135 | 0.0017
GEN-2022-161 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 21.6957 | 21.6974 | 0.0017
GEN-2022-102 | 03 CENTRAL | 300304 | 2MOCITY | 69 | 9.2183 | 9.22 | 0.0017
GEN-2022-024 | 03 CENTRAL | 533639 | MARMATN2 | 69 | 8.7268 | 8.7285 | 0.0017
GEN-2022-015 | 03 CENTRAL | 640288 | N.PLATT8 | 69 | 4.8808 | 4.8825 | 0.0017
GEN-2022-144 | 03 CENTRAL | 300324 | 2CHAPHL | 69 | 3.9093 | 3.911 | 0.0017
GEN-2022-161 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.5913 | 5.593 | 0.0017
GEN-2022-073 | 03 CENTRAL | 541197 | MULLNCR7 | 345 | 7.8776 | 7.8793 | 0.0017
GEN-2022-142 | 03 CENTRAL | 541261 | STALEY 2 | 69 | 5.611 | 5.6127 | 0.0017
GEN-2022-004 | 03 CENTRAL | 539003 | CLDWELL4 | 138 | 5.5914 | 5.593 | 0.0016
GEN-2022-161 | 03 CENTRAL | 533506 | DAVIS 2 | 69 | 7.1714 | 7.173 | 0.0016
GEN-2022-102 | 03 CENTRAL | 300091 | 5LATHRP | 161 | 8.6261 | 8.6277 | 0.0016
GEN-2022-100 | 03 CENTRAL | 346171 | 2SPRK TAP | 69 | 6.8424 | 6.844 | 0.0016
GEN-2022-054 | 03 CENTRAL | 532798 | VIOLA 7 | 345 | 14.0923 | 14.0939 | 0.0016
GEN-2022-100 | 03 CENTRAL | 346169 | 2DUPONT | 69 | 6.6367 | 6.6383 | 0.0016
GEN-2022-054 | 03 CENTRAL | 515576 | RANCHRD7 | 345 | 11.8376 | 11.8392 | 0.0016
GEN-2022-024 | 03 CENTRAL | 512750 | TONECE7 | 345 | 14.9039 | 14.9055 | 0.0016
GEN-2022-065 | 03 CENTRAL | 530552 | GORHAM 3 | 115 | 3.1011 | 3.1027 | 0.0016
GEN-2022-054 | 03 CENTRAL | 532990 | MIDIAN 4 | 138 | 10.7867 | 10.7883 | 0.0016
GEN-2022-013 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.4066 | 16.4081 | 0.0015
GEN-2022-006 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 29.712 | 29.7135 | 0.0015
GEN-2022-006 | 03 CENTRAL | 543069 | PAOLA 5 | 161 | 10.7289 | 10.7304 | 0.0015
GEN-2022-006 | 03 CENTRAL | 533640 | MCKEE 2 | 69 | 4.1786 | 4.1801 | 0.0015
GEN-2022-065 | 03 CENTRAL | 539698 | WALDO 3 | 115 | 2.7126 | 2.7141 | 0.0015
GEN-2022-161 | 03 CENTRAL | 533394 | CORONAD3 | 115 | 6.9846 | 6.9861 | 0.0015
GEN-2022-161 | 03 CENTRAL | 532992 | TIMBJCT4 | 138 | 6.3326 | 6.3341 | 0.0015
GEN-2022-075 | 03 CENTRAL | 539758 | FORD 3 | 115 | 5.1265 | 5.128 | 0.0015
GEN-2022-015 | 03 CENTRAL | 640101 | CAMBRIG8 | 69 | 2.2104 | 2.2119 | 0.0015
GEN-2022-006 | 03 CENTRAL | 533279 | ATLNTIC3 | 115 | 37.5074 | 37.5089 | 0.0015
GEN-2022-004 | 03 CENTRAL | 533783 | BELL 2 | 69 | 4.6626 | 4.6641 | 0.0015
GEN-2022-054 | 03 CENTRAL | 532993 | TALLGRS4 | 138 | 10.2227 | 10.2242 | 0.0015
GEN-2022-024 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 28.7602 | 28.7617 | 0.0015
GEN-2022-073 | 03 CENTRAL | 640140 | COOPER 5 | 161 | 17.2518 | 17.2532 | 0.0014
GEN-2022-144 | 03 CENTRAL | 300313 | 2WESTBR | 69 | 5.3997 | 5.4011 | 0.0014
GEN-2022-073 | 03 CENTRAL | 588250 | GEN-2016-174 | 345 | 5.8792 | 5.8806 | 0.0014
GEN-2022-015 | 03 CENTRAL | 659134 | SIDNEY___TS4 | 230 | 4.7322 | 4.7336 | 0.0014
GEN-2022-015 | 03 CENTRAL | 640359 | STAPLETON 7 | 115 | 4.015 | 4.0164 | 0.0014
GEN-2022-100 | 03 CENTRAL | 99911 | GI91POI | 69 | 2.8137 | 2.8151 | 0.0014
GEN-2022-142 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 12.5502 | 12.5516 | 0.0014
GEN-2022-161 | 03 CENTRAL | 532875 | DVISTA 6 | 230 | 4.8043 | 4.8057 | 0.0014
GEN-2022-015 | 03 CENTRAL | 652832 | GRPRAR1-LNX3 | 345 | 5.4695 | 5.4709 | 0.0014
GEN-2022-024 | 03 CENTRAL | 532926 | BAKER 2 | 69 | 4.8865 | 4.8879 | 0.0014
GEN-2022-054 | 03 CENTRAL | 533703 | ORDNJCT2 | 69 | 8.3395 | 8.3409 | 0.0014
GEN-2022-024 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 22.0197 | 22.0211 | 0.0014
GEN-2022-073 | 03 CENTRAL | 300044 | 7MCCRED | 345 | 17.4284 | 17.4298 | 0.0014
GEN-2022-013 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 21.6961 | 21.6974 | 0.0013
GEN-2022-102 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 7.7518 | 7.7531 | 0.0013
GEN-2022-161 | 03 CENTRAL | 533439 | WHEATLD3 | 115 | 6.8185 | 6.8198 | 0.0013
GEN-2022-024 | 03 CENTRAL | 533773 | SOPITT 2 | 69 | 5.479 | 5.4803 | 0.0013
GEN-2022-065 | 03 CENTRAL | 530688 | BUFLOCRK6 | 230 | 3.5536 | 3.5549 | 0.0013
GEN-2022-024 | 03 CENTRAL | 533647 | UN1ELSM2 | 69 | 7.827 | 7.8283 | 0.0013
GEN-2022-144 | 03 CENTRAL | 346048 | 2MAURER | 69 | 3.1537 | 3.155 | 0.0013
GEN-2022-054 | 03 CENTRAL | 542966 | WGARDNR5 | 161 | 29.7122 | 29.7135 | 0.0013
GEN-2022-006 | 03 CENTRAL | 543105 | BULLCRK5 | 161 | 28.7604 | 28.7617 | 0.0013
GEN-2022-054 | 03 CENTRAL | 513570 | CHOUTEAUCRK5 | 161 | 19.6518 | 19.653 | 0.0012
GEN-2022-024 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 30.0681 | 30.0693 | 0.0012
GEN-2022-013 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.2887 | 21.2899 | 0.0012
GEN-2022-102 | 03 CENTRAL | 543116 | BLUEMLS2 | 69 | 7.3943 | 7.3955 | 0.0012
GEN-2022-073 | 03 CENTRAL | 533211 | ARNOLD 3 | 115 | 8.0376 | 8.0388 | 0.0012
GEN-2022-006 | 03 CENTRAL | 533645 | SE9HIAT2 | 69 | 3.709 | 3.7102 | 0.0012
GEN-2022-006 | 03 CENTRAL | 533650 | UN8HUMB2 | 69 | 4.351 | 4.3522 | 0.0012
GEN-2022-006 | 03 CENTRAL | 547530 | COL 94 2 | 69 | 6.286 | 6.2872 | 0.0012
GEN-2022-075 | 03 CENTRAL | 539699 | W-DODGE3 | 115 | 4.1987 | 4.1998 | 0.0011
GEN-2022-161 | 03 CENTRAL | 765200 | G20-090-TAP | 345 | 10.3824 | 10.3835 | 0.0011
GEN-2022-054 | 03 CENTRAL | 533629 | CC2SHAR2 | 69 | 4.5997 | 4.6008 | 0.0011
GEN-2022-144 | 03 CENTRAL | 300305 | 2ORRICK | 69 | 3.7757 | 3.7768 | 0.0011
GEN-2022-006 | 03 CENTRAL | 533644 | SE4DEVO2 | 69 | 3.6409 | 3.642 | 0.0011
GEN-2022-161 | 03 CENTRAL | 533380 | SPRGCRK3 | 115 | 3.7939 | 3.795 | 0.0011
GEN-2022-054 | 03 CENTRAL | 533008 | TV1MNDV4 | 138 | 6.9533 | 6.9544 | 0.0011
GEN-2022-013 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.9537 | 16.9548 | 0.0011
GEN-2022-006 | 03 CENTRAL | 542977 | CRAIG 7 | 345 | 22.02 | 22.0211 | 0.0011
GEN-2022-161 | 03 CENTRAL | 532994 | TCBURNS4 | 138 | 3.9453 | 3.9463 | 0.001
GEN-2022-102 | 03 CENTRAL | 541260 | RNRDGE 2 | 69 | 5.1758 | 5.1768 | 0.001
GEN-2022-102 | 03 CENTRAL | 541261 | STALEY 2 | 69 | 5.6117 | 5.6127 | 0.001
GEN-2022-024 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.4071 | 16.4081 | 0.001
GEN-2022-102 | 03 CENTRAL | 345408 | 7OVERTON | 345 | 12.5506 | 12.5516 | 0.001
GEN-2022-006 | 03 CENTRAL | 543049 | CEDRCRK5 | 161 | 30.0683 | 30.0693 | 0.001
GEN-2022-075 | 03 CENTRAL | 640224 | HOLDREG7 | 115 | 5.9753 | 5.9763 | 0.001
GEN-2022-054 | 03 CENTRAL | 533626 | BURLJCT2 | 69 | 4.9189 | 4.9199 | 0.001
GEN-2022-054 | 03 CENTRAL | 532935 | MARMTNW5 | 161 | 8.4672 | 8.4681 | 0.0009
GEN-2022-054 | 03 CENTRAL | 532934 | MARMTNE5 | 161 | 8.4721 | 8.473 | 0.0009
GEN-2022-054 | 03 CENTRAL | 533604 | WEAVER 2 | 69 | 11.7419 | 11.7428 | 0.0009
GEN-2022-054 | 03 CENTRAL | 533758 | CRAWFOR2 | 69 | 7.2088 | 7.2097 | 0.0009
GEN-2022-054 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.4072 | 16.4081 | 0.0009
GEN-2022-024 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.2891 | 21.2899 | 0.0008
GEN-2022-024 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 21.6966 | 21.6974 | 0.0008
GEN-2022-054 | 03 CENTRAL | 532771 | RENO 7 | 345 | 11.1158 | 11.1166 | 0.0008
GEN-2022-054 | 03 CENTRAL | 533630 | CC3WEST2 | 69 | 4.5417 | 4.5425 | 0.0008
GEN-2022-102 | 03 CENTRAL | 543093 | LAKCTYK2 | 69 | 7.4959 | 7.4967 | 0.0008
GEN-2022-075 | 03 CENTRAL | 539783 | CRKCK 3 | 115 | 4.0463 | 4.0471 | 0.0008
GEN-2022-073 | 03 CENTRAL | 588260 | GEN-2016-176 | 345 | 4.9286 | 4.9294 | 0.0008
GEN-2022-006 | 03 CENTRAL | 532774 | SWISVAL7 | 345 | 16.4073 | 16.4081 | 0.0008
GEN-2022-006 | 03 CENTRAL | 543132 | BNSF 5 | 161 | 21.6967 | 21.6974 | 0.0007
GEN-2022-142 | 03 CENTRAL | 588250 | GEN-2016-174 | 345 | 5.8799 | 5.8806 | 0.0007
GEN-2022-054 | 03 CENTRAL | 532803 | BURNS 7 | 345 | 10.6843 | 10.685 | 0.0007
GEN-2022-024 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.9541 | 16.9548 | 0.0007
GEN-2022-073 | 03 CENTRAL | 640590 | MONOLITH 3 | 345 | 20.4912 | 20.4919 | 0.0007
GEN-2022-144 | 03 CENTRAL | 300204 | 2KNOXVL | 69 | 3.4917 | 3.4924 | 0.0007
GEN-2022-102 | 03 CENTRAL | 543091 | DUNCNRD2 | 69 | 6.3702 | 6.3709 | 0.0007
GEN-2022-054 | 03 CENTRAL | 512751 | TONECE5 | 161 | 14.8952 | 14.8959 | 0.0007
GEN-2022-006 | 03 CENTRAL | 532856 | SWISVAL6 | 230 | 21.2893 | 21.2899 | 0.0006
GEN-2022-073 | 03 CENTRAL | 345088 | 7MCCREDIE | 345 | 6.561 | 6.5616 | 0.0006
GEN-2022-013 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 5.9514 | 5.952 | 0.0006
GEN-2022-013 | 03 CENTRAL | 533640 | MCKEE 2 | 69 | 4.1795 | 4.1801 | 0.0006
GEN-2022-075 | 03 CENTRAL | 539763 | SSTARTP3 | 115 | 4.0099 | 4.0105 | 0.0006
GEN-2022-006 | 03 CENTRAL | 547411 | COL282 2 | 69 | 4.4798 | 4.4804 | 0.0006
GEN-2022-006 | 03 CENTRAL | 532768 | EMPEC 7 | 345 | 16.9542 | 16.9548 | 0.0006
GEN-2022-006 | 03 CENTRAL | 547455 | SCM66T 2 | 69 | 4.3106 | 4.3111 | 0.0005
GEN-2022-100 | 03 CENTRAL | 541500 | KETCHEM7 | 345 | 7.7526 | 7.7531 | 0.0005
GEN-2022-054 | 03 CENTRAL | 533636 | GREEN 2 | 69 | 4.0292 | 4.0297 | 0.0005
GEN-2022-161 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.4644 | 10.4649 | 0.0005
GEN-2022-054 | 03 CENTRAL | 533628 | CC1BURL2 | 69 | 3.3813 | 3.3818 | 0.0005
GEN-2022-054 | 03 CENTRAL | 533624 | BURLING2 | 69 | 3.3827 | 3.3832 | 0.0005
GEN-2022-161 | 03 CENTRAL | 533359 | UNIONRG3 | 115 | 3.7149 | 3.7154 | 0.0005
GEN-2022-024 | 03 CENTRAL | 533640 | MCKEE 2 | 69 | 4.1797 | 4.1801 | 0.0004
GEN-2022-015 | 03 CENTRAL | 640096 | CALAMS 7 | 115 | 3.3365 | 3.3369 | 0.0004
GEN-2022-054 | 03 CENTRAL | 533639 | MARMATN2 | 69 | 8.7281 | 8.7285 | 0.0004
GEN-2022-013 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.2966 | 10.297 | 0.0004
GEN-2022-013 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.4645 | 10.4649 | 0.0004
GEN-2022-054 | 03 CENTRAL | 533625 | BURLIND2 | 69 | 3.0153 | 3.0157 | 0.0004
GEN-2022-161 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.2966 | 10.297 | 0.0004
GEN-2022-024 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 5.9516 | 5.952 | 0.0004
GEN-2022-006 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 5.9516 | 5.952 | 0.0004
GEN-2022-006 | 03 CENTRAL | 547412 | SEK225T2 | 69 | 3.4501 | 3.4504 | 0.0003
GEN-2022-006 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.2967 | 10.297 | 0.0003
GEN-2022-024 | 03 CENTRAL | 543077 | PLSTVAL5 | 161 | 10.2967 | 10.297 | 0.0003
GEN-2022-054 | 03 CENTRAL | 532926 | BAKER 2 | 69 | 4.8876 | 4.8879 | 0.0003
GEN-2022-054 | 03 CENTRAL | 512727 | GRDA1 2 | 69 | 11.9475 | 11.9477 | 0.0002
GEN-2022-024 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.4647 | 10.4649 | 0.0002
GEN-2022-006 | 03 CENTRAL | 543054 | CEDARNL5 | 161 | 10.4647 | 10.4649 | 0.0002
GEN-2022-161 | 03 CENTRAL | 533653 | WOLFCRK2 | 69 | 5.9519 | 5.952 | 0.0001
GEN-2022-054 | 03 CENTRAL | 512700 | WAGNOR 5 | 161 | 9.5036 | 9.5037 | 0.0001
GEN-2022-100 | 03 CENTRAL | 346096 | 2MACON_AM | 69 | 1.5411 | 1.5412 | 0.0001
GEN-2022-013 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.5484 | 2.5485 | 0.0001
GEN-2022-006 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.5484 | 2.5485 | 0.0001
GEN-2022-054 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.5484 | 2.5485 | 0.0001
GEN-2022-024 | 03 CENTRAL | 541541 | LAC_LAKE_2 | 69 | 2.5484 | 2.5485 | 0.0001
GEN-2022-161 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.641 | 0.641 | 0
GEN-2022-100 | 03 CENTRAL | 346170 | 2ROTH TAP | 69 | 1.7545 | 1.7545 | 0
GEN-2022-161 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.6807 | 2.6807 | 0
GEN-2022-024 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.6807 | 2.6807 | 0
GEN-2022-161 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.614 | 0.614 | 0
GEN-2022-054 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.614 | 0.614 | 0
GEN-2022-054 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.6807 | 2.6807 | 0
GEN-2022-024 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.641 | 0.641 | 0
GEN-2022-006 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.614 | 0.614 | 0
GEN-2022-006 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.641 | 0.641 | 0
GEN-2022-013 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.6807 | 2.6807 | 0
GEN-2022-013 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.641 | 0.641 | 0
GEN-2022-006 | 03 CENTRAL | 543659 | LACYGNE2 | 69 | 2.6807 | 2.6807 | 0
GEN-2022-054 | 03 CENTRAL | 543667 | LAC3_STAR7 | 345 | 0.641 | 0.641 | 0
GEN-2022-024 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.614 | 0.614 | 0
GEN-2022-013 | 03 CENTRAL | 543669 | LAC8_STAR7 | 345 | 0.614 | 0.614 | 0
GEN-2022-009 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.5004 | 7.5028 | 0.0024
GEN-2022-009 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 11.7442 | 11.7576 | 0.0134
GEN-2022-009 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 9.6998 | 9.7567 | 0.0569
GEN-2022-009 | 01 NORTH | 652216 | WATFORD4 | 230 | 7.2147 | 7.2555 | 0.0408
GEN-2022-009 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.103 | 1.103 | 0
GEN-2022-009 | 01 NORTH | 652391 | WILLISTON27 | 115 | 20.5443 | 20.7564 | 0.2121
GEN-2022-009 | 01 NORTH | 652400 | WILISTN4 | 230 | 13.1978 | 13.5075 | 0.3097
GEN-2022-009 | 01 NORTH | 652408 | WATFORD7 | 115 | 9.2421 | 9.2661 | 0.024
GEN-2022-009 | 01 NORTH | 652419 | KILDEER7 | 115 | 5.1155 | 5.1188 | 0.0033
GEN-2022-009 | 01 NORTH | 652421 | WILISTN7 | 115 | 20.5328 | 20.7443 | 0.2115
GEN-2022-009 | 01 NORTH | 652424 | BELFELD3 | 345 | 7.0257 | 7.047 | 0.0213
GEN-2022-009 | 01 NORTH | 652425 | BELFELD4 | 230 | 9.9265 | 9.9454 | 0.0189
GEN-2022-009 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 5.7072 | 5.7124 | 0.0052
GEN-2022-009 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9749 | 0.9749 | 0
GEN-2022-009 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.9021 | 0.9021 | 0
GEN-2022-009 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.9089 | 0.9089 | 0
GEN-2022-009 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.689 | 0.689 | 0
GEN-2022-009 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6174 | 0.6174 | 0
GEN-2022-009 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1093 | 1.1093 | 0
GEN-2022-009 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.1151 | 1.1151 | 0
GEN-2022-009 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.1055 | 1.1055 | 0
GEN-2022-009 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5104 | 1.5105 | 0.0001
GEN-2022-009 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.0217 | 1.0217 | 0
GEN-2022-009 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9892 | 0.9893 | 0.0001
GEN-2022-009 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.9896 | 0.9897 | 0.0001
GEN-2022-009 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.548 | 1.548 | 0
GEN-2022-009 | 01 NORTH | 655790 | HELMUT -LY7 | 115 | 6.1083 | 6.112 | 0.0037
GEN-2022-009 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 2.0815 | 2.0822 | 0.0007
GEN-2022-009 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.8926 | 3.895 | 0.0024
GEN-2022-009 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 6.1883 | 6.2074 | 0.0191
GEN-2022-009 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.1842 | 4.1884 | 0.0042
GEN-2022-009 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 4.0934 | 4.0996 | 0.0062
GEN-2022-009 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 8.1063 | 8.131 | 0.0247
GEN-2022-009 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 14.2392 | 14.2818 | 0.0426
GEN-2022-009 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 6.9741 | 6.9843 | 0.0102
GEN-2022-009 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.1246 | 3.1269 | 0.0023
GEN-2022-009 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.5444 | 5.5517 | 0.0073
GEN-2022-009 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.687 | 3.692 | 0.005
GEN-2022-009 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.1386 | 4.1468 | 0.0082
GEN-2022-009 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 9.2421 | 9.2661 | 0.024
GEN-2022-009 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 7.5203 | 7.5289 | 0.0086
GEN-2022-009 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.3151 | 3.3204 | 0.0053
GEN-2022-009 | 01 NORTH | 655843 | TRUEOIL -MK7 | 115 | 1.6383 | 1.6387 | 0.0004
GEN-2022-009 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.3641 | 5.378 | 0.0139
GEN-2022-009 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.8043 | 4.8108 | 0.0065
GEN-2022-009 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.2445 | 4.2532 | 0.0087
GEN-2022-009 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 4.3567 | 4.3637 | 0.007
GEN-2022-009 | 01 NORTH | 655848 | BERG -MK7 | 115 | 5.8019 | 5.8145 | 0.0126
GEN-2022-009 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 10.0125 | 10.0503 | 0.0378
GEN-2022-009 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.5229 | 3.5289 | 0.006
GEN-2022-009 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9155 | 2.9175 | 0.002
GEN-2022-009 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5675 | 3.5706 | 0.0031
GEN-2022-009 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.3707 | 8.3874 | 0.0167
GEN-2022-009 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.5519 | 3.5566 | 0.0047
GEN-2022-009 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.9551 | 4.962 | 0.0069
GEN-2022-009 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.6876 | 6.7093 | 0.0217
GEN-2022-009 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.6034 | 2.6059 | 0.0025
GEN-2022-009 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 4.3892 | 4.3964 | 0.0072
GEN-2022-009 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.7658 | 3.7711 | 0.0053
GEN-2022-009 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.3429 | 2.3455 | 0.0026
GEN-2022-009 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.1731 | 3.178 | 0.0049
GEN-2022-009 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 5.816 | 5.8287 | 0.0127
GEN-2022-009 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 5.9665 | 5.9798 | 0.0133
GEN-2022-009 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 4.1015 | 4.1078 | 0.0063
GEN-2022-009 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 3.0286 | 3.0331 | 0.0045
GEN-2022-009 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7893 | 2.7931 | 0.0038
GEN-2022-009 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6866 | 2.6901 | 0.0035
GEN-2022-009 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.9867 | 3.9944 | 0.0077
GEN-2022-009 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 7.0543 | 7.0729 | 0.0186
GEN-2022-009 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 6.4347 | 6.4502 | 0.0155
GEN-2022-009 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 8.0248 | 8.0428 | 0.018
GEN-2022-009 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.8662 | 8.8883 | 0.0221
GEN-2022-009 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.4488 | 5.4572 | 0.0084
GEN-2022-009 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 4.0239 | 4.0284 | 0.0045
GEN-2022-009 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.8423 | 4.8489 | 0.0066
GEN-2022-009 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 5.8354 | 5.8481 | 0.0127
GEN-2022-009 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 13.4203 | 13.4882 | 0.0679
GEN-2022-009 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 10.0639 | 10.102 | 0.0381
GEN-2022-009 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 7.8985 | 7.922 | 0.0235
GEN-2022-009 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 5.494 | 5.5054 | 0.0114
GEN-2022-009 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 4.278 | 4.2848 | 0.0068
GEN-2022-009 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 5.1039 | 5.1136 | 0.0097
GEN-2022-009 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.5002 | 3.5061 | 0.0059
GEN-2022-009 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.4116 | 6.4315 | 0.0199
GEN-2022-009 | 01 NORTH | 655891 | KILLDEER-MK7 | 115 | 4.9403 | 4.9434 | 0.0031
GEN-2022-009 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 4.0833 | 4.0913 | 0.008
GEN-2022-009 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.26 | 6.2693 | 0.0093
GEN-2022-009 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.5485 | 3.5515 | 0.003
GEN-2022-009 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.4202 | 4.4257 | 0.0055
GEN-2022-009 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.4781 | 3.4826 | 0.0045
GEN-2022-009 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 5.356 | 5.3667 | 0.0107
GEN-2022-009 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.176 | 3.1788 | 0.0028
GEN-2022-009 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 6.4769 | 6.4926 | 0.0157
GEN-2022-009 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 18.9155 | 19.001 | 0.0855
GEN-2022-009 | 01 NORTH | 655924 | STATELIN-MW7 | 115 | 15.3858 | 15.4451 | 0.0593
GEN-2022-009 | 01 NORTH | 655925 | JUDSON -MW7 | 115 | 15.8451 | 15.9609 | 0.1158
GEN-2022-009 | 01 NORTH | 655926 | SW.WLSTN-MW7 | 115 | 8.8573 | 8.8933 | 0.036
GEN-2022-009 | 01 NORTH | 655931 | BLKTLTAP-MW7 | 115 | 10.4949 | 10.5543 | 0.0594
GEN-2022-009 | 01 NORTH | 655933 | N.MISRDG-MW7 | 115 | 15.7342 | 15.8767 | 0.1425
GEN-2022-009 | 01 NORTH | 655934 | N.WLST_T-MW7 | 115 | 14.4007 | 14.5197 | 0.119
GEN-2022-009 | 01 NORTH | 655935 | NW.WLSTN-MW7 | 115 | 12.7889 | 12.8795 | 0.0906
GEN-2022-009 | 01 NORTH | 655936 | N.WILSTN-MW7 | 115 | 14.0651 | 14.1791 | 0.114
GEN-2022-009 | 01 NORTH | 655937 | NE.WLSTN-MW7 | 115 | 13.1068 | 13.2084 | 0.1016
GEN-2022-009 | 01 NORTH | 655938 | SE.WLSTN-MW7 | 115 | 8.4661 | 8.5065 | 0.0404
GEN-2022-009 | 01 NORTH | 655940 | MONT -MW7 | 115 | 16.1808 | 16.2913 | 0.1105
GEN-2022-009 | 01 NORTH | 655941 | STRNDAHL-MW7 | 115 | 10.3627 | 10.4031 | 0.0404
GEN-2022-009 | 01 NORTH | 655945 | WHEELS_T-MW7 | 115 | 9.3067 | 9.3489 | 0.0422
GEN-2022-009 | 01 NORTH | 655955 | ZAHL -MW7 | 115 | 7.8622 | 7.8951 | 0.0329
GEN-2022-009 | 01 NORTH | 655956 | TYRONE -MW7 | 115 | 12.1936 | 12.2844 | 0.0908
GEN-2022-009 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 18.211 | 18.4367 | 0.2257
GEN-2022-009 | 01 NORTH | 655958 | FOLVAG -MW7 | 115 | 14.4647 | 14.6022 | 0.1375
GEN-2022-009 | 01 NORTH | 655966 | OLIVER -MW7 | 115 | 7.071 | 7.0963 | 0.0253
GEN-2022-009 | 01 NORTH | 659060 | FINSTAD345 | 345 | 6.8288 | 6.8625 | 0.0337
GEN-2022-009 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 14.8265 | 14.8722 | 0.0457
GEN-2022-009 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 17.1792 | 17.2086 | 0.0294
GEN-2022-009 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 23.8285 | 23.8563 | 0.0278
GEN-2022-009 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.3821 | 5.3828 | 0.0007
GEN-2022-009 | 01 NORTH | 659112 | CULBRTSN-UM7 | 115 | 4.4999 | 4.5021 | 0.0022
GEN-2022-009 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 7.3459 | 7.3528 | 0.0069
GEN-2022-009 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 12.6499 | 12.753 | 0.1031
GEN-2022-009 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 6.1027 | 6.1162 | 0.0135
GEN-2022-009 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 6.1546 | 6.1584 | 0.0038
GEN-2022-009 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 7.723 | 7.7282 | 0.0052
GEN-2022-009 | 01 NORTH | 659181 | BICNTNIL-BE7 | 115 | 3.476 | 3.4778 | 0.0018
GEN-2022-009 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 14.364 | 14.4074 | 0.0434
GEN-2022-009 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 11.1797 | 11.2699 | 0.0902
GEN-2022-009 | 01 NORTH | 659184 | ROUGHRDR-BE7 | 115 | 4.4495 | 4.453 | 0.0035
GEN-2022-009 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.7503 | 3.7532 | 0.0029
GEN-2022-009 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 21.7375 | 21.7605 | 0.023
GEN-2022-009 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 14.2245 | 14.2665 | 0.042
GEN-2022-009 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 14.8265 | 14.8722 | 0.0457
GEN-2022-009 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.5301 | 9.5339 | 0.0038
GEN-2022-009 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.0344 | 7.0412 | 0.0068
GEN-2022-009 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.209 | 7.2111 | 0.0021
GEN-2022-009 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.5436 | 5.5482 | 0.0046
GEN-2022-009 | 01 NORTH | 659248 | HALLIDAY-UM7 | 115 | 4.1814 | 4.1826 | 0.0012
GEN-2022-009 | 01 NORTH | 659262 | CULBSN.E-BE7 | 115 | 5.8636 | 5.8677 | 0.0041
GEN-2022-009 | 01 NORTH | 659269 | CULB_GEN-BE7 | 115 | 5.7442 | 5.7474 | 0.0032
GEN-2022-009 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 12.0476 | 12.1228 | 0.0752
GEN-2022-009 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.3163 | 2.3169 | 0.0006
GEN-2022-009 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 9.9265 | 9.9454 | 0.0189
GEN-2022-009 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 11.376 | 11.9492 | 0.5732
GEN-2022-009 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 13.3296 | 13.6818 | 0.3522
GEN-2022-009 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 8.7458 | 8.8352 | 0.0894
GEN-2022-009 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 12.5014 | 12.6041 | 0.1027
GEN-2022-009 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 7.7399 | 7.7452 | 0.0053
GEN-2022-009 | 01 NORTH | 659347 | PIONEER1-BE7 | 115 | 15.3858 | 15.4451 | 0.0593
GEN-2022-009 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 12.7409 | 12.7952 | 0.0543
GEN-2022-009 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 12.741 | 12.7953 | 0.0543
GEN-2022-009 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 8.1052 | 8.1755 | 0.0703
GEN-2022-009 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 9.5932 | 9.6389 | 0.0457
GEN-2022-009 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 9.885 | 9.9551 | 0.0701
GEN-2022-009 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 12.0101 | 12.0445 | 0.0344
GEN-2022-009 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 7.8935 | 7.9642 | 0.0707
GEN-2022-009 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 14.9267 | 15.0107 | 0.084
GEN-2022-009 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 10.4317 | 10.6199 | 0.1882
GEN-2022-009 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 19.6524 | 19.8404 | 0.188
GEN-2022-009 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 4.7964 | 4.8214 | 0.025
GEN-2022-009 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 14.8265 | 14.8722 | 0.0457
GEN-2022-009 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.1998 | 4.2002 | 0.0004
GEN-2022-009 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 17.1792 | 17.2086 | 0.0294
GEN-2022-009 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 17.1792 | 17.2086 | 0.0294
GEN-2022-009 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 8.7458 | 8.8352 | 0.0894
GEN-2022-009 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.9404 | 1.9408 | 0.0004
GEN-2022-009 | 01 NORTH | 659443 | SKUNKHIL-RR7 | 115 | 1.7456 | 1.7459 | 0.0003
GEN-2022-009 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.7913 | 6.7978 | 0.0065
GEN-2022-009 | 01 NORTH | 659450 | BRADYWND 4 | 230 | 3.665 | 3.6664 | 0.0014
GEN-2022-009 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 19.5473 | 19.7344 | 0.1871
GEN-2022-009 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 19.5599 | 19.7471 | 0.1872
GEN-2022-009 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 6.2116 | 6.2543 | 0.0427
GEN-2022-009 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.9404 | 1.9408 | 0.0004
GEN-2022-009 | 01 NORTH | 659600 | EFORK_-BE334 | 345 | 9.1746 | 9.4167 | 0.2421
GEN-2022-009 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 7.1349 | 7.1749 | 0.04
GEN-2022-009 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 12.6499 | 12.753 | 0.1031
GEN-2022-009 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 12.9024 | 12.9552 | 0.0528
GEN-2022-009 | 01 NORTH | 661087 | RAY JCT7 | 115 | 5.8368 | 5.8494 | 0.0126
GEN-2022-009 | 01 NORTH | 661089 | LTLMUDY7 | 115 | 7.1728 | 7.1959 | 0.0231
GEN-2022-009 | 01 NORTH | 672603 | BDV 4 | 230 | 5.0138 | 5.0188 | 0.005
GEN-2022-009 | 01 NORTH | 763021 | GEN-2018-067 | 115 | 10.3627 | 10.4031 | 0.0404
GEN-2022-009 | 01 NORTH | 763703 | GEN-2019-037 | 345 | 11.0502 | 11.062 | 0.0118
GEN-2022-009 | 01 NORTH | 764180 | GEN-2020-014 | 115 | 7.7399 | 7.7452 | 0.0053
GEN-2022-009 | 01 NORTH | 764225 | GEN-2020-091 | 345 | 10.2517 | 10.4329 | 0.1812
GEN-2022-009 | 01 NORTH | 765070 | GEN-2020-083 | 115 | 5.7072 | 5.7124 | 0.0052
GEN-2022-009 | 01 NORTH | 767161 | GEN-2022-009 | 345 | 9.0852 | 9.8886 | 0.8034
GEN-2022-010 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.4977 | 7.5028 | 0.0051
GEN-2022-010 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 11.7293 | 11.7576 | 0.0283
GEN-2022-010 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 9.6375 | 9.7567 | 0.1192
GEN-2022-010 | 01 NORTH | 652216 | WATFORD4 | 230 | 7.1698 | 7.2555 | 0.0857
GEN-2022-010 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.103 | 1.103 | 0
GEN-2022-010 | 01 NORTH | 652391 | WILLISTON27 | 115 | 20.314 | 20.7564 | 0.4424
GEN-2022-010 | 01 NORTH | 652400 | WILISTN4 | 230 | 12.8703 | 13.5075 | 0.6372
GEN-2022-010 | 01 NORTH | 652408 | WATFORD7 | 115 | 9.2156 | 9.2661 | 0.0505
GEN-2022-010 | 01 NORTH | 652419 | KILDEER7 | 115 | 5.1119 | 5.1188 | 0.0069
GEN-2022-010 | 01 NORTH | 652421 | WILISTN7 | 115 | 20.3031 | 20.7443 | 0.4412
GEN-2022-010 | 01 NORTH | 652424 | BELFELD3 | 345 | 7.0021 | 7.047 | 0.0449
GEN-2022-010 | 01 NORTH | 652425 | BELFELD4 | 230 | 9.9055 | 9.9454 | 0.0399
GEN-2022-010 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 5.7014 | 5.7124 | 0.011
GEN-2022-010 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9749 | 0.9749 | 0
GEN-2022-010 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.9021 | 0.9021 | 0
GEN-2022-010 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.9089 | 0.9089 | 0
GEN-2022-010 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.689 | 0.689 | 0
GEN-2022-010 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6174 | 0.6174 | 0
GEN-2022-010 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1093 | 1.1093 | 0
GEN-2022-010 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.1151 | 1.1151 | 0
GEN-2022-010 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.1055 | 1.1055 | 0
GEN-2022-010 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5104 | 1.5105 | 0.0001
GEN-2022-010 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.0217 | 1.0217 | 0
GEN-2022-010 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9892 | 0.9893 | 0.0001
GEN-2022-010 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.9896 | 0.9897 | 0.0001
GEN-2022-010 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.5479 | 1.548 | 0.0001
GEN-2022-010 | 01 NORTH | 655790 | HELMUT -LY7 | 115 | 6.1042 | 6.112 | 0.0078
GEN-2022-010 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 2.0807 | 2.0822 | 0.0015
GEN-2022-010 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.8899 | 3.895 | 0.0051
GEN-2022-010 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 6.1674 | 6.2074 | 0.04
GEN-2022-010 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.1796 | 4.1884 | 0.0088
GEN-2022-010 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 4.0865 | 4.0996 | 0.0131
GEN-2022-010 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 8.0791 | 8.131 | 0.0519
GEN-2022-010 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 14.1921 | 14.2818 | 0.0897
GEN-2022-010 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 6.9628 | 6.9843 | 0.0215
GEN-2022-010 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.122 | 3.1269 | 0.0049
GEN-2022-010 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.5363 | 5.5517 | 0.0154
GEN-2022-010 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.6813 | 3.692 | 0.0107
GEN-2022-010 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.1294 | 4.1468 | 0.0174
GEN-2022-010 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 9.2156 | 9.2661 | 0.0505
GEN-2022-010 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 7.5108 | 7.5289 | 0.0181
GEN-2022-010 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.3092 | 3.3204 | 0.0112
GEN-2022-010 | 01 NORTH | 655843 | TRUEOIL -MK7 | 115 | 1.6379 | 1.6387 | 0.0008
GEN-2022-010 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.3487 | 5.378 | 0.0293
GEN-2022-010 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.7971 | 4.8108 | 0.0137
GEN-2022-010 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.2349 | 4.2532 | 0.0183
GEN-2022-010 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 4.3488 | 4.3637 | 0.0149
GEN-2022-010 | 01 NORTH | 655848 | BERG -MK7 | 115 | 5.788 | 5.8145 | 0.0265
GEN-2022-010 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 9.971 | 10.0503 | 0.0793
GEN-2022-010 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.5163 | 3.5289 | 0.0126
GEN-2022-010 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9132 | 2.9175 | 0.0043
GEN-2022-010 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5642 | 3.5706 | 0.0064
GEN-2022-010 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.3523 | 8.3874 | 0.0351
GEN-2022-010 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.5467 | 3.5566 | 0.0099
GEN-2022-010 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.9474 | 4.962 | 0.0146
GEN-2022-010 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.6638 | 6.7093 | 0.0455
GEN-2022-010 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.6006 | 2.6059 | 0.0053
GEN-2022-010 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 4.3812 | 4.3964 | 0.0152
GEN-2022-010 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.76 | 3.7711 | 0.0111
GEN-2022-010 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.34 | 2.3455 | 0.0055
GEN-2022-010 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.1677 | 3.178 | 0.0103
GEN-2022-010 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 5.802 | 5.8287 | 0.0267
GEN-2022-010 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 5.9518 | 5.9798 | 0.028
GEN-2022-010 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 4.0945 | 4.1078 | 0.0133
GEN-2022-010 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 3.0237 | 3.0331 | 0.0094
GEN-2022-010 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7852 | 2.7931 | 0.0079
GEN-2022-010 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6828 | 2.6901 | 0.0073
GEN-2022-010 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.9782 | 3.9944 | 0.0162
GEN-2022-010 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 7.0337 | 7.0729 | 0.0392
GEN-2022-010 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 6.4176 | 6.4502 | 0.0326
GEN-2022-010 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 8.0048 | 8.0428 | 0.038
GEN-2022-010 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.8419 | 8.8883 | 0.0464
GEN-2022-010 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.4396 | 5.4572 | 0.0176
GEN-2022-010 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 4.0188 | 4.0284 | 0.0096
GEN-2022-010 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.835 | 4.8489 | 0.0139
GEN-2022-010 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 5.8213 | 5.8481 | 0.0268
GEN-2022-010 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 13.3457 | 13.4882 | 0.1425
GEN-2022-010 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 10.0219 | 10.102 | 0.0801
GEN-2022-010 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 7.8726 | 7.922 | 0.0494
GEN-2022-010 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 5.4815 | 5.5054 | 0.0239
GEN-2022-010 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 4.2705 | 4.2848 | 0.0143
GEN-2022-010 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 5.0931 | 5.1136 | 0.0205
GEN-2022-010 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.4936 | 3.5061 | 0.0125
GEN-2022-010 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.3897 | 6.4315 | 0.0418
GEN-2022-010 | 01 NORTH | 655891 | KILLDEER-MK7 | 115 | 4.9369 | 4.9434 | 0.0065
GEN-2022-010 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 4.0744 | 4.0913 | 0.0169
GEN-2022-010 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.2497 | 6.2693 | 0.0196
GEN-2022-010 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.5452 | 3.5515 | 0.0063
GEN-2022-010 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.4141 | 4.4257 | 0.0116
GEN-2022-010 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.4731 | 3.4826 | 0.0095
GEN-2022-010 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 5.3441 | 5.3667 | 0.0226
GEN-2022-010 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1729 | 3.1788 | 0.0059
GEN-2022-010 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 6.4596 | 6.4926 | 0.033
GEN-2022-010 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 18.8215 | 19.001 | 0.1795
GEN-2022-010 | 01 NORTH | 655924 | STATELIN-MW7 | 115 | 15.3206 | 15.4451 | 0.1245
GEN-2022-010 | 01 NORTH | 655925 | JUDSON -MW7 | 115 | 15.7185 | 15.9609 | 0.2424
GEN-2022-010 | 01 NORTH | 655926 | SW.WLSTN-MW7 | 115 | 8.8176 | 8.8933 | 0.0757
GEN-2022-010 | 01 NORTH | 655931 | BLKTLTAP-MW7 | 115 | 10.4297 | 10.5543 | 0.1246
GEN-2022-010 | 01 NORTH | 655933 | N.MISRDG-MW7 | 115 | 15.5789 | 15.8767 | 0.2978
GEN-2022-010 | 01 NORTH | 655934 | N.WLST_T-MW7 | 115 | 14.2708 | 14.5197 | 0.2489
GEN-2022-010 | 01 NORTH | 655935 | NW.WLSTN-MW7 | 115 | 12.6898 | 12.8795 | 0.1897
GEN-2022-010 | 01 NORTH | 655936 | N.WILSTN-MW7 | 115 | 13.9406 | 14.1791 | 0.2385
GEN-2022-010 | 01 NORTH | 655937 | NE.WLSTN-MW7 | 115 | 12.9959 | 13.2084 | 0.2125
GEN-2022-010 | 01 NORTH | 655938 | SE.WLSTN-MW7 | 115 | 8.4216 | 8.5065 | 0.0849
GEN-2022-010 | 01 NORTH | 655940 | MONT -MW7 | 115 | 16.0598 | 16.2913 | 0.2315
GEN-2022-010 | 01 NORTH | 655941 | STRNDAHL-MW7 | 115 | 10.3183 | 10.4031 | 0.0848
GEN-2022-010 | 01 NORTH | 655945 | WHEELS_T-MW7 | 115 | 9.2604 | 9.3489 | 0.0885
GEN-2022-010 | 01 NORTH | 655955 | ZAHL -MW7 | 115 | 7.8261 | 7.8951 | 0.069
GEN-2022-010 | 01 NORTH | 655956 | TYRONE -MW7 | 115 | 12.0943 | 12.2844 | 0.1901
GEN-2022-010 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 17.9668 | 18.4367 | 0.4699
GEN-2022-010 | 01 NORTH | 655958 | FOLVAG -MW7 | 115 | 14.3151 | 14.6022 | 0.2871
GEN-2022-010 | 01 NORTH | 655966 | OLIVER -MW7 | 115 | 7.0431 | 7.0963 | 0.0532
GEN-2022-010 | 01 NORTH | 659060 | FINSTAD345 | 345 | 6.7918 | 6.8625 | 0.0707
GEN-2022-010 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 14.776 | 14.8722 | 0.0962
GEN-2022-010 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 17.1467 | 17.2086 | 0.0619
GEN-2022-010 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 23.7977 | 23.8563 | 0.0586
GEN-2022-010 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.3813 | 5.3828 | 0.0015
GEN-2022-010 | 01 NORTH | 659112 | CULBRTSN-UM7 | 115 | 4.4974 | 4.5021 | 0.0047
GEN-2022-010 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 7.3381 | 7.3528 | 0.0147
GEN-2022-010 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 12.5375 | 12.753 | 0.2155
GEN-2022-010 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 6.0878 | 6.1162 | 0.0284
GEN-2022-010 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 6.1504 | 6.1584 | 0.008
GEN-2022-010 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 7.7172 | 7.7282 | 0.011
GEN-2022-010 | 01 NORTH | 659181 | BICNTNIL-BE7 | 115 | 3.474 | 3.4778 | 0.0038
GEN-2022-010 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 14.3162 | 14.4074 | 0.0912
GEN-2022-010 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 11.0811 | 11.2699 | 0.1888
GEN-2022-010 | 01 NORTH | 659184 | ROUGHRDR-BE7 | 115 | 4.4457 | 4.453 | 0.0073
GEN-2022-010 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.747 | 3.7532 | 0.0062
GEN-2022-010 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 21.712 | 21.7605 | 0.0485
GEN-2022-010 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 14.1781 | 14.2665 | 0.0884
GEN-2022-010 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 14.776 | 14.8722 | 0.0962
GEN-2022-010 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.5259 | 9.5339 | 0.008
GEN-2022-010 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.0268 | 7.0412 | 0.0144
GEN-2022-010 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.2066 | 7.2111 | 0.0045
GEN-2022-010 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.5385 | 5.5482 | 0.0097
GEN-2022-010 | 01 NORTH | 659248 | HALLIDAY-UM7 | 115 | 4.18 | 4.1826 | 0.0026
GEN-2022-010 | 01 NORTH | 659262 | CULBSN.E-BE7 | 115 | 5.8591 | 5.8677 | 0.0086
GEN-2022-010 | 01 NORTH | 659269 | CULB_GEN-BE7 | 115 | 5.7406 | 5.7474 | 0.0068
GEN-2022-010 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.9651 | 12.1228 | 0.1577
GEN-2022-010 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.3158 | 2.3169 | 0.0011
GEN-2022-010 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 9.9055 | 9.9454 | 0.0399
GEN-2022-010 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 10.8008 | 11.9492 | 1.1484
GEN-2022-010 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 12.9593 | 13.6818 | 0.7225
GEN-2022-010 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 8.6486 | 8.8352 | 0.1866
GEN-2022-010 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 12.3892 | 12.6041 | 0.2149
GEN-2022-010 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 7.734 | 7.7452 | 0.0112
GEN-2022-010 | 01 NORTH | 659347 | PIONEER1-BE7 | 115 | 15.3206 | 15.4451 | 0.1245
GEN-2022-010 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 12.6811 | 12.7952 | 0.1141
GEN-2022-010 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 12.6812 | 12.7953 | 0.1141
GEN-2022-010 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 8.0286 | 8.1755 | 0.1469
GEN-2022-010 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 9.5429 | 9.6389 | 0.096
GEN-2022-010 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 9.8083 | 9.9551 | 0.1468
GEN-2022-010 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 11.9722 | 12.0445 | 0.0723
GEN-2022-010 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 7.8165 | 7.9642 | 0.1477
GEN-2022-010 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 14.8346 | 15.0107 | 0.1761
GEN-2022-010 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 10.2305 | 10.6199 | 0.3894
GEN-2022-010 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 19.4478 | 19.8404 | 0.3926
GEN-2022-010 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 4.769 | 4.8214 | 0.0524
GEN-2022-010 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 14.776 | 14.8722 | 0.0962
GEN-2022-010 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.1993 | 4.2002 | 0.0009
GEN-2022-010 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 17.1467 | 17.2086 | 0.0619
GEN-2022-010 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 17.1467 | 17.2086 | 0.0619
GEN-2022-010 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 8.6486 | 8.8352 | 0.1866
GEN-2022-010 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.94 | 1.9408 | 0.0008
GEN-2022-010 | 01 NORTH | 659443 | SKUNKHIL-RR7 | 115 | 1.7452 | 1.7459 | 0.0007
GEN-2022-010 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.784 | 6.7978 | 0.0138
GEN-2022-010 | 01 NORTH | 659450 | BRADYWND 4 | 230 | 3.6634 | 3.6664 | 0.003
GEN-2022-010 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 19.3437 | 19.7344 | 0.3907
GEN-2022-010 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 19.3562 | 19.7471 | 0.3909
GEN-2022-010 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 6.165 | 6.2543 | 0.0893
GEN-2022-010 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.94 | 1.9408 | 0.0008
GEN-2022-010 | 01 NORTH | 659600 | EFORK_-BE334 | 345 | 8.9199 | 9.4167 | 0.4968
GEN-2022-010 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 7.0911 | 7.1749 | 0.0838
GEN-2022-010 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 12.5375 | 12.753 | 0.2155
GEN-2022-010 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 12.8442 | 12.9552 | 0.111
GEN-2022-010 | 01 NORTH | 661087 | RAY JCT7 | 115 | 5.8229 | 5.8494 | 0.0265
GEN-2022-010 | 01 NORTH | 661089 | LTLMUDY7 | 115 | 7.1473 | 7.1959 | 0.0486
GEN-2022-010 | 01 NORTH | 672603 | BDV 4 | 230 | 5.0084 | 5.0188 | 0.0104
GEN-2022-010 | 01 NORTH | 763021 | GEN-2018-067 | 115 | 10.3183 | 10.4031 | 0.0848
GEN-2022-010 | 01 NORTH | 763703 | GEN-2019-037 | 345 | 11.0371 | 11.062 | 0.0249
GEN-2022-010 | 01 NORTH | 764180 | GEN-2020-014 | 115 | 7.734 | 7.7452 | 0.0112
GEN-2022-010 | 01 NORTH | 764225 | GEN-2020-091 | 345 | 10.0577 | 10.4329 | 0.3752
GEN-2022-010 | 01 NORTH | 765070 | GEN-2020-083 | 115 | 5.7014 | 5.7124 | 0.011
GEN-2022-010 | 01 NORTH | 767161 | GEN-2022-009 | 345 | 8.3335 | 9.8886 | 1.5551
GEN-2022-083 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.4977 | 7.5028 | 0.0051
GEN-2022-083 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 11.7293 | 11.7576 | 0.0283
GEN-2022-083 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 9.6375 | 9.7567 | 0.1192
GEN-2022-083 | 01 NORTH | 652216 | WATFORD4 | 230 | 7.1698 | 7.2555 | 0.0857
GEN-2022-083 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.103 | 1.103 | 0
GEN-2022-083 | 01 NORTH | 652391 | WILLISTON27 | 115 | 20.314 | 20.7564 | 0.4424
GEN-2022-083 | 01 NORTH | 652400 | WILISTN4 | 230 | 12.8703 | 13.5075 | 0.6372
GEN-2022-083 | 01 NORTH | 652408 | WATFORD7 | 115 | 9.2156 | 9.2661 | 0.0505
GEN-2022-083 | 01 NORTH | 652419 | KILDEER7 | 115 | 5.1119 | 5.1188 | 0.0069
GEN-2022-083 | 01 NORTH | 652421 | WILISTN7 | 115 | 20.3031 | 20.7443 | 0.4412
GEN-2022-083 | 01 NORTH | 652424 | BELFELD3 | 345 | 7.0021 | 7.047 | 0.0449
GEN-2022-083 | 01 NORTH | 652425 | BELFELD4 | 230 | 9.9055 | 9.9454 | 0.0399
GEN-2022-083 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 5.7014 | 5.7124 | 0.011
GEN-2022-083 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9749 | 0.9749 | 0
GEN-2022-083 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.9021 | 0.9021 | 0
GEN-2022-083 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.9089 | 0.9089 | 0
GEN-2022-083 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.689 | 0.689 | 0
GEN-2022-083 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6174 | 0.6174 | 0
GEN-2022-083 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1093 | 1.1093 | 0
GEN-2022-083 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.1151 | 1.1151 | 0
GEN-2022-083 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.1055 | 1.1055 | 0
GEN-2022-083 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5104 | 1.5105 | 0.0001
GEN-2022-083 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.0217 | 1.0217 | 0
GEN-2022-083 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9892 | 0.9893 | 0.0001
GEN-2022-083 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.9896 | 0.9897 | 0.0001
GEN-2022-083 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.5479 | 1.548 | 0.0001
GEN-2022-083 | 01 NORTH | 655790 | HELMUT -LY7 | 115 | 6.1042 | 6.112 | 0.0078
GEN-2022-083 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 2.0807 | 2.0822 | 0.0015
GEN-2022-083 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.8899 | 3.895 | 0.0051
GEN-2022-083 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 6.1674 | 6.2074 | 0.04
GEN-2022-083 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.1796 | 4.1884 | 0.0088
GEN-2022-083 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 4.0865 | 4.0996 | 0.0131
GEN-2022-083 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 8.0791 | 8.131 | 0.0519
GEN-2022-083 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 14.1921 | 14.2818 | 0.0897
GEN-2022-083 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 6.9628 | 6.9843 | 0.0215
GEN-2022-083 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.122 | 3.1269 | 0.0049
GEN-2022-083 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.5363 | 5.5517 | 0.0154
GEN-2022-083 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.6813 | 3.692 | 0.0107
GEN-2022-083 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.1294 | 4.1468 | 0.0174
GEN-2022-083 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 9.2156 | 9.2661 | 0.0505
GEN-2022-083 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 7.5108 | 7.5289 | 0.0181
GEN-2022-083 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.3092 | 3.3204 | 0.0112
GEN-2022-083 | 01 NORTH | 655843 | TRUEOIL -MK7 | 115 | 1.6379 | 1.6387 | 0.0008
GEN-2022-083 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.3487 | 5.378 | 0.0293
GEN-2022-083 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.7971 | 4.8108 | 0.0137
GEN-2022-083 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.2349 | 4.2532 | 0.0183
GEN-2022-083 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 4.3488 | 4.3637 | 0.0149
GEN-2022-083 | 01 NORTH | 655848 | BERG -MK7 | 115 | 5.788 | 5.8145 | 0.0265
GEN-2022-083 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 9.971 | 10.0503 | 0.0793
GEN-2022-083 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.5163 | 3.5289 | 0.0126
GEN-2022-083 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9132 | 2.9175 | 0.0043
GEN-2022-083 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5642 | 3.5706 | 0.0064
GEN-2022-083 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.3523 | 8.3874 | 0.0351
GEN-2022-083 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.5467 | 3.5566 | 0.0099
GEN-2022-083 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.9474 | 4.962 | 0.0146
GEN-2022-083 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.6638 | 6.7093 | 0.0455
GEN-2022-083 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.6006 | 2.6059 | 0.0053
GEN-2022-083 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 4.3812 | 4.3964 | 0.0152
GEN-2022-083 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.76 | 3.7711 | 0.0111
GEN-2022-083 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.34 | 2.3455 | 0.0055
GEN-2022-083 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.1677 | 3.178 | 0.0103
GEN-2022-083 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 5.802 | 5.8287 | 0.0267
GEN-2022-083 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 5.9518 | 5.9798 | 0.028
GEN-2022-083 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 4.0945 | 4.1078 | 0.0133
GEN-2022-083 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 3.0237 | 3.0331 | 0.0094
GEN-2022-083 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7852 | 2.7931 | 0.0079
GEN-2022-083 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6828 | 2.6901 | 0.0073
GEN-2022-083 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.9782 | 3.9944 | 0.0162
GEN-2022-083 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 7.0337 | 7.0729 | 0.0392
GEN-2022-083 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 6.4176 | 6.4502 | 0.0326
GEN-2022-083 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 8.0048 | 8.0428 | 0.038
GEN-2022-083 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.8419 | 8.8883 | 0.0464
GEN-2022-083 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.4396 | 5.4572 | 0.0176
GEN-2022-083 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 4.0188 | 4.0284 | 0.0096
GEN-2022-083 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.835 | 4.8489 | 0.0139
GEN-2022-083 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 5.8213 | 5.8481 | 0.0268
GEN-2022-083 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 13.3457 | 13.4882 | 0.1425
GEN-2022-083 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 10.0219 | 10.102 | 0.0801
GEN-2022-083 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 7.8726 | 7.922 | 0.0494
GEN-2022-083 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 5.4815 | 5.5054 | 0.0239
GEN-2022-083 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 4.2705 | 4.2848 | 0.0143
GEN-2022-083 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 5.0931 | 5.1136 | 0.0205
GEN-2022-083 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.4936 | 3.5061 | 0.0125
GEN-2022-083 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.3897 | 6.4315 | 0.0418
GEN-2022-083 | 01 NORTH | 655891 | KILLDEER-MK7 | 115 | 4.9369 | 4.9434 | 0.0065
GEN-2022-083 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 4.0744 | 4.0913 | 0.0169
GEN-2022-083 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.2497 | 6.2693 | 0.0196
GEN-2022-083 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.5452 | 3.5515 | 0.0063
GEN-2022-083 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.4141 | 4.4257 | 0.0116
GEN-2022-083 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.4731 | 3.4826 | 0.0095
GEN-2022-083 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 5.3441 | 5.3667 | 0.0226
GEN-2022-083 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1729 | 3.1788 | 0.0059
GEN-2022-083 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 6.4596 | 6.4926 | 0.033
GEN-2022-083 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 18.8215 | 19.001 | 0.1795
GEN-2022-083 | 01 NORTH | 655924 | STATELIN-MW7 | 115 | 15.3206 | 15.4451 | 0.1245
GEN-2022-083 | 01 NORTH | 655925 | JUDSON -MW7 | 115 | 15.7185 | 15.9609 | 0.2424
GEN-2022-083 | 01 NORTH | 655926 | SW.WLSTN-MW7 | 115 | 8.8176 | 8.8933 | 0.0757
GEN-2022-083 | 01 NORTH | 655931 | BLKTLTAP-MW7 | 115 | 10.4297 | 10.5543 | 0.1246
GEN-2022-083 | 01 NORTH | 655933 | N.MISRDG-MW7 | 115 | 15.5789 | 15.8767 | 0.2978
GEN-2022-083 | 01 NORTH | 655934 | N.WLST_T-MW7 | 115 | 14.2708 | 14.5197 | 0.2489
GEN-2022-083 | 01 NORTH | 655935 | NW.WLSTN-MW7 | 115 | 12.6898 | 12.8795 | 0.1897
GEN-2022-083 | 01 NORTH | 655936 | N.WILSTN-MW7 | 115 | 13.9406 | 14.1791 | 0.2385
GEN-2022-083 | 01 NORTH | 655937 | NE.WLSTN-MW7 | 115 | 12.9959 | 13.2084 | 0.2125
GEN-2022-083 | 01 NORTH | 655938 | SE.WLSTN-MW7 | 115 | 8.4216 | 8.5065 | 0.0849
GEN-2022-083 | 01 NORTH | 655940 | MONT -MW7 | 115 | 16.0598 | 16.2913 | 0.2315
GEN-2022-083 | 01 NORTH | 655941 | STRNDAHL-MW7 | 115 | 10.3183 | 10.4031 | 0.0848
GEN-2022-083 | 01 NORTH | 655945 | WHEELS_T-MW7 | 115 | 9.2604 | 9.3489 | 0.0885
GEN-2022-083 | 01 NORTH | 655955 | ZAHL -MW7 | 115 | 7.8261 | 7.8951 | 0.069
GEN-2022-083 | 01 NORTH | 655956 | TYRONE -MW7 | 115 | 12.0943 | 12.2844 | 0.1901
GEN-2022-083 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 17.9668 | 18.4367 | 0.4699
GEN-2022-083 | 01 NORTH | 655958 | FOLVAG -MW7 | 115 | 14.3151 | 14.6022 | 0.2871
GEN-2022-083 | 01 NORTH | 655966 | OLIVER -MW7 | 115 | 7.0431 | 7.0963 | 0.0532
GEN-2022-083 | 01 NORTH | 659060 | FINSTAD345 | 345 | 6.7918 | 6.8625 | 0.0707
GEN-2022-083 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 14.776 | 14.8722 | 0.0962
GEN-2022-083 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 17.1467 | 17.2086 | 0.0619
GEN-2022-083 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 23.7977 | 23.8563 | 0.0586
GEN-2022-083 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.3813 | 5.3828 | 0.0015
GEN-2022-083 | 01 NORTH | 659112 | CULBRTSN-UM7 | 115 | 4.4974 | 4.5021 | 0.0047
GEN-2022-083 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 7.3381 | 7.3528 | 0.0147
GEN-2022-083 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 12.5375 | 12.753 | 0.2155
GEN-2022-083 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 6.0878 | 6.1162 | 0.0284
GEN-2022-083 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 6.1504 | 6.1584 | 0.008
GEN-2022-083 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 7.7172 | 7.7282 | 0.011
GEN-2022-083 | 01 NORTH | 659181 | BICNTNIL-BE7 | 115 | 3.474 | 3.4778 | 0.0038
GEN-2022-083 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 14.3162 | 14.4074 | 0.0912
GEN-2022-083 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 11.0811 | 11.2699 | 0.1888
GEN-2022-083 | 01 NORTH | 659184 | ROUGHRDR-BE7 | 115 | 4.4457 | 4.453 | 0.0073
GEN-2022-083 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.747 | 3.7532 | 0.0062
GEN-2022-083 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 21.712 | 21.7605 | 0.0485
GEN-2022-083 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 14.1781 | 14.2665 | 0.0884
GEN-2022-083 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 14.776 | 14.8722 | 0.0962
GEN-2022-083 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.5259 | 9.5339 | 0.008
GEN-2022-083 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.0268 | 7.0412 | 0.0144
GEN-2022-083 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.2066 | 7.2111 | 0.0045
GEN-2022-083 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.5385 | 5.5482 | 0.0097
GEN-2022-083 | 01 NORTH | 659248 | HALLIDAY-UM7 | 115 | 4.18 | 4.1826 | 0.0026
GEN-2022-083 | 01 NORTH | 659262 | CULBSN.E-BE7 | 115 | 5.8591 | 5.8677 | 0.0086
GEN-2022-083 | 01 NORTH | 659269 | CULB_GEN-BE7 | 115 | 5.7406 | 5.7474 | 0.0068
GEN-2022-083 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 11.9651 | 12.1228 | 0.1577
GEN-2022-083 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.3158 | 2.3169 | 0.0011
GEN-2022-083 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 9.9055 | 9.9454 | 0.0399
GEN-2022-083 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 10.8008 | 11.9492 | 1.1484
GEN-2022-083 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 12.9593 | 13.6818 | 0.7225
GEN-2022-083 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 8.6486 | 8.8352 | 0.1866
GEN-2022-083 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 12.3892 | 12.6041 | 0.2149
GEN-2022-083 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 7.734 | 7.7452 | 0.0112
GEN-2022-083 | 01 NORTH | 659347 | PIONEER1-BE7 | 115 | 15.3206 | 15.4451 | 0.1245
GEN-2022-083 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 12.6811 | 12.7952 | 0.1141
GEN-2022-083 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 12.6812 | 12.7953 | 0.1141
GEN-2022-083 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 8.0286 | 8.1755 | 0.1469
GEN-2022-083 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 9.5429 | 9.6389 | 0.096
GEN-2022-083 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 9.8083 | 9.9551 | 0.1468
GEN-2022-083 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 11.9722 | 12.0445 | 0.0723
GEN-2022-083 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 7.8165 | 7.9642 | 0.1477
GEN-2022-083 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 14.8346 | 15.0107 | 0.1761
GEN-2022-083 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 10.2305 | 10.6199 | 0.3894
GEN-2022-083 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 19.4478 | 19.8404 | 0.3926
GEN-2022-083 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 4.769 | 4.8214 | 0.0524
GEN-2022-083 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 14.776 | 14.8722 | 0.0962
GEN-2022-083 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.1993 | 4.2002 | 0.0009
GEN-2022-083 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 17.1467 | 17.2086 | 0.0619
GEN-2022-083 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 17.1467 | 17.2086 | 0.0619
GEN-2022-083 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 8.6486 | 8.8352 | 0.1866
GEN-2022-083 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.94 | 1.9408 | 0.0008
GEN-2022-083 | 01 NORTH | 659443 | SKUNKHIL-RR7 | 115 | 1.7452 | 1.7459 | 0.0007
GEN-2022-083 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.784 | 6.7978 | 0.0138
GEN-2022-083 | 01 NORTH | 659450 | BRADYWND 4 | 230 | 3.6634 | 3.6664 | 0.003
GEN-2022-083 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 19.3437 | 19.7344 | 0.3907
GEN-2022-083 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 19.3562 | 19.7471 | 0.3909
GEN-2022-083 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 6.165 | 6.2543 | 0.0893
GEN-2022-083 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.94 | 1.9408 | 0.0008
GEN-2022-083 | 01 NORTH | 659600 | EFORK_-BE334 | 345 | 8.9199 | 9.4167 | 0.4968
GEN-2022-083 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 7.0911 | 7.1749 | 0.0838
GEN-2022-083 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 12.5375 | 12.753 | 0.2155
GEN-2022-083 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 12.8442 | 12.9552 | 0.111
GEN-2022-083 | 01 NORTH | 661087 | RAY JCT7 | 115 | 5.8229 | 5.8494 | 0.0265
GEN-2022-083 | 01 NORTH | 661089 | LTLMUDY7 | 115 | 7.1473 | 7.1959 | 0.0486
GEN-2022-083 | 01 NORTH | 672603 | BDV 4 | 230 | 5.0084 | 5.0188 | 0.0104
GEN-2022-083 | 01 NORTH | 763021 | GEN-2018-067 | 115 | 10.3183 | 10.4031 | 0.0848
GEN-2022-083 | 01 NORTH | 763703 | GEN-2019-037 | 345 | 11.0371 | 11.062 | 0.0249
GEN-2022-083 | 01 NORTH | 764180 | GEN-2020-014 | 115 | 7.734 | 7.7452 | 0.0112
GEN-2022-083 | 01 NORTH | 764225 | GEN-2020-091 | 345 | 10.0577 | 10.4329 | 0.3752
GEN-2022-083 | 01 NORTH | 765070 | GEN-2020-083 | 115 | 5.7014 | 5.7124 | 0.011
GEN-2022-083 | 01 NORTH | 767161 | GEN-2022-009 | 345 | 8.3335 | 9.8886 | 1.5551

## SCRCCT Results
Region | GI Number | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | WSCR | WSCR PASS/FAIL | EMT Anlaysis Needed
03 CENTRAL | GEN-2022-013 | 4.9781 | FAIL | 23.1304 | PASS | None | PASS | YES
03 CENTRAL | GEN-2022-024 | 4.9781 | FAIL | 46.3643 | PASS | None | PASS | YES
03 CENTRAL | GEN-2022-054 | 6.8827 | PASS | 0.2836 | PASS | None | PASS | NO
03 CENTRAL | GEN-2022-161 | 4.4076 | FAIL | 0.2489 | PASS | None | PASS | YES
03 CENTRAL | GEN-2022-015 | 4.7284 | FAIL | 36.0887 | PASS | None | PASS | YES
03 CENTRAL | GEN-2022-065 | 6.7314 | PASS | 4.8423 | PASS | None | PASS | NO
03 CENTRAL | GEN-2022-007 | 2.231 | FAIL | 11.7095 | PASS | None | PASS | YES
03 CENTRAL | GEN-2022-005 | 3.4196 | FAIL | 9.7959 | PASS | None | PASS | YES
03 CENTRAL | GEN-2022-214 | 6.4857 | PASS | 11.5745 | PASS | None | PASS | NO
04 SOUTHEAST | GEN-2022-012 | 4.3941 | FAIL | 33.4177 | PASS | None | PASS | YES
04 SOUTHEAST | GEN-2022-016 | 4.3941 | FAIL | 29.7318 | PASS | None | PASS | YES
04 SOUTHEAST | GEN-2022-017 | 4.3941 | FAIL | 33.271 | PASS | None | PASS | YES
04 SOUTHEAST | GEN-2022-038 | 5.6019 | FAIL | 0.2269 | PASS | None | PASS | YES
04 SOUTHEAST | GEN-2022-055 | 4.141 | FAIL | 11.055 | PASS | None | PASS | YES
04 SOUTHEAST | GEN-2022-098 | 4.4909 | FAIL | 10.8727 | PASS | None | PASS | YES
04 SOUTHEAST | GEN-2022-136 | 4.5802 | FAIL | 4.7914 | PASS | 3.0791 | FAIL | YES
04 SOUTHEAST | GEN-2022-145 | 3.1083 | FAIL | 2.6329 | PASS | 4.3808 | FAIL | YES
04 SOUTHEAST | GEN-2022-176 | 1.923 | FAIL | 0.1083 | FAIL | None | PASS | YES
04 SOUTHEAST | GEN-2022-234 | 1.97 | FAIL | 4.0985 | PASS | None | PASS | YES
04 SOUTHEAST | GEN-2022-143 | 8.6355 | PASS | 5.2572 | PASS | 3.0791 | FAIL | YES
04 SOUTHEAST | GEN-2022-071 | 8.8982 | PASS | 17.2955 | PASS | None | PASS | NO
04 SOUTHEAST | GEN-2022-104 | 2.9507 | FAIL | 12.2658 | PASS | 3.0791 | FAIL | YES
04 SOUTHEAST | GEN-2022-235 | 8.6065 | PASS | 5.5348 | PASS | 4.3808 | FAIL | YES
04 SOUTHEAST | GEN-2022-231 | 5.4501 | FAIL | 21.9031 | PASS | None | PASS | YES
04 SOUTHEAST | GEN-2022-111 | 40.2817 | PASS | 6.5921 | PASS | None | PASS | NO
04 SOUTHEAST | GEN-2022-130 | 12.529 | PASS | 5.2347 | PASS | None | PASS | NO
04 SOUTHEAST | GEN-2022-139 | 23.085 | PASS | 7.2306 | PASS | None | PASS | NO
04 SOUTHEAST | GEN-2022-154 | 25.6921 | PASS | 17.4513 | PASS | None | PASS | NO
04 SOUTHEAST | GEN-2022-155 | 18.7726 | PASS | 18.3513 | PASS | None | PASS | NO
04 SOUTHEAST | GEN-2022-156 | 12.0714 | PASS | 17.5346 | PASS | None | PASS | NO
04 SOUTHEAST | GEN-2022-238 | 12.6206 | PASS | 4.922 | PASS | None | PASS | NO

## SCRCCT
Study Name | Group | Season | Gen Number | POI | Contingency | SCR | SCR PASS/FAIL | CCT | CCT PASS/FAIL | Stability Margin | Pg_out | Pg_rated
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | base | 139.1205 | PASS | 13.8713 | PASS | 13771.2534 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | base | 14.1777 | PASS | 9.8589 | PASS | 9758.8701 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | base | 27.2804 | PASS | 11.0767 | PASS | 10976.7307 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | base | 20.5347 | PASS | 11.8823 | PASS | 11782.2825 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | base | 6.0206 | PASS | 23.2123 | PASS | 23112.2525 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | base | 6.0206 | PASS | 23.2123 | PASS | 23112.2525 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | base | 6.0206 | PASS | 46.772 | PASS | 46671.9724 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | base | 11.0062 | PASS | 36.5452 | PASS | 36445.1637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | base | 11.0062 | PASS | 36.5452 | PASS | 36445.1637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | base | 13.5932 | PASS | 0.3026 | PASS | 202.5502 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | base | 15.5267 | PASS | 5.0446 | PASS | 4944.6259 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | base | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | base | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | base | 21.1112 | PASS | 2.9858 | PASS | 2885.768 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | base | 24.8224 | PASS | 6.06 | PASS | 5959.9818 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | base | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | base | 40.9012 | PASS | 14.7199 | PASS | 14619.9402 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | base | 23.9769 | PASS | 5.4618 | PASS | 5361.8197 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | base | 23.5573 | PASS | 5.4527 | PASS | 5352.7408 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | base | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | base | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | base | 12.3284 | PASS | 11.7269 | PASS | 11626.9273 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | base | 12.3284 | PASS | 11.7269 | PASS | 11626.9273 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 139.123 | PASS | 13.8715 | PASS | 13771.4929 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 14.1778 | PASS | 9.859 | PASS | 9758.9554 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 27.2804 | PASS | 11.0769 | PASS | 10976.868 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2613 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.3894 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.3894 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 6.0206 | PASS | 46.7721 | PASS | 46672.0902 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1658 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1658 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 13.5932 | PASS | 0.3025 | PASS | 202.4976 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 15.5267 | PASS | 5.0447 | PASS | 4944.733 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 25.9296 | PASS | 1.6856 | PASS | 1585.5544 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 25.9296 | PASS | 1.6856 | PASS | 1585.5544 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 21.111 | PASS | 2.9857 | PASS | 2885.6879 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 24.8006 | PASS | 6.0579 | PASS | 5957.8553 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 24.8006 | PASS | 1.7196 | PASS | 1619.5988 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 40.689 | PASS | 14.7114 | PASS | 14611.4078 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 23.9225 | PASS | 5.4549 | PASS | 5354.9055 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 22.9006 | PASS | 5.4205 | PASS | 5320.5465 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 9.4882 | PASS | 0.2604 | PASS | 160.4437 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 9.4882 | PASS | 0.2489 | PASS | 148.9369 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 12.3286 | PASS | 11.7271 | PASS | 11627.0923 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 12.3286 | PASS | 11.7271 | PASS | 11627.0923 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 138.4354 | PASS | 13.8246 | PASS | 13724.5591 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 13.921 | PASS | 9.8225 | PASS | 9722.4714 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 26.3528 | PASS | 11.0438 | PASS | 10943.7978 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 20.5221 | PASS | 11.8784 | PASS | 11778.4182 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 5.8384 | FAIL | 23.1936 | PASS | 23093.6239 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 5.8384 | FAIL | 23.1936 | PASS | 23093.6239 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 5.8384 | FAIL | 47.4441 | PASS | 47344.1164 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 11.0045 | PASS | 36.5425 | PASS | 36442.4973 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 11.0045 | PASS | 36.5425 | PASS | 36442.4973 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.6495 | PASS | 0.3026 | PASS | 202.6174 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 15.5188 | PASS | 5.0358 | PASS | 4935.7745 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 26.021 | PASS | 1.6862 | PASS | 1586.2346 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 26.021 | PASS | 1.6862 | PASS | 1586.2346 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 21.1081 | PASS | 2.9849 | PASS | 2884.8664 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 24.8184 | PASS | 6.059 | PASS | 5958.9853 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 24.8184 | PASS | 1.7195 | PASS | 1619.5268 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 40.8914 | PASS | 14.7181 | PASS | 14618.0704 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 23.9718 | PASS | 5.4595 | PASS | 5359.4869 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 23.5506 | PASS | 5.4499 | PASS | 5349.8846 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 9.4623 | PASS | 0.2604 | PASS | 160.4257 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 9.4623 | PASS | 0.2489 | PASS | 148.9134 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.2835 | PASS | 11.6999 | PASS | 11599.9244 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300740 [7SPORTSMAN 345.00] CKT 1 | 12.2835 | PASS | 11.6999 | PASS | 11599.9244 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 138.5746 | PASS | 13.8528 | PASS | 13752.7842 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 13.8925 | PASS | 9.8371 | PASS | 9737.111 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 26.1321 | PASS | 11.0532 | PASS | 10953.2436 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 20.5257 | PASS | 11.8806 | PASS | 11780.555 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 5.7751 | FAIL | 23.1989 | PASS | 23098.9195 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 5.7751 | FAIL | 23.1989 | PASS | 23098.9195 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 5.7751 | FAIL | 47.3357 | PASS | 47235.7086 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 11.0034 | PASS | 36.5416 | PASS | 36441.5877 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 11.0034 | PASS | 36.5416 | PASS | 36441.5877 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.2632 | PASS | 0.305 | PASS | 204.951 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 15.5229 | PASS | 5.0422 | PASS | 4942.2142 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 26.0182 | PASS | 1.6855 | PASS | 1585.4634 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 26.0182 | PASS | 1.6855 | PASS | 1585.4634 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 21.0935 | PASS | 2.977 | PASS | 2876.9716 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 24.8063 | PASS | 6.0569 | PASS | 5956.862 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 24.8063 | PASS | 1.7197 | PASS | 1619.667 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 40.8838 | PASS | 14.7146 | PASS | 14614.5699 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 23.9677 | PASS | 5.4546 | PASS | 5354.5521 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 23.5487 | PASS | 5.4465 | PASS | 5346.4789 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 9.4756 | PASS | 0.2604 | PASS | 160.4446 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 9.4756 | PASS | 0.2489 | PASS | 148.9379 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.3 | PASS | 11.7172 | PASS | 11617.2365 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 300949 [7JASPER 345.00] CKT 1 | 12.3 | PASS | 11.7172 | PASS | 11617.2365 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 138.6744 | PASS | 13.8545 | PASS | 13754.5115 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 13.0066 | PASS | 9.8141 | PASS | 9714.0579 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 22.5358 | PASS | 11.0359 | PASS | 10935.8904 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 20.5203 | PASS | 11.8791 | PASS | 11779.1347 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 5.0121 | FAIL | 23.199 | PASS | 23098.9569 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 5.0121 | FAIL | 23.199 | PASS | 23098.9569 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 5.0121 | FAIL | 52.1491 | PASS | 52049.0809 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 11.0052 | PASS | 36.5444 | PASS | 36444.367 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 11.0052 | PASS | 36.5444 | PASS | 36444.367 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.324 | PASS | 0.3106 | PASS | 210.6257 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 15.5234 | PASS | 5.0422 | PASS | 4942.1807 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 26.0213 | PASS | 1.6861 | PASS | 1586.103 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 26.0213 | PASS | 1.6861 | PASS | 1586.103 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 21.105 | PASS | 2.9834 | PASS | 2883.3695 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 24.8207 | PASS | 6.0595 | PASS | 5959.5434 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 24.8207 | PASS | 1.7195 | PASS | 1619.4894 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 40.8918 | PASS | 14.7176 | PASS | 14617.5716 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 23.9715 | PASS | 5.4586 | PASS | 5358.6037 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 23.553 | PASS | 5.4501 | PASS | 5350.0711 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 9.4745 | PASS | 0.2604 | PASS | 160.4403 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 9.4745 | PASS | 0.2489 | PASS | 148.9324 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.3048 | PASS | 11.7177 | PASS | 11617.743 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.3048 | PASS | 11.7177 | PASS | 11617.743 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 139.1197 | PASS | 13.8712 | PASS | 13771.2068 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 14.1773 | PASS | 9.8588 | PASS | 9758.7713 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 27.2793 | PASS | 11.0766 | PASS | 10976.6258 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 20.5345 | PASS | 11.8823 | PASS | 11782.2554 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 6.0204 | PASS | 23.2121 | PASS | 23112.1497 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 6.0204 | PASS | 23.2121 | PASS | 23112.1497 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 6.0204 | PASS | 46.7722 | PASS | 46672.2381 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0577 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0577 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 13.5928 | PASS | 0.3026 | PASS | 202.5619 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 15.5266 | PASS | 5.0446 | PASS | 4944.6064 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 26.0007 | PASS | 1.6863 | PASS | 1586.3092 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 26.0007 | PASS | 1.6863 | PASS | 1586.3092 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 21.1106 | PASS | 2.9854 | PASS | 2885.4241 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 24.8199 | PASS | 6.0612 | PASS | 5961.1537 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 24.8199 | PASS | 1.7194 | PASS | 1619.3811 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 40.6275 | PASS | 14.722 | PASS | 14622.0019 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 23.971 | PASS | 5.459 | PASS | 5359.0361 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 21.893 | PASS | 5.4556 | PASS | 5355.6169 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9212 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9212 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 139.1125 | PASS | 13.8704 | PASS | 13770.4351 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 14.1764 | PASS | 9.8583 | PASS | 9758.3139 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 27.2771 | PASS | 11.0759 | PASS | 10975.8722 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 20.5346 | PASS | 11.8822 | PASS | 11782.2367 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 6.02 | PASS | 23.2113 | PASS | 23111.3178 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 6.02 | PASS | 23.2113 | PASS | 23111.3178 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 6.02 | PASS | 46.7709 | PASS | 46670.9471 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.159 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.159 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 13.5909 | PASS | 0.3028 | PASS | 202.8313 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 15.5265 | PASS | 5.0443 | PASS | 4944.2992 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 26.026 | PASS | 1.6867 | PASS | 1586.7459 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 26.026 | PASS | 1.6867 | PASS | 1586.7459 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 21.1117 | PASS | 2.986 | PASS | 2885.9908 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 24.4633 | PASS | 6.061 | PASS | 5960.9511 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 24.4633 | PASS | 1.7192 | PASS | 1619.2228 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 40.8999 | PASS | 14.7206 | PASS | 14620.6292 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 23.9761 | PASS | 5.4626 | PASS | 5362.5655 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 23.5562 | PASS | 5.4538 | PASS | 5353.84 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 9.4873 | PASS | 0.2604 | PASS | 160.4428 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 9.4873 | PASS | 0.2489 | PASS | 148.9358 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 12.3277 | PASS | 11.7264 | PASS | 11626.3862 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 12.3277 | PASS | 11.7264 | PASS | 11626.3862 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 139.1178 | PASS | 1387% | PASS | 13770.9849 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 14.1773 | PASS | 9.8587 | PASS | 9758.7126 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 27.2795 | PASS | 1108% | PASS | 10976.5285 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2697 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 6.0204 | PASS | 23.2121 | PASS | 23112.0578 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 6.0204 | PASS | 23.2121 | PASS | 23112.0578 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 6.0204 | PASS | 46.7717 | PASS | 46671.6632 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1063 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1063 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 13.5928 | PASS | 0.3026 | PASS | 202.5997 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.5122 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 26.0247 | PASS | 1.6868 | PASS | 1586.8422 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 26.0247 | PASS | 1.6868 | PASS | 1586.8422 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 21.1111 | PASS | 2.9857 | PASS | 2885.6741 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 24.2528 | PASS | 6.0852 | PASS | 5985.2107 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 24.2528 | PASS | 1.7175 | PASS | 1617.5217 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 40.8987 | PASS | 14.7212 | PASS | 14621.2465 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 23.9757 | PASS | 5.4632 | PASS | 5363.1667 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 23.554 | PASS | 5.4549 | PASS | 5354.8693 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 9.4877 | PASS | 0.2604 | PASS | 160.4433 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 9.4877 | PASS | 0.2489 | PASS | 148.9364 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 12.3282 | PASS | 11.7268 | PASS | 11626.7583 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT 1 | 12.3282 | PASS | 11.7268 | PASS | 11626.7583 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 139.1141 | PASS | 13.8706 | PASS | 13770.595 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 14.1767 | PASS | 9.8584 | PASS | 9758.4458 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 27.2778 | PASS | 11.076 | PASS | 10976.0422 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 20.5347 | PASS | 11.8823 | PASS | 11782.2593 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 6.0201 | PASS | 23.2115 | PASS | 23111.484 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 6.0201 | PASS | 23.2115 | PASS | 23111.484 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 6.0201 | PASS | 46.7711 | PASS | 46671.091 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 11.0062 | PASS | 36.5452 | PASS | 36445.2083 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 11.0062 | PASS | 36.5452 | PASS | 36445.2083 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 13.5913 | PASS | 0.3028 | PASS | 202.7958 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 15.5265 | PASS | 5.0444 | PASS | 4944.3666 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 26.0275 | PASS | 1.6869 | PASS | 1586.8978 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 26.0275 | PASS | 1.6869 | PASS | 1586.8978 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 21.1119 | PASS | 2.9861 | PASS | 2886.1121 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 20.8867 | PASS | 5.9463 | PASS | 5846.3122 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 20.8867 | PASS | 1.7256 | PASS | 1625.5908 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 40.9027 | PASS | 14.721 | PASS | 14620.9778 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 23.9774 | PASS | 5.4635 | PASS | 5363.4887 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 23.5588 | PASS | 5.4539 | PASS | 5353.9273 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 9.4874 | PASS | 0.2604 | PASS | 160.4429 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 9.4874 | PASS | 0.2489 | PASS | 148.9359 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 12.3278 | PASS | 11.7265 | PASS | 11626.4817 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345411 [5OVERTON 2 161.00] CKT Z | 12.3278 | PASS | 11.7265 | PASS | 11626.4817 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 139.1205 | PASS | 13.8713 | PASS | 13771.2555 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.869 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7274 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2818 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2484 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2484 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46671.9579 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1633 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1633 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5515 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6265 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.603 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.603 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7665 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 24.8179 | PASS | 6.0569 | PASS | 5956.9034 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 24.8179 | PASS | 1.7197 | PASS | 1619.6663 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 40.9007 | PASS | 14.7198 | PASS | 14619.8021 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 23.9767 | PASS | 5.4617 | PASS | 5361.6757 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 23.557 | PASS | 5.4525 | PASS | 5352.5092 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9286 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9286 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 139.1205 | PASS | 13.8713 | PASS | 13771.2555 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 14.1776 | PASS | 9.8589 | PASS | 9758.8693 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 27.2804 | PASS | 11.0767 | PASS | 10976.7281 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 20.5347 | PASS | 11.8823 | PASS | 11782.282 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 6.0206 | PASS | 23.2122 | PASS | 23112.2496 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 6.0206 | PASS | 23.2122 | PASS | 23112.2496 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 6.0206 | PASS | 46.772 | PASS | 46671.9555 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.1634 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.1634 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 13.5932 | PASS | 0.3026 | PASS | 202.5513 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 15.5267 | PASS | 5.0446 | PASS | 4944.6265 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 26.028 | PASS | 1.6866 | PASS | 1586.6058 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 26.028 | PASS | 1.6866 | PASS | 1586.6058 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 21.1112 | PASS | 2.9858 | PASS | 2885.7666 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 24.8185 | PASS | 6.0573 | PASS | 5957.2734 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 24.8185 | PASS | 1.7196 | PASS | 1619.6416 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 40.9008 | PASS | 14.7198 | PASS | 14619.8191 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 23.9767 | PASS | 5.4617 | PASS | 5361.6931 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 23.557 | PASS | 5.4525 | PASS | 5352.5371 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 12.3284 | PASS | 11.7269 | PASS | 11626.9287 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 346117 [2OVERTON 69.000] CKT 2 | 12.3284 | PASS | 11.7269 | PASS | 11626.9287 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 139.1181 | PASS | 13.8716 | PASS | 13771.5954 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8895 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 27.2805 | PASS | 11.0767 | PASS | 10976.7493 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 20.5348 | PASS | 11.8824 | PASS | 11782.363 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2744 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2744 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 6.0206 | PASS | 46.7722 | PASS | 46672.2383 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 11.0068 | PASS | 36.5447 | PASS | 36444.6787 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 11.0068 | PASS | 36.5447 | PASS | 36444.6787 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 13.5932 | PASS | 0.3025 | PASS | 202.5477 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 15.0045 | PASS | 5.0654 | PASS | 4965.3698 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6259 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6259 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 20.1975 | PASS | 2.9679 | PASS | 2867.8779 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9809 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.939 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8177 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7398 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 9.4877 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 9.4877 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 12.3284 | PASS | 11.7271 | PASS | 11627.134 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530584 [POSTROCK6 230.00] CKT 1 | 12.3284 | PASS | 11.7271 | PASS | 11627.134 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 139.0837 | PASS | 13.8704 | PASS | 13770.4173 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.8269 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 27.2801 | PASS | 11.0767 | PASS | 10976.689 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 20.5334 | PASS | 11.8821 | PASS | 11782.0693 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2025 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2025 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 6.0205 | PASS | 46.7734 | PASS | 46673.3595 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 11.0055 | PASS | 36.5439 | PASS | 36443.9216 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 11.0055 | PASS | 36.5439 | PASS | 36443.9216 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5568 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 14.4628 | PASS | 5.0068 | PASS | 4906.7652 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6172 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6172 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 19.9331 | PASS | 3.0047 | PASS | 2904.7416 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9788 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4605 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9038 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7716 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7038 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 9.4857 | PASS | 0.2604 | PASS | 160.4428 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 9.4857 | PASS | 0.2489 | PASS | 148.9357 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 12.3262 | PASS | 11.7264 | PASS | 11626.3978 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 12.3262 | PASS | 11.7264 | PASS | 11626.3978 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 138.8146 | PASS | 13.8717 | PASS | 13771.6781 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 14.1841 | PASS | 9.8623 | PASS | 9762.2797 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 27.2885 | PASS | 11.0798 | PASS | 10979.7855 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 20.5224 | PASS | 11.8815 | PASS | 11781.5117 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 6.0217 | PASS | 23.2152 | PASS | 23115.2412 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 6.0217 | PASS | 23.2152 | PASS | 23115.2412 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 6.0217 | PASS | 46.7792 | PASS | 46679.1655 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 10.966 | PASS | 36.4993 | PASS | 36399.2896 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 10.966 | PASS | 36.4993 | PASS | 36399.2896 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 13.5908 | PASS | 0.3026 | PASS | 202.6028 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 14.8681 | PASS | 5.0193 | PASS | 4919.2986 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 26.0126 | PASS | 1.6849 | PASS | 1584.8879 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 26.0126 | PASS | 1.6849 | PASS | 1584.8879 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 15.8729 | PASS | 3.0428 | PASS | 2942.7759 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 24.8213 | PASS | 6.0594 | PASS | 5959.402 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 24.8213 | PASS | 1.7195 | PASS | 1619.4991 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 40.8777 | PASS | 14.7128 | PASS | 14612.8087 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 23.9652 | PASS | 5.4527 | PASS | 5352.682 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 23.547 | PASS | 5.4452 | PASS | 5345.1617 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 9.4699 | PASS | 0.2604 | PASS | 160.4496 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 9.4699 | PASS | 0.2489 | PASS | 148.9445 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 12.3075 | PASS | 11.7253 | PASS | 11625.2952 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 560082 [G16-050-TAP 345.00] CKT 1 | 12.3075 | PASS | 11.7253 | PASS | 11625.2952 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 139.1389 | PASS | 13.8731 | PASS | 13773.0742 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 14.1788 | PASS | 9.8594 | PASS | 9759.4145 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 27.283 | PASS | 11.0775 | PASS | 10977.4764 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 20.5349 | PASS | 11.8824 | PASS | 11782.3847 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 6.0209 | PASS | 23.2129 | PASS | 23112.9381 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 6.0209 | PASS | 23.2129 | PASS | 23112.9381 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 6.0209 | PASS | 46.7734 | PASS | 46673.3596 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 11.008 | PASS | 36.5478 | PASS | 36447.8069 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 11.008 | PASS | 36.5478 | PASS | 36447.8069 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 13.5949 | PASS | 0.3023 | PASS | 202.3189 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 15.5289 | PASS | 5.0474 | PASS | 4947.3975 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6099 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6099 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 21.1176 | PASS | 2.9881 | PASS | 2888.1369 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 24.8218 | PASS | 6.0597 | PASS | 5959.6979 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 24.8218 | PASS | 1.7195 | PASS | 1619.4793 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.8771 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 23.9768 | PASS | 5.4617 | PASS | 5361.7494 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 23.5571 | PASS | 5.4526 | PASS | 5352.6002 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 9.4885 | PASS | 0.2604 | PASS | 160.4441 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 9.4885 | PASS | 0.2489 | PASS | 148.9375 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 12.3304 | PASS | 11.7284 | PASS | 11628.3722 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 765990 [GEN-2021-076345.00] CKT 1 | 12.3304 | PASS | 11.7284 | PASS | 11628.3722 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 139.1311 | PASS | 13.8713 | PASS | 13771.341 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.8254 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 27.2802 | PASS | 11.0767 | PASS | 10976.6694 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 20.5248 | PASS | 11.8824 | PASS | 11782.3621 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2052 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2052 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 6.0205 | PASS | 46.7721 | PASS | 46672.0996 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 11.0067 | PASS | 36.5446 | PASS | 36444.5904 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 11.0067 | PASS | 36.5446 | PASS | 36444.5904 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 13.5931 | PASS | 0.3026 | PASS | 202.5723 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 15.3994 | PASS | 5.0558 | PASS | 4955.7556 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 26.0276 | PASS | 1.6866 | PASS | 1586.5785 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 26.0276 | PASS | 1.6866 | PASS | 1586.5785 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 16.4311 | PASS | 3.062 | PASS | 2962.0239 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9805 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4605 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 40.9005 | PASS | 14.7197 | PASS | 14619.7468 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 23.9765 | PASS | 5.4616 | PASS | 5361.572 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 23.557 | PASS | 5.4526 | PASS | 5352.5517 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 9.4845 | PASS | 0.2604 | PASS | 160.4431 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 9.4845 | PASS | 0.2489 | PASS | 148.9362 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 12.3294 | PASS | 11.727 | PASS | 11626.9569 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 530584 [POSTROCK6 230.00] TO BUS 530673 [POSTROCK1 13.800] CKT 1 | 12.3294 | PASS | 11.727 | PASS | 11626.9569 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 139.1168 | PASS | 13.8703 | PASS | 13770.3008 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.7967 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 27.2802 | PASS | 11.0767 | PASS | 10976.6616 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 20.5345 | PASS | 11.8821 | PASS | 11782.106 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1731 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1731 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 6.0205 | PASS | 4677% | PASS | 46671.836 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 11.0044 | PASS | 36.5458 | PASS | 36445.8185 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 11.0044 | PASS | 3655% | PASS | 36445.8185 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5551 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 15.4341 | PASS | 5.037 | PASS | 4937.0062 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6285 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6285 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 21.0739 | PASS | 2.9785 | PASS | 2878.5232 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9798 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4605 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 40.9012 | PASS | 14.72 | PASS | 14619.9506 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8309 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7538 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4427 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9357 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 12.3279 | PASS | 11.7263 | PASS | 11626.3186 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 539679 [GRTBEND6 230.00] CKT 1 | 12.3279 | PASS | 11.7263 | PASS | 11626.3186 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 139.1219 | PASS | 13.8715 | PASS | 13771.51 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8935 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 27.2805 | PASS | 11.0768 | PASS | 10976.7561 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 20.5348 | PASS | 11.8823 | PASS | 11782.3183 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2782 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2782 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46672.031 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 10.9581 | PASS | 36.5615 | PASS | 36461.5415 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 10.9581 | PASS | 36.5615 | PASS | 36461.5415 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.5443 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 15.5254 | PASS | 5.0479 | PASS | 4947.8993 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6345 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6345 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 21.1078 | PASS | 2.9893 | PASS | 2889.2813 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9821 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 40.9013 | PASS | 14.72 | PASS | 14619.9741 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 23.9769 | PASS | 5.4619 | PASS | 5361.8629 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7731 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4436 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9368 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 12.3286 | PASS | 11.7271 | PASS | 11627.1076 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531452 [MINGTER1 13.800] CKT 1 | 12.3286 | PASS | 11.7271 | PASS | 11627.1076 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 139.122 | PASS | 13.8712 | PASS | 13771.218 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8736 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7397 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2575 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2587 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2587 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46672.0013 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 10.9461 | PASS | 36.4086 | PASS | 36308.6459 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 10.9461 | PASS | 36.4086 | PASS | 36308.6459 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.5437 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 15.5249 | PASS | 5.0417 | PASS | 4941.6556 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6371 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6371 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 21.1071 | PASS | 2.9838 | PASS | 2883.83 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9782 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4605 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 40.9013 | PASS | 14.72 | PASS | 14619.9847 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 23.9769 | PASS | 5.4619 | PASS | 5361.8765 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7851 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9365 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 12.3285 | PASS | 11.7269 | PASS | 11626.9214 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531451 [MINGO 7 345.00] TO BUS 531453 [MINGTER 13.800] CKT 1 | 12.3285 | PASS | 11.7269 | PASS | 11626.9214 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 139.0468 | PASS | 13.8724 | PASS | 13772.4378 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 14.178 | PASS | 9.8592 | PASS | 9759.1545 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 27.2806 | PASS | 11.077 | PASS | 10977.0022 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 20.5338 | PASS | 11.8824 | PASS | 11782.3544 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 6.0206 | PASS | 23.2125 | PASS | 23112.5176 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 6.0206 | PASS | 23.2125 | PASS | 23112.5176 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 6.0206 | PASS | 46.7727 | PASS | 46672.71 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 7.6045 | PASS | 42.5501 | PASS | 42450.0586 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 7.6045 | PASS | 42.5501 | PASS | 42450.0586 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 13.5928 | PASS | 0.3025 | PASS | 202.5266 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 15.4218 | PASS | 5.0374 | PASS | 4937.3745 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 26.0278 | PASS | 1.6866 | PASS | 1586.5837 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 26.0278 | PASS | 1.6866 | PASS | 1586.5837 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 21.0084 | PASS | 2.9808 | PASS | 2880.8117 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9789 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4605 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 40.9006 | PASS | 14.7198 | PASS | 14619.7639 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 23.9766 | PASS | 5.4616 | PASS | 5361.5961 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 23.557 | PASS | 5.4525 | PASS | 5352.5447 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 9.4839 | PASS | 0.2604 | PASS | 160.4448 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 9.4839 | PASS | 0.2489 | PASS | 148.9383 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 12.3241 | PASS | 11.7277 | PASS | 11627.7333 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531465 [SETAB 7 345.00] CKT 1 | 12.3241 | PASS | 11.7277 | PASS | 11627.7333 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 139.1312 | PASS | 13.8719 | PASS | 13771.9477 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 14.1785 | PASS | 9.8593 | PASS | 9759.2669 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 27.2824 | PASS | 11.0773 | PASS | 10977.3133 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2504 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 6.0208 | PASS | 23.2128 | PASS | 23112.7818 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 6.0208 | PASS | 23.2128 | PASS | 23112.7818 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 6.0208 | PASS | 46.7732 | PASS | 46673.172 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 10.9968 | PASS | 37.5927 | PASS | 37492.6677 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 10.9968 | PASS | 37.5927 | PASS | 37492.6677 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 13.5946 | PASS | 0.3024 | PASS | 202.3569 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 15.5261 | PASS | 5.037 | PASS | 4937.0298 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 26.0277 | PASS | 1.6866 | PASS | 1586.5801 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 26.0277 | PASS | 1.6866 | PASS | 1586.5801 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 21.1109 | PASS | 2.981 | PASS | 2881.0072 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 24.8218 | PASS | 6.0597 | PASS | 5959.7069 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 24.8218 | PASS | 1.7195 | PASS | 1619.4787 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 40.9006 | PASS | 14.7198 | PASS | 14619.7565 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 23.9766 | PASS | 5.4616 | PASS | 5361.5931 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 23.5569 | PASS | 5.4525 | PASS | 5352.4875 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 9.4883 | PASS | 0.2604 | PASS | 160.4436 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 9.4883 | PASS | 0.2489 | PASS | 148.9368 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 12.3295 | PASS | 11.7276 | PASS | 11627.5701 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 531632 [GEN-2015-065345.00] CKT 1 | 12.3295 | PASS | 11.7276 | PASS | 11627.5701 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 139.1288 | PASS | 13.87 | PASS | 13770.0047 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 14.177 | PASS | 9.8585 | PASS | 9758.5262 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 27.2794 | PASS | 11.0764 | PASS | 10976.3928 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 20.5333 | PASS | 11.882 | PASS | 11781.9703 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 6.0204 | PASS | 23.2119 | PASS | 23111.93 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 6.0204 | PASS | 23.2119 | PASS | 23111.93 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 6.0204 | PASS | 46.7713 | PASS | 46671.3178 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 11.004 | PASS | 36.544 | PASS | 36444.0413 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 11.004 | PASS | 36.544 | PASS | 36444.0413 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 13.5931 | PASS | 0.3026 | PASS | 202.5898 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 9.0455 | PASS | 5.0991 | PASS | 4999.1028 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.5945 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.5945 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 21.1264 | PASS | 2.9762 | PASS | 2876.2001 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9724 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4611 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 40.9008 | PASS | 14.7198 | PASS | 14619.8175 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 23.9767 | PASS | 5.4617 | PASS | 5361.6575 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 23.5571 | PASS | 5.4526 | PASS | 5352.6458 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 9.4881 | PASS | 0.2604 | PASS | 160.4423 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 9.4881 | PASS | 0.2489 | PASS | 148.9351 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 12.3286 | PASS | 11.7262 | PASS | 11626.2015 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531468 [SPERTER1 13.800] TO BUS 539695 [SPEARVL6 230.00] TO BUS 531469 [SPERVIL7 345.00] CKT 1 | 12.3286 | PASS | 11.7262 | PASS | 11626.2015 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 139.0018 | PASS | 13.8709 | PASS | 13770.9447 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 14.1774 | PASS | 9.8589 | PASS | 9758.9012 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 27.2795 | PASS | 11.0768 | PASS | 10976.7547 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 20.5343 | PASS | 11.8823 | PASS | 11782.2989 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 6.0204 | PASS | 23.2123 | PASS | 23112.2753 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 6.0204 | PASS | 23.2123 | PASS | 23112.2753 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 6.0204 | PASS | 46.7727 | PASS | 46672.7371 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 10.9759 | PASS | 36.5703 | PASS | 36470.2992 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 10.9759 | PASS | 36.5703 | PASS | 36470.2992 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 13.5924 | PASS | 0.3026 | PASS | 202.5556 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 15.2894 | PASS | 5.0491 | PASS | 4949.0765 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6148 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6148 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 20.6978 | PASS | 2.9994 | PASS | 2899.4024 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9803 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.8921 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7586 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.6851 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 9.4823 | PASS | 0.2604 | PASS | 160.446 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 9.4823 | PASS | 0.2489 | PASS | 148.9398 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 12.3207 | PASS | 11.7267 | PASS | 11626.6656 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539803 [IRONWOOD7 345.00] CKT 1 | 12.3207 | PASS | 11.7267 | PASS | 11626.6656 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 139.0193 | PASS | 13.8707 | PASS | 13770.6514 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 14.1771 | PASS | 9.8587 | PASS | 9758.7272 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 27.2791 | PASS | 11.0766 | PASS | 10976.6006 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 20.5344 | PASS | 11.8822 | PASS | 11782.2122 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 6.0204 | PASS | 23.2121 | PASS | 23112.116 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 6.0204 | PASS | 23.2121 | PASS | 23112.116 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 6.0204 | PASS | 46.7726 | PASS | 46672.5994 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 10.9714 | PASS | 36.5643 | PASS | 36464.3485 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 10.9714 | PASS | 36.5643 | PASS | 36464.3485 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 13.5926 | PASS | 0.3026 | PASS | 202.5513 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 15.2654 | PASS | 5.0451 | PASS | 4945.1333 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 26.0284 | PASS | 1.6866 | PASS | 1586.6482 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 26.0284 | PASS | 1.6866 | PASS | 1586.6482 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 20.6555 | PASS | 2.9941 | PASS | 2894.0951 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9829 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 40.9015 | PASS | 14.72 | PASS | 14620.0328 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 23.977 | PASS | 5.4619 | PASS | 5361.9361 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 23.5574 | PASS | 5.4528 | PASS | 5352.8471 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 9.4829 | PASS | 0.2604 | PASS | 160.4461 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 9.4829 | PASS | 0.2489 | PASS | 148.9398 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 12.3219 | PASS | 11.7266 | PASS | 11626.6193 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 763677 [G19-030-TAP 345.00] CKT 1 | 12.3219 | PASS | 11.7266 | PASS | 11626.6193 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 139.0963 | PASS | 13.871 | PASS | 13771.0307 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8536 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 27.2801 | PASS | 11.0767 | PASS | 10976.7168 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 20.5343 | PASS | 11.8823 | PASS | 11782.2606 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2356 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2356 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 6.0205 | PASS | 46.7724 | PASS | 46672.3664 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 10.9728 | PASS | 36.5531 | PASS | 36453.0912 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 10.9728 | PASS | 36.5531 | PASS | 36453.0912 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 13.5931 | PASS | 0.3025 | PASS | 202.5487 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 15.4746 | PASS | 5.0392 | PASS | 4939.203 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6291 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6291 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 21.0271 | PASS | 2.9858 | PASS | 2885.8481 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9791 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4605 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 40.9012 | PASS | 14.72 | PASS | 14619.9521 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8345 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7535 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 9.4864 | PASS | 0.2604 | PASS | 160.444 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 9.4864 | PASS | 0.2489 | PASS | 148.9373 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 12.3269 | PASS | 11.7268 | PASS | 11626.787 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 1 | 12.3269 | PASS | 11.7268 | PASS | 11626.787 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 139.0924 | PASS | 13.871 | PASS | 13771.0376 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 14.1775 | PASS | 9.8589 | PASS | 9758.8548 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 27.2801 | PASS | 11.0767 | PASS | 10976.7179 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 20.5342 | PASS | 11.8823 | PASS | 11782.2609 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 6.0205 | PASS | 23.2122 | PASS | 23112.2365 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 6.0205 | PASS | 23.2122 | PASS | 23112.2365 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 6.0205 | PASS | 46.7724 | PASS | 46672.4261 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 10.9678 | PASS | 36.5542 | PASS | 36454.2452 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 10.9678 | PASS | 36.5542 | PASS | 36454.2452 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 13.5931 | PASS | 0.3025 | PASS | 202.5481 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 15.4665 | PASS | 5.0392 | PASS | 4939.164 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 26.0282 | PASS | 1.6866 | PASS | 1586.6297 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 26.0282 | PASS | 168.7% | PASS | 1586.6297 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 21.0138 | PASS | 2.9863 | PASS | 2886.3495 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 24.8224 | PASS | 606% | PASS | 5959.9789 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 24.8224 | PASS | 1.7195 | PASS | 1619.4605 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 40.9012 | PASS | 14.72 | PASS | 14619.9548 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 23.9769 | PASS | 5.4618 | PASS | 5361.8378 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 23.5573 | PASS | 5.4528 | PASS | 5352.7562 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 9.4861 | PASS | 0.2604 | PASS | 160.4441 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 9.4861 | PASS | 0.2489 | PASS | 148.9374 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 12.3266 | PASS | 11.7268 | PASS | 11626.7941 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 765911 [G21-068-TAP 345.00] CKT 2 | 12.3266 | PASS | 11.7268 | PASS | 11626.7941 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 139.1215 | PASS | 13.871 | PASS | 13771.0454 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.7866 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 27.2801 | PASS | 11.0766 | PASS | 10976.6464 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2656 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1726 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1726 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 6.0205 | PASS | 46.7718 | PASS | 46671.7951 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 11.0048 | PASS | 36.5423 | PASS | 36442.3225 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 11.0048 | PASS | 36.5423 | PASS | 36442.3225 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 13.5931 | PASS | 0.3026 | PASS | 202.5615 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 15.5317 | PASS | 5.0416 | PASS | 4941.5596 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6339 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6339 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 21.0805 | PASS | 2.9823 | PASS | 2882.3388 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9837 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4602 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 40.9013 | PASS | 14.72 | PASS | 14619.972 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 23.9769 | PASS | 5.4619 | PASS | 5361.8594 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7767 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 12.3286 | PASS | 11.7269 | PASS | 11626.8762 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 539759 [SPRVL 3 115.00] TO BUS 539960 [SPRVL-T 13.800] CKT 1 | 12.3286 | PASS | 11.7269 | PASS | 11626.8762 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 139.1151 | PASS | 13.871 | PASS | 13770.987 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 14.1589 | PASS | 9.857 | PASS | 9756.9548 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 27.2322 | PASS | 11.0751 | PASS | 10975.0509 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 20.5345 | PASS | 11.8822 | PASS | 11782.2136 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 6.0178 | PASS | 23.2115 | PASS | 23111.5212 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 6.0178 | PASS | 23.2115 | PASS | 23111.5212 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 6.0178 | PASS | 46.7368 | PASS | 46636.8249 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1368 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1368 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 13.5914 | PASS | 0.3026 | PASS | 202.6308 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 15.5266 | PASS | 5.0446 | PASS | 4944.584 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6206 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6206 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 21.1111 | PASS | 2.9857 | PASS | 2885.7205 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9713 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.461 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9151 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7838 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.709 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 12.3281 | PASS | 11.7268 | PASS | 11626.788 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532710 [NSES 2X1 13.200] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 533778 [NEOSHOS2 69.000] CKT 1 | 12.3281 | PASS | 11.7268 | PASS | 11626.788 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 139.119 | PASS | 13.8712 | PASS | 13771.1958 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 14.1711 | PASS | 9.8587 | PASS | 9758.7262 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 27.2655 | PASS | 11.0767 | PASS | 10976.686 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2677 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 6.0197 | PASS | 23.2122 | PASS | 23112.2305 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 6.0197 | PASS | 23.2122 | PASS | 23112.2305 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 6.0197 | PASS | 46.7619 | PASS | 46661.9334 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1551 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1551 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 13.5927 | PASS | 0.3026 | PASS | 202.5636 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6149 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6247 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6247 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7532 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9811 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9339 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8105 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7334 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.8959 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532711 [NEC U3 12.000] TO BUS 533022 [NEOSHON4 138.00] TO BUS 533768 [NEOSHON2 69.000] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.8959 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 138.1182 | PASS | 13.8727 | PASS | 13772.6624 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.7722 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 27.2802 | PASS | 11.0767 | PASS | 10976.6526 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 20.5345 | PASS | 11.8822 | PASS | 11782.1927 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.1491 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.1491 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 6.0205 | PASS | 46.7721 | PASS | 46672.0949 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1303 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1303 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 13.5933 | PASS | 0.3026 | PASS | 202.5525 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.5155 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6263 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6263 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 21.111 | PASS | 2.9857 | PASS | 2885.6882 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9816 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9408 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8195 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7418 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4432 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9363 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 12.3034 | PASS | 11.7275 | PASS | 11627.5286 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532733 [GEC U3 14.400] TO BUS 533044 [GILL E 4 138.00] TO BUS 533796 [GILL W 2 69.000] CKT 1 | 12.3034 | PASS | 11.7275 | PASS | 11627.5286 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 139.0642 | PASS | 13.8743 | PASS | 13774.3163 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 14.179 | PASS | 9.8599 | PASS | 9759.9213 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 27.2821 | PASS | 11.078 | PASS | 10977.9883 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 20.3604 | PASS | 11.8827 | PASS | 11782.6783 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.0208 | PASS | 23.2134 | PASS | 23113.4403 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.0208 | PASS | 23.2134 | PASS | 23113.4403 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.0208 | PASS | 46.7769 | PASS | 46676.8572 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 11.0065 | PASS | 36.546 | PASS | 36446.0064 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 11.0065 | PASS | 36.546 | PASS | 36446.0064 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 13.5939 | PASS | 0.3023 | PASS | 202.2565 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 15.5254 | PASS | 5.0461 | PASS | 4946.0818 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 26.026 | PASS | 1.6867 | PASS | 1586.7163 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 26.026 | PASS | 1.6867 | PASS | 1586.7163 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.1098 | PASS | 2.9873 | PASS | 2887.2594 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 24.8217 | PASS | 6.0597 | PASS | 5959.7044 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 24.8217 | PASS | 1.7195 | PASS | 1619.4788 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 40.9001 | PASS | 14.7203 | PASS | 14620.3078 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 23.976 | PASS | 5.4623 | PASS | 5362.2986 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 23.5566 | PASS | 5.453 | PASS | 5353.0178 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.4052 | PASS | 0.2605 | PASS | 160.5102 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.4052 | PASS | 0.249 | PASS | 149.0194 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.3266 | PASS | 11.729 | PASS | 11628.9527 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532740 [EMPEC121 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.3266 | PASS | 11.729 | PASS | 11628.9527 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 139.064 | PASS | 13.8743 | PASS | 13774.3169 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 14.1789 | PASS | 9.8599 | PASS | 9759.9224 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 27.2821 | PASS | 11.078 | PASS | 10977.9884 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 20.36 | PASS | 11.8827 | PASS | 11782.6778 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.0208 | PASS | 23.2134 | PASS | 23113.4403 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.0208 | PASS | 23.2134 | PASS | 23113.4403 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.0208 | PASS | 46.7769 | PASS | 46676.866 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 11.0065 | PASS | 36.546 | PASS | 36446.0065 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 11.0065 | PASS | 36.546 | PASS | 36446.0065 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 13.5939 | PASS | 0.3023 | PASS | 202.2565 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 15.5254 | PASS | 5.0461 | PASS | 4946.0829 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 26.026 | PASS | 1.6867 | PASS | 1586.7164 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 26.026 | PASS | 1.6867 | PASS | 1586.7164 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.1098 | PASS | 2.9873 | PASS | 2887.2596 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 24.8217 | PASS | 6.0597 | PASS | 5959.7043 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 24.8217 | PASS | 1.7195 | PASS | 1619.4788 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 40.9001 | PASS | 14.7203 | PASS | 14620.3083 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 23.976 | PASS | 5.4623 | PASS | 5362.2989 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 23.5566 | PASS | 5.453 | PASS | 5353.018 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.405 | PASS | 0.2605 | PASS | 160.5104 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.405 | PASS | 0.249 | PASS | 149.0196 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.3266 | PASS | 11.729 | PASS | 11628.9536 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532741 [EMPEC341 13.800] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.3266 | PASS | 11.729 | PASS | 11628.9536 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 138.9936 | PASS | 13.8779 | PASS | 13777.9295 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 14.1804 | PASS | 9.8612 | PASS | 9761.1579 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 27.284 | PASS | 11.0795 | PASS | 10979.4621 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 20.151 | PASS | 11.8831 | PASS | 11783.0619 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.021 | PASS | 23.2148 | PASS | 23114.831 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.021 | PASS | 23.2148 | PASS | 23114.831 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.021 | PASS | 46.7828 | PASS | 46682.8166 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 11.0069 | PASS | 36.547 | PASS | 36447.0271 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 11.0069 | PASS | 36.547 | PASS | 36447.0271 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 13.5945 | PASS | 0.3019 | PASS | 201.9147 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 15.524 | PASS | 5.0478 | PASS | 4947.806 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 26.0233 | PASS | 1.6868 | PASS | 1586.8167 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 26.0233 | PASS | 1.6868 | PASS | 1586.8167 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.1082 | PASS | 2.989 | PASS | 2889.0132 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 24.8207 | PASS | 6.0594 | PASS | 5959.3514 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 24.8207 | PASS | 1.7195 | PASS | 1619.5023 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 40.8987 | PASS | 14.7207 | PASS | 14620.7145 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 23.9749 | PASS | 5.4628 | PASS | 5362.8278 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 23.5557 | PASS | 5.4533 | PASS | 5353.3093 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.3057 | PASS | 0.2606 | PASS | 160.589 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.3057 | PASS | 0.2491 | PASS | 149.117 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.3242 | PASS | 11.7313 | PASS | 11631.3398 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532742 [EMPEC5 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.3242 | PASS | 11.7313 | PASS | 11631.3398 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 139.0024 | PASS | 13.8789 | PASS | 13778.8956 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 14.1811 | PASS | 9.8615 | PASS | 9761.4895 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 27.2853 | PASS | 11.0799 | PASS | 10979.8582 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 20.1499 | PASS | 11.8831 | PASS | 11783.1461 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.0212 | PASS | 23.2152 | PASS | 23115.2038 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.0212 | PASS | 23.2152 | PASS | 23115.2038 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.0212 | PASS | 46.7836 | PASS | 46683.5813 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 11.0071 | PASS | 36.5473 | PASS | 36447.2708 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 11.0071 | PASS | 36.5473 | PASS | 36447.2708 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 13.5952 | PASS | 0.3018 | PASS | 201.8222 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 15.5243 | PASS | 5.0483 | PASS | 4948.2653 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 26.0236 | PASS | 1.6868 | PASS | 1586.8432 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 26.0236 | PASS | 1.6868 | PASS | 1586.8432 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.1088 | PASS | 2.9895 | PASS | 2889.4595 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 24.8205 | PASS | 6.0592 | PASS | 5959.248 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 24.8205 | PASS | 1.7195 | PASS | 1619.5093 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 40.8991 | PASS | 14.7208 | PASS | 14620.8208 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 23.9751 | PASS | 5.463 | PASS | 5362.9686 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 23.5557 | PASS | 5.4534 | PASS | 5353.3845 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.3062 | PASS | 0.2606 | PASS | 160.5905 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.3062 | PASS | 0.2491 | PASS | 149.119 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.325 | PASS | 11.732 | PASS | 11631.9788 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532743 [EMPEC6 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.325 | PASS | 11.732 | PASS | 11631.9788 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 139.1204 | PASS | 13.8712 | PASS | 13771.2461 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8681 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7273 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2821 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2497 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2497 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46671.966 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.163 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.163 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5509 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.623 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.626 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.626 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7647 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9824 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9393 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8187 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 23.5573 | PASS | 545.3% | PASS | 5352.7402 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 9.4879 | PASS | 24.89% | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9226 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532744 [EMPEC7 1 18.000] TO BUS 532768 [EMPEC 7 345.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9226 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 138.0177 | PASS | 13.9625 | PASS | 13862.5006 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 14.1568 | PASS | 9.8949 | PASS | 9794.9091 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 27.0515 | PASS | 11.1205 | PASS | 11020.5076 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.5171 | PASS | 11.887 | PASS | 11786.9712 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 5.9746 | FAIL | 23.2608 | PASS | 23160.7521 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 5.9746 | FAIL | 23.2608 | PASS | 23160.7521 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 5.9746 | FAIL | 47.3061 | PASS | 47206.1155 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.0149 | PASS | 36.5602 | PASS | 36460.1673 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.0149 | PASS | 36.5602 | PASS | 36460.1673 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.3072 | PASS | 0.2836 | PASS | 183.6134 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 15.5285 | PASS | 5.0648 | PASS | 4964.8245 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 26.0287 | PASS | 1.6883 | PASS | 1588.2879 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 26.0287 | PASS | 1.6883 | PASS | 1588.2879 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.1349 | PASS | 3.0124 | PASS | 2912.3638 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 24.7875 | PASS | 6.0456 | PASS | 5945.5911 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 24.7875 | PASS | 1.7204 | PASS | 1620.42 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 40.9115 | PASS | 14.7269 | PASS | 14626.9221 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 23.981 | PASS | 5.4713 | PASS | 5371.2545 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 23.5579 | PASS | 5.4594 | PASS | 5359.411 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.4389 | PASS | 0.2605 | PASS | 160.4869 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.4389 | PASS | 0.249 | PASS | 148.9923 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.3081 | PASS | 11.7791 | PASS | 11679.119 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532751 [WCGS U1 25.000] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.3081 | PASS | 11.7791 | PASS | 11679.119 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 139.0926 | PASS | 13.869 | PASS | 13768.9697 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 14.1693 | PASS | 9.8585 | PASS | 9758.4685 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 27.2758 | PASS | 11.0768 | PASS | 10976.7934 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 7.3701 | PASS | 11.722 | PASS | 11621.9904 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 6.0202 | PASS | 23.2119 | PASS | 23111.8879 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 6.0202 | PASS | 23.2119 | PASS | 23111.8879 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 6.0202 | PASS | 46.7745 | PASS | 46674.5352 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1595 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1595 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 13.5928 | PASS | 0.3026 | PASS | 202.5986 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 15.526 | PASS | 5.0439 | PASS | 4943.8819 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 26.0275 | PASS | 1.6865 | PASS | 1586.5122 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 26.0275 | PASS | 1.6865 | PASS | 1586.5122 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 21.1108 | PASS | 2.9855 | PASS | 2885.5179 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9361 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4635 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 40.9 | PASS | 14.7195 | PASS | 14619.4945 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 23.9762 | PASS | 5.4612 | PASS | 5361.183 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 23.5568 | PASS | 5.4523 | PASS | 5352.2957 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 9.436 | PASS | 0.2605 | PASS | 160.5217 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 9.436 | PASS | 0.249 | PASS | 149.033 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 12.3269 | PASS | 11.7256 | PASS | 11625.553 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532769 [LANG 7 345.00] CKT 1 | 12.3269 | PASS | 11.7256 | PASS | 11625.553 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 139.005 | PASS | 13.8715 | PASS | 13771.5076 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 14.1767 | PASS | 9.8589 | PASS | 9758.9192 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 27.2774 | PASS | 11.0768 | PASS | 10976.7656 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 20.0439 | PASS | 11.8841 | PASS | 11784.1128 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 6.0201 | PASS | 23.2123 | PASS | 23112.2921 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 6.0201 | PASS | 23.2123 | PASS | 23112.2921 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 6.0201 | PASS | 46.7726 | PASS | 46672.5916 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2291 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2291 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 13.5915 | PASS | 0.3025 | PASS | 202.547 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 15.5258 | PASS | 5.0448 | PASS | 4944.7763 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6475 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6475 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 21.1084 | PASS | 2.986 | PASS | 2886.0016 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.997 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4593 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 40.9016 | PASS | 14.72 | PASS | 14620.0232 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 23.9771 | PASS | 5.4619 | PASS | 5361.9391 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 23.5574 | PASS | 5.4528 | PASS | 5352.8325 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 9.1164 | PASS | 0.2609 | PASS | 160.8639 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 9.1164 | PASS | 0.2495 | PASS | 149.4563 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 12.3222 | PASS | 11.7271 | PASS | 11627.0852 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532770 [MORRIS 7 345.00] CKT 1 | 12.3222 | PASS | 11.7271 | PASS | 11627.0852 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 138.6765 | PASS | 13.8691 | PASS | 13769.0972 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 14.1788 | PASS | 9.8594 | PASS | 9759.3529 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 27.282 | PASS | 11.0773 | PASS | 10977.3059 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 19.4734 | PASS | 11.8819 | PASS | 11781.9293 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 6.0208 | PASS | 23.2129 | PASS | 23112.8998 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 6.0208 | PASS | 23.2129 | PASS | 23112.8998 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 6.0208 | PASS | 46.7748 | PASS | 46674.7959 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 11.005 | PASS | 36.5445 | PASS | 36444.479 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 11.005 | PASS | 36.5445 | PASS | 36444.479 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 13.5937 | PASS | 0.3025 | PASS | 202.497 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 15.518 | PASS | 5.0434 | PASS | 4943.3697 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 25.9894 | PASS | 1.6863 | PASS | 1586.3298 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 25.9894 | PASS | 1.6863 | PASS | 1586.3298 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 21.0965 | PASS | 2.9838 | PASS | 2883.8298 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 24.82 | PASS | 6.0596 | PASS | 5959.6259 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 24.82 | PASS | 1.7195 | PASS | 1619.484 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 40.8676 | PASS | 14.7188 | PASS | 14618.7593 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 23.9543 | PASS | 5.4599 | PASS | 5359.8896 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 23.5384 | PASS | 5.4513 | PASS | 5351.3133 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 8.8929 | PASS | 0.261 | PASS | 161.0356 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 8.8929 | PASS | 0.2497 | PASS | 149.6683 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 12.3033 | PASS | 11.7254 | PASS | 11625.393 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532774 [SWISVAL7 345.00] CKT 1 | 12.3033 | PASS | 11.7254 | PASS | 11625.393 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 139.1529 | PASS | 13.8744 | PASS | 13774.3797 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 14.18 | PASS | 9.8599 | PASS | 9759.9435 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 27.2849 | PASS | 11.078 | PASS | 10978.0134 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 20.5373 | PASS | 11.8826 | PASS | 11782.6462 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 6.0212 | PASS | 23.2135 | PASS | 23113.4644 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 6.0212 | PASS | 23.2135 | PASS | 23113.4644 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 6.0212 | PASS | 46.7756 | PASS | 46675.5661 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 11.0067 | PASS | 36.546 | PASS | 36445.9751 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 11.0067 | PASS | 36.546 | PASS | 36445.9751 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 13.5954 | PASS | 0.3023 | PASS | 202.2502 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 15.5276 | PASS | 5.0461 | PASS | 4946.1109 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 26.029 | PASS | 1.6867 | PASS | 1586.7182 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 26.029 | PASS | 1.6867 | PASS | 1586.7182 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 21.1133 | PASS | 2.9872 | PASS | 2887.2455 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 24.8218 | PASS | 6.0597 | PASS | 5959.6986 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 24.8218 | PASS | 1.7195 | PASS | 1619.4793 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 40.9024 | PASS | 14.7203 | PASS | 14620.3154 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 23.9775 | PASS | 5.4623 | PASS | 5362.3113 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 23.5577 | PASS | 5.453 | PASS | 5353.0256 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 9.4925 | PASS | 0.2605 | PASS | 160.4764 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 9.4925 | PASS | 0.249 | PASS | 148.9775 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 12.3312 | PASS | 11.729 | PASS | 11628.995 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532776 [READWF 7 345.00] CKT 1 | 12.3312 | PASS | 11.729 | PASS | 11628.995 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 139.0925 | PASS | 13.869 | PASS | 13768.9694 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 14.1693 | PASS | 9.8585 | PASS | 9758.4703 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 27.2758 | PASS | 11.0768 | PASS | 10976.7913 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 7.3698 | PASS | 11.7224 | PASS | 11622.4479 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 6.0202 | PASS | 23.2119 | PASS | 23111.8866 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 6.0202 | PASS | 23.2119 | PASS | 23111.8866 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 6.0202 | PASS | 46.7745 | PASS | 46674.5315 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1575 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1575 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 13.5928 | PASS | 0.3026 | PASS | 202.5991 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 15.526 | PASS | 5.0439 | PASS | 4943.8811 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 26.0275 | PASS | 1.6865 | PASS | 1586.5123 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 26.0275 | PASS | 1.6865 | PASS | 1586.5123 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 21.1108 | PASS | 2.9855 | PASS | 2885.5159 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9367 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4634 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 40.9 | PASS | 14.7195 | PASS | 14619.4948 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 23.9762 | PASS | 5.4612 | PASS | 5361.1833 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 23.5567 | PASS | 5.4523 | PASS | 5352.2965 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 9.4359 | PASS | 0.2605 | PASS | 160.5218 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 9.4359 | PASS | 0.249 | PASS | 149.033 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 12.3269 | PASS | 11.7256 | PASS | 11625.5513 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532769 [LANG 7 345.00] TO BUS 533304 [LANG 3 115.00] TO BUS 532808 [LANG 1 14.400] CKT 1 | 12.3269 | PASS | 11.7256 | PASS | 11625.5513 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 135.9093 | PASS | 13.8539 | PASS | 13753.8865 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 14.161 | PASS | 9.8549 | PASS | 9754.8766 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 27.2402 | PASS | 11.0729 | PASS | 10972.887 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 20.5243 | PASS | 11.8804 | PASS | 11780.4045 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.0135 | PASS | 23.2081 | PASS | 23108.1018 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.0135 | PASS | 23.2081 | PASS | 23108.1018 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.0135 | PASS | 46.787 | PASS | 46686.9657 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 11.0033 | PASS | 36.5439 | PASS | 36443.8691 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 11.0033 | PASS | 36.5439 | PASS | 36443.8691 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 13.5697 | PASS | 0.3027 | PASS | 202.6593 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 15.4604 | PASS | 5.0466 | PASS | 4946.5748 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 26.0263 | PASS | 1.6865 | PASS | 1586.53 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 26.0263 | PASS | 1.6865 | PASS | 1586.53 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 21.0419 | PASS | 2.9861 | PASS | 2886.0786 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 24.8228 | PASS | 6.0601 | PASS | 5960.1266 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 24.8228 | PASS | 1.7195 | PASS | 1619.4507 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 40.8997 | PASS | 14.7197 | PASS | 14619.6523 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 23.976 | PASS | 5.4614 | PASS | 5361.3927 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 23.5576 | PASS | 5.453 | PASS | 5353.0039 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.3065 | PASS | 0.2606 | PASS | 160.5758 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.3065 | PASS | 0.2491 | PASS | 149.0985 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.1398 | PASS | 11.7183 | PASS | 11618.276 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.1398 | PASS | 11.7183 | PASS | 11618.276 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 136.2584 | PASS | 13.8845 | PASS | 13784.5208 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 13.7836 | PASS | 9.8371 | PASS | 9737.1101 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 25.4751 | PASS | 11.057 | PASS | 10957.0309 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 20.5213 | PASS | 11.8803 | PASS | 11780.339 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 5.6391 | FAIL | 23.1984 | PASS | 23098.3863 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 5.6391 | FAIL | 23.1984 | PASS | 23098.3863 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 5.6391 | FAIL | 48.9491 | PASS | 48849.112 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 11.0072 | PASS | 36.5487 | PASS | 36448.741 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 11.0072 | PASS | 36.5487 | PASS | 36448.741 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 13.5135 | PASS | 0.3034 | PASS | 203.3826 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 15.515 | PASS | 5.0461 | PASS | 4946.0508 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 26.0268 | PASS | 1.6866 | PASS | 1586.5595 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 26.0268 | PASS | 1.6866 | PASS | 1586.5595 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 21.1031 | PASS | 2.992 | PASS | 2892.0003 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 24.8211 | PASS | 6.0596 | PASS | 5959.5911 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 24.8211 | PASS | 1.7195 | PASS | 1619.4863 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 40.8991 | PASS | 14.7195 | PASS | 14619.5467 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 23.9758 | PASS | 5.4614 | PASS | 5361.371 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 23.5551 | PASS | 5.4517 | PASS | 5351.7428 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 9.4178 | PASS | 0.2605 | PASS | 160.4535 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 9.4178 | PASS | 0.2489 | PASS | 148.9488 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.2108 | PASS | 11.7345 | PASS | 11634.4614 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532793 [NEOSHO 7 345.00] CKT 1 | 12.2108 | PASS | 11.7345 | PASS | 11634.4614 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 138.8637 | PASS | 13.8736 | PASS | 13773.5836 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 14.1769 | PASS | 9.859 | PASS | 9759.0049 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 27.2777 | PASS | 11.0769 | PASS | 10976.8631 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 20.5309 | PASS | 11.8824 | PASS | 11782.4113 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.0201 | PASS | 23.2124 | PASS | 23112.4292 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.0201 | PASS | 23.2124 | PASS | 23112.4292 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 6.0201 | PASS | 46.7812 | PASS | 46681.2374 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 11.0036 | PASS | 36.5458 | PASS | 36445.8393 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 11.0036 | PASS | 36.5458 | PASS | 36445.8393 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 13.5907 | PASS | 0.3025 | PASS | 202.5447 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 15.5108 | PASS | 5.0459 | PASS | 4945.8809 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6256 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6256 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 21.0845 | PASS | 2.9866 | PASS | 2886.5912 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9839 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4602 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.937 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.8162 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7362 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.4647 | PASS | 0.2605 | PASS | 160.4766 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.4647 | PASS | 0.249 | PASS | 148.9776 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.3183 | PASS | 11.7284 | PASS | 11628.373 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.3183 | PASS | 11.7284 | PASS | 11628.373 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 138.8637 | PASS | 13.8736 | PASS | 13773.5836 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 14.1769 | PASS | 985.9% | PASS | 9759.0049 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 27.2777 | PASS | 11.0769 | PASS | 10976.8631 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 20.5309 | PASS | 1188% | PASS | 11782.4113 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 6.0201 | PASS | 23.2124 | PASS | 23112.4292 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 6.0201 | PASS | 23.2124 | PASS | 23112.4292 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 6.0201 | PASS | 46.7812 | PASS | 46681.2374 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 11.0036 | PASS | 36.5458 | PASS | 36445.8393 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 11.0036 | PASS | 36.5458 | PASS | 36445.8393 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 13.5907 | PASS | 0.3025 | PASS | 202.5447 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 15.5108 | PASS | 5.0459 | PASS | 4945.8809 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 26.028 | PASS | 1.6866 | PASS | 1586.6256 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 26.028 | PASS | 1.6866 | PASS | 1586.6256 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 21.0845 | PASS | 2.9866 | PASS | 2886.5912 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 24.8224 | PASS | 6.06 | PASS | 5959.9839 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 24.8224 | PASS | 1.7195 | PASS | 1619.4602 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 40.9011 | PASS | 14.7199 | PASS | 14619.937 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 23.9768 | PASS | 5.4618 | PASS | 5361.8162 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 23.5572 | PASS | 5.4527 | PASS | 5352.7362 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 9.4647 | PASS | 0.2605 | PASS | 160.4766 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 9.4647 | PASS | 0.249 | PASS | 148.9776 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 12.3183 | PASS | 11.7284 | PASS | 11628.373 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 2 | 12.3183 | PASS | 11.7284 | PASS | 11628.373 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 138.8783 | PASS | 13.8639 | PASS | 13763.9327 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 14.1522 | PASS | 9.8596 | PASS | 9759.5599 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 27.1367 | PASS | 11.0771 | PASS | 10977.0742 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 20.5083 | PASS | 11.8819 | PASS | 11781.8564 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 5.9903 | FAIL | 23.2131 | PASS | 23113.1109 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 5.9903 | FAIL | 23.2131 | PASS | 23113.1109 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 5.9903 | FAIL | 46.8725 | PASS | 46772.5343 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 11.0021 | PASS | 36.5446 | PASS | 36444.6172 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 11.0021 | PASS | 36.5446 | PASS | 36444.6172 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 13.5731 | PASS | 0.3027 | PASS | 202.6555 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 15.4936 | PASS | 5.0418 | PASS | 4941.819 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6181 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6181 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 21.0618 | PASS | 2.9834 | PASS | 2883.4185 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 24.8225 | PASS | 6.06 | PASS | 5960.0285 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 24.8225 | PASS | 1.7195 | PASS | 1619.4572 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9369 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.796 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 23.5575 | PASS | 5.4529 | PASS | 5352.8966 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 9.3137 | PASS | 0.2606 | PASS | 160.5562 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 9.3137 | PASS | 0.2491 | PASS | 149.0755 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 12.2916 | PASS | 11.7207 | PASS | 11620.6737 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532794 [ROSEHIL7 345.00] CKT 1 | 12.2916 | PASS | 11.7207 | PASS | 11620.6737 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 138.9776 | PASS | 13.8554 | PASS | 13755.4458 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 14.1272 | PASS | 9.8569 | PASS | 9756.9378 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 27.1035 | PASS | 11.0748 | PASS | 10974.8201 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 20.4837 | PASS | 11.8812 | PASS | 11781.2037 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 5.9872 | FAIL | 23.2098 | PASS | 23109.8357 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 5.9872 | FAIL | 23.2098 | PASS | 23109.8357 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 5.9872 | FAIL | 46.988 | PASS | 46887.9753 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 10.9961 | PASS | 36.5459 | PASS | 36445.8919 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 10.9961 | PASS | 36.5459 | PASS | 36445.8919 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 13.4283 | PASS | 0.3027 | PASS | 202.6666 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 15.4358 | PASS | 5.0447 | PASS | 4944.7282 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6441 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6441 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 20.9778 | PASS | 2.9855 | PASS | 2885.5237 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5960.0101 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4584 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 40.9015 | PASS | 14.72 | PASS | 14620.043 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 23.977 | PASS | 5.4619 | PASS | 5361.9408 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 23.5576 | PASS | 5.453 | PASS | 5352.9822 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.0353 | PASS | 0.2608 | PASS | 160.826 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 9.0353 | PASS | 0.2494 | PASS | 149.4099 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.2758 | PASS | 11.7203 | PASS | 11620.3244 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532796 [WICHITA7 345.00] CKT 1 | 12.2758 | PASS | 11.7203 | PASS | 11620.3244 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 136.158 | PASS | 13.8239 | PASS | 13723.8955 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 14.1318 | PASS | 9.838 | PASS | 9737.9537 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 27.1949 | PASS | 11.0525 | PASS | 10952.4716 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 20.5075 | PASS | 11.8766 | PASS | 11776.5556 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 6.0037 | PASS | 23.1805 | PASS | 23080.4594 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 6.0037 | PASS | 23.1805 | PASS | 23080.4594 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 6.0037 | PASS | 46.6951 | PASS | 46595.1196 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 11.0077 | PASS | 36.5506 | PASS | 36450.5812 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 11.0077 | PASS | 36.5506 | PASS | 36450.5812 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 13.2686 | PASS | 0.3147 | PASS | 214.7071 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 15.5064 | PASS | 5.0389 | PASS | 4938.9364 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 26.0228 | PASS | 1.686 | PASS | 1586.0228 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 26.0228 | PASS | 1.686 | PASS | 1586.0228 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 21.1002 | PASS | 2.9933 | PASS | 2893.3215 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 24.8201 | PASS | 6.0589 | PASS | 5958.9044 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 24.8201 | PASS | 1.7195 | PASS | 1619.5323 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 40.8915 | PASS | 14.717 | PASS | 14617.0497 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 23.9719 | PASS | 5.458 | PASS | 5357.9787 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 23.5508 | PASS | 5.4482 | PASS | 5348.1691 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 9.3671 | PASS | 0.2605 | PASS | 160.4539 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 9.3671 | PASS | 0.2489 | PASS | 148.9476 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 12.1879 | PASS | 11.7069 | PASS | 11606.9387 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 12.1879 | PASS | 11.7069 | PASS | 11606.9387 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 138.8279 | PASS | 13.8626 | PASS | 13762.632 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.5526 | PASS | 9.8702 | PASS | 9770.2161 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 24.418 | PASS | 11.0814 | PASS | 10981.4038 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 20.5338 | PASS | 11.8817 | PASS | 11781.693 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 5.4175 | FAIL | 23.2239 | PASS | 23123.8559 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 5.4175 | FAIL | 23.2239 | PASS | 23123.8559 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 5.4175 | FAIL | 50.1782 | PASS | 50078.1876 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.006 | PASS | 36.5452 | PASS | 36445.164 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 11.006 | PASS | 36.5452 | PASS | 36445.164 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 13.3489 | PASS | 0.3054 | PASS | 205.4207 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 15.5233 | PASS | 5.0405 | PASS | 4940.4591 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 26.0042 | PASS | 1.6857 | PASS | 1585.7284 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 26.0042 | PASS | 1.6857 | PASS | 1585.7284 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 21.113 | PASS | 2.9869 | PASS | 2886.8958 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 24.8211 | PASS | 6.0593 | PASS | 5959.3344 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 24.8211 | PASS | 1.7195 | PASS | 1619.5036 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 40.8737 | PASS | 14.7158 | PASS | 14615.8064 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 23.9606 | PASS | 5.4562 | PASS | 5356.1966 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 23.5415 | PASS | 5.4473 | PASS | 5347.3302 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 9.4759 | PASS | 0.2604 | PASS | 160.4324 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 9.4759 | PASS | 0.2489 | PASS | 148.9221 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.3121 | PASS | 11.7211 | PASS | 11621.1431 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 542981 [LACYGNE7 345.00] CKT 1 | 12.3121 | PASS | 11.7211 | PASS | 11621.1431 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 139.1762 | PASS | 13.8765 | PASS | 13776.5134 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 14.1958 | PASS | 9.8638 | PASS | 9763.7777 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 27.3259 | PASS | 11.0798 | PASS | 10979.7949 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 20.536 | PASS | 11.8828 | PASS | 11782.8459 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 6.0284 | PASS | 23.2132 | PASS | 23113.2269 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 6.0284 | PASS | 23.2132 | PASS | 23113.2269 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 6.0284 | PASS | 46.7243 | PASS | 46624.2628 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 11.0069 | PASS | 36.5463 | PASS | 36446.3048 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 11.0069 | PASS | 36.5463 | PASS | 36446.3048 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 13.602 | PASS | 0.302 | PASS | 201.9629 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 15.5276 | PASS | 5.0461 | PASS | 4946.0849 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 26.0297 | PASS | 1.6868 | PASS | 1586.7975 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 26.0297 | PASS | 1.6868 | PASS | 1586.7975 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 21.1145 | PASS | 2.9878 | PASS | 2887.841 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 24.8208 | PASS | 6.0593 | PASS | 5959.2788 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 24.8208 | PASS | 1.7195 | PASS | 1619.5072 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 40.9037 | PASS | 14.7207 | PASS | 14620.7057 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 23.9781 | PASS | 5.4628 | PASS | 5362.7931 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 23.5585 | PASS | 5.4536 | PASS | 5353.621 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 9.4894 | PASS | 0.2604 | PASS | 160.4451 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 9.4894 | PASS | 0.2489 | PASS | 148.9387 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 12.3325 | PASS | 11.73 | PASS | 11629.9964 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 762680 [GEN-2018-032345.00] CKT 1 | 12.3325 | PASS | 11.73 | PASS | 11629.9964 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 139.2463 | PASS | 13.8844 | PASS | 13784.3877 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 14.2093 | PASS | 9.8736 | PASS | 9773.6029 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 27.3217 | PASS | 11.0887 | PASS | 10988.7133 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 20.5378 | PASS | 11.8837 | PASS | 11783.6898 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 6.0258 | PASS | 23.2221 | PASS | 23122.142 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 6.0258 | PASS | 23.2221 | PASS | 23122.142 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 6.0258 | PASS | 46.7899 | PASS | 46689.8897 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 11.008 | PASS | 36.5479 | PASS | 36447.9167 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 11.008 | PASS | 36.5479 | PASS | 36447.9167 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 13.6054 | PASS | 0.3008 | PASS | 200.8418 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 15.529 | PASS | 5.0482 | PASS | 4948.1641 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 26.0317 | PASS | 1.687 | PASS | 1587.0328 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 26.0317 | PASS | 1.687 | PASS | 1587.0328 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 21.119 | PASS | 2.9908 | PASS | 2890.7911 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 24.8179 | PASS | 6.0581 | PASS | 5958.0712 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 24.8179 | PASS | 1.7196 | PASS | 1619.5876 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 40.9071 | PASS | 14.7217 | PASS | 14621.7464 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 23.9798 | PASS | 5.4641 | PASS | 5364.1293 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 23.56 | PASS | 5.4548 | PASS | 5354.794 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 9.4911 | PASS | 0.2604 | PASS | 160.4475 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 9.4911 | PASS | 0.2489 | PASS | 148.9419 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 12.3381 | PASS | 11.7345 | PASS | 11634.5291 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 765350 [GEN-2021-006345.00] CKT 1 | 12.3381 | PASS | 11.7345 | PASS | 11634.5291 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 139.0727 | PASS | 13.8688 | PASS | 13768.8369 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 12.8361 | PASS | 9.8732 | PASS | 9773.2434 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 24.9882 | PASS | 11.0785 | PASS | 10978.4753 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 20.5365 | PASS | 11.883 | PASS | 11783.0111 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 5.9339 | FAIL | 23.2084 | PASS | 23108.3735 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 5.9339 | FAIL | 23.2084 | PASS | 23108.3735 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 5.9339 | FAIL | 46.5407 | PASS | 46440.7386 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.9075 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.9075 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 13.5432 | PASS | 0.3033 | PASS | 203.3306 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 15.5262 | PASS | 5.044 | PASS | 4944.0426 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 26.0274 | PASS | 1.6866 | PASS | 1586.5717 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 26.0274 | PASS | 1.6866 | PASS | 1586.5717 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 21.1106 | PASS | 2.9855 | PASS | 2885.4538 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 24.8222 | PASS | 6.0599 | PASS | 5959.8967 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 24.8222 | PASS | 1.7195 | PASS | 1619.4661 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 40.9 | PASS | 14.7197 | PASS | 14619.6895 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 23.9762 | PASS | 5.4615 | PASS | 5361.4784 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 23.5566 | PASS | 5.4524 | PASS | 5352.3991 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 9.4864 | PASS | 0.2604 | PASS | 160.4428 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 9.4864 | PASS | 0.2489 | PASS | 148.9358 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 12.3254 | PASS | 11.7255 | PASS | 11625.4966 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 533021 [NEOSHO 4 138.00] TO BUS 532824 [N345 1 1 13.800] CKT 1 | 12.3254 | PASS | 11.7255 | PASS | 11625.4966 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 136.3574 | PASS | 13.8186 | PASS | 13718.6175 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 14.1292 | PASS | 9.8375 | PASS | 9737.5341 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 27.1884 | PASS | 11.0507 | PASS | 10950.6861 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 20.5152 | PASS | 11.8764 | PASS | 11776.4219 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 6.0023 | PASS | 23.1778 | PASS | 23077.7568 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 6.0023 | PASS | 23.1778 | PASS | 23077.7568 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 6.0023 | PASS | 46.7031 | PASS | 46603.0769 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.0069 | PASS | 36.5477 | PASS | 36447.7194 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 11.0069 | PASS | 36.5477 | PASS | 36447.7194 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 13.2952 | PASS | 0.3154 | PASS | 215.3726 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 15.5134 | PASS | 5.0357 | PASS | 4935.7012 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 26.0226 | PASS | 1.686 | PASS | 1586.0119 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 26.0226 | PASS | 1.686 | PASS | 1586.0119 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 21.1078 | PASS | 2.9894 | PASS | 2889.3681 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 24.8202 | PASS | 6.0589 | PASS | 5958.9362 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 24.8202 | PASS | 1.7195 | PASS | 1619.5302 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 40.8914 | PASS | 14.717 | PASS | 14617.0298 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 23.9718 | PASS | 5.4579 | PASS | 5357.9332 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 23.551 | PASS | 5.4483 | PASS | 5348.3071 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.4157 | PASS | 0.2604 | PASS | 160.4249 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 9.4157 | PASS | 0.2489 | PASS | 148.9117 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.2032 | PASS | 11.7014 | PASS | 11601.4129 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532797 [WOLFCRK7 345.00] CKT 1 | 12.2032 | PASS | 11.7014 | PASS | 11601.4129 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 136.9066 | PASS | 13.8479 | PASS | 13747.859 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 14.1563 | PASS | 9.8497 | PASS | 9749.7362 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 27.2418 | PASS | 11.0676 | PASS | 10967.593 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 20.4974 | PASS | 11.8796 | PASS | 11779.5768 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.0146 | PASS | 23.2036 | PASS | 23103.5891 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.0146 | PASS | 23.2036 | PASS | 23103.5891 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 6.0146 | PASS | 46.7613 | PASS | 46661.3383 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 11.0017 | PASS | 3654% | PASS | 36441.2445 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 11.0017 | PASS | 36.5412 | PASS | 36441.2445 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 13.5739 | PASS | 30.43% | PASS | 204.3326 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 15.5009 | PASS | 5.0352 | PASS | 4935.1945 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 26.0254 | PASS | 1.6864 | PASS | 1586.4433 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 26.0254 | PASS | 1.6864 | PASS | 1586.4433 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 21.0728 | PASS | 2.9795 | PASS | 2879.4582 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 24.8225 | PASS | 6.06 | PASS | 5959.9981 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 24.8225 | PASS | 1.7195 | PASS | 1619.4592 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 40.8979 | PASS | 14.7192 | PASS | 14619.1973 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 23.975 | PASS | 5.4608 | PASS | 5360.8154 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 23.5561 | PASS | 5.4522 | PASS | 5352.1683 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.2812 | PASS | 0.2606 | PASS | 160.6335 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 9.2812 | PASS | 0.2492 | PASS | 149.1704 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 11.5558 | PASS | 11.7457 | PASS | 11645.7451 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532798 [VIOLA 7 345.00] CKT 1 | 11.5558 | PASS | 11.7457 | PASS | 11645.7451 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 135.6229 | PASS | 13.8598 | PASS | 13759.8067 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 14.1763 | PASS | 9.8583 | PASS | 9758.2656 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 27.2796 | PASS | 11.0763 | PASS | 10976.3102 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 20.533 | PASS | 11.8815 | PASS | 11781.538 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 6.0204 | PASS | 23.2117 | PASS | 23111.68 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 6.0204 | PASS | 23.2117 | PASS | 23111.68 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 6.0204 | PASS | 46.7737 | PASS | 46673.7274 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 11.0056 | PASS | 36.5448 | PASS | 36444.8031 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 11.0056 | PASS | 36.5448 | PASS | 36444.8031 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 13.5939 | PASS | 0.3026 | PASS | 202.5579 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 15.5242 | PASS | 5.0442 | PASS | 4944.169 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6264 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6264 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 21.1069 | PASS | 2.9852 | PASS | 2885.2445 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9861 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4601 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9465 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8235 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7704 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 9.4713 | PASS | 0.2605 | PASS | 160.488 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 9.4713 | PASS | 0.249 | PASS | 148.9919 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 12.2679 | PASS | 11.7221 | PASS | 11622.1343 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532829 [WICH11 1 13.800] CKT 1 | 12.2679 | PASS | 11.7221 | PASS | 11622.1343 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 134.8405 | PASS | 13.8569 | PASS | 13756.9187 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 14.176 | PASS | 9.8581 | PASS | 9758.1239 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 27.2794 | PASS | 11.0762 | PASS | 10976.215 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 20.5326 | PASS | 11.8814 | PASS | 11781.3533 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 6.0204 | PASS | 23.2115 | PASS | 23111.5491 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 6.0204 | PASS | 23.2115 | PASS | 23111.5491 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 6.0204 | PASS | 46.7741 | PASS | 46674.1399 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 11.0055 | PASS | 36.5447 | PASS | 36444.7321 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 11.0055 | PASS | 36.5447 | PASS | 36444.7321 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 13.5941 | PASS | 0.3026 | PASS | 202.5581 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 15.5236 | PASS | 5.0441 | PASS | 4944.0894 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6269 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6269 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 21.1059 | PASS | 2.9851 | PASS | 2885.1497 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9855 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4601 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9485 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.8264 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.779 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 9.4672 | PASS | 0.2605 | PASS | 160.4979 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 9.4672 | PASS | 0.249 | PASS | 149.0042 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 12.2543 | PASS | 11.7209 | PASS | 11620.9402 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 533040 [EVANS N4 138.00] TO BUS 532830 [WICH12 1 13.800] CKT 1 | 12.2543 | PASS | 11.7209 | PASS | 11620.9402 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 138.4422 | PASS | 13.8786 | PASS | 13778.6275 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 14.1696 | PASS | 9.8558 | PASS | 9755.8327 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 27.2685 | PASS | 11.0739 | PASS | 10973.9215 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 20.5334 | PASS | 11.8818 | PASS | 11781.7894 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 6.0189 | PASS | 23.2096 | PASS | 23109.6119 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 6.0189 | PASS | 23.2096 | PASS | 23109.6119 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 6.0189 | PASS | 46.7648 | PASS | 46664.8386 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 11.0066 | PASS | 36.5463 | PASS | 36446.3215 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 11.0066 | PASS | 36.5463 | PASS | 36446.3215 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 12.9781 | PASS | 0.301 | PASS | 200.9794 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 15.523 | PASS | 5.0439 | PASS | 4943.887 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 25.9954 | PASS | 1.6865 | PASS | 1586.4741 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 25.9954 | PASS | 1.6865 | PASS | 1586.4741 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 21.1121 | PASS | 2.9888 | PASS | 2888.7726 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 24.8214 | PASS | 6.0602 | PASS | 5960.2027 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 24.8214 | PASS | 1.7194 | PASS | 1619.4456 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 40.8709 | PASS | 14.7192 | PASS | 14619.2134 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 23.9578 | PASS | 5.4609 | PASS | 5360.9256 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 23.5379 | PASS | 5.4518 | PASS | 5351.795 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 9.4732 | PASS | 0.2604 | PASS | 160.4441 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 9.4732 | PASS | 0.2489 | PASS | 148.9371 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 12.2998 | PASS | 11.7304 | PASS | 11630.3633 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 532799 [WAVERLY7 345.00] CKT 1 | 12.2998 | PASS | 11.7304 | PASS | 11630.3633 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 136.4152 | PASS | 13.8756 | PASS | 13775.6357 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 14.1525 | PASS | 9.847 | PASS | 9747.047 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 27.2343 | PASS | 11.0633 | PASS | 10963.3422 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 20.5139 | PASS | 11.8805 | PASS | 11780.5423 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 6.0117 | PASS | 23.1957 | PASS | 23095.6544 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 6.0117 | PASS | 23.1957 | PASS | 23095.6544 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 6.0117 | PASS | 46.7324 | PASS | 46632.4305 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 11.007 | PASS | 36.5496 | PASS | 36449.5738 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 11.007 | PASS | 36.5496 | PASS | 36449.5738 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 13.3027 | PASS | 0.3104 | PASS | 210.4261 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 15.5087 | PASS | 5.046 | PASS | 4945.9974 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 26.0247 | PASS | 1.6863 | PASS | 1586.2595 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 26.0247 | PASS | 1.6863 | PASS | 1586.2595 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 21.0965 | PASS | 2.9935 | PASS | 2893.4774 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 24.8211 | PASS | 6.0594 | PASS | 5959.3752 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 24.8211 | PASS | 1.7195 | PASS | 1619.5008 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 40.895 | PASS | 14.7182 | PASS | 14618.1654 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 23.9737 | PASS | 5.4595 | PASS | 5359.4744 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 23.553 | PASS | 5.4499 | PASS | 5349.8851 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 9.38 | PASS | 0.2605 | PASS | 160.4667 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 9.38 | PASS | 0.249 | PASS | 148.9649 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 12.2071 | PASS | 11.7316 | PASS | 11631.616 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 766141 [G21-096-TAP 345.00] CKT 1 | 12.2071 | PASS | 11.7316 | PASS | 11631.616 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 139.0635 | PASS | 13.8673 | PASS | 13767.287 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 14.1293 | PASS | 9.8487 | PASS | 9748.6943 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 27.2526 | PASS | 11.0754 | PASS | 10975.4124 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 20.5343 | PASS | 11.8821 | PASS | 11782.0736 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 6.0192 | PASS | 23.2096 | PASS | 23109.555 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 6.0192 | PASS | 23.2096 | PASS | 23109.555 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 6.0192 | PASS | 46.7758 | PASS | 46675.8139 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.8857 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.8857 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 13.5669 | PASS | 0.3037 | PASS | 203.6653 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 15.5261 | PASS | 5.044 | PASS | 4943.9726 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 26.0277 | PASS | 1.6866 | PASS | 1586.5738 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 26.0277 | PASS | 1.6866 | PASS | 1586.5738 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 21.1104 | PASS | 2.9853 | PASS | 2885.3153 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 24.8222 | PASS | 6.0599 | PASS | 5959.8603 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 24.8222 | PASS | 1.7195 | PASS | 1619.4685 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 40.9004 | PASS | 14.7197 | PASS | 14619.7029 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 23.9764 | PASS | 5.4615 | PASS | 5361.4804 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 23.5568 | PASS | 5.4524 | PASS | 5352.426 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 9.4864 | PASS | 0.2604 | PASS | 160.4427 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 9.4864 | PASS | 0.2489 | PASS | 148.9356 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 12.3248 | PASS | 11.7248 | PASS | 11624.7823 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 533653 [WOLFCRK2 69.000] TO BUS 532962 [WOLFCRK1 17.000] CKT 1 | 12.3248 | PASS | 11.7248 | PASS | 11624.7823 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 136.3162 | PASS | 13.7882 | PASS | 13688.2217 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 14.1764 | PASS | 9.8581 | PASS | 9758.1426 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 27.2796 | PASS | 11.0762 | PASS | 10976.2189 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 20.5327 | PASS | 11.8816 | PASS | 11781.6167 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 6.0203 | PASS | 23.2115 | PASS | 23111.5201 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 6.0203 | PASS | 23.2115 | PASS | 23111.5201 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 6.0203 | PASS | 46.7722 | PASS | 46672.2331 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 11.0064 | PASS | 36.5455 | PASS | 36445.4842 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 11.0064 | PASS | 36.5455 | PASS | 36445.4842 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 13.5939 | PASS | 0.3025 | PASS | 202.5367 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 15.5265 | PASS | 5.0442 | PASS | 4944.2234 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6321 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6321 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 21.1114 | PASS | 2.9859 | PASS | 2885.8944 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.978 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4606 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 40.9012 | PASS | 14.72 | PASS | 14619.9623 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8496 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7508 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 9.4888 | PASS | 0.2605 | PASS | 160.4528 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 9.4888 | PASS | 0.2489 | PASS | 148.9487 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 11.7714 | PASS | 11.5745 | PASS | 11474.5057 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532832 [VIOLA1X1 13.800] CKT 1 | 11.7714 | PASS | 11.5745 | PASS | 11474.5057 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 134.529 | PASS | 14.0945 | PASS | 13994.4567 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 14.1822 | PASS | 9.8621 | PASS | 9762.069 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 27.2841 | PASS | 11.0796 | PASS | 10979.5933 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 20.5375 | PASS | 11.8847 | PASS | 11784.7119 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 6.0214 | PASS | 23.2157 | PASS | 23115.7487 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 6.0214 | PASS | 23.2157 | PASS | 23115.7487 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 6.0214 | PASS | 46.7901 | PASS | 46690.101 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 11.0065 | PASS | 36.5465 | PASS | 36446.4729 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 11.0065 | PASS | 36.5465 | PASS | 36446.4729 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 13.5908 | PASS | 0.3023 | PASS | 202.3117 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 15.5275 | PASS | 5.0521 | PASS | 4952.1158 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 26.0282 | PASS | 1.6866 | PASS | 1586.6407 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 26.0282 | PASS | 1.6866 | PASS | 1586.6407 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 21.1106 | PASS | 2.9896 | PASS | 2889.6431 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 24.8225 | PASS | 6.06 | PASS | 5960.018 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 24.8225 | PASS | 1.7195 | PASS | 1619.4579 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 40.9013 | PASS | 14.72 | PASS | 14620.0026 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 23.9769 | PASS | 5.4619 | PASS | 5361.9061 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 23.5573 | PASS | 5.4528 | PASS | 5352.8205 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 9.485 | PASS | 0.2605 | PASS | 160.4515 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 9.485 | PASS | 0.2489 | PASS | 148.9471 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 11.5664 | PASS | 12.0051 | PASS | 11905.1095 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 533075 [VIOLA 4 138.00] TO BUS 532833 [VIOL2X1 13.800] CKT 2 | 11.5664 | PASS | 12.0051 | PASS | 11905.1095 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 139.0884 | PASS | 13.8716 | PASS | 13771.6388 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 14.0039 | PASS | 9.8638 | PASS | 9763.7849 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 26.2284 | PASS | 11.0878 | PASS | 10987.8057 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 20.5348 | PASS | 11.8824 | PASS | 11782.4137 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 5.9855 | FAIL | 23.2156 | PASS | 23115.579 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 5.9855 | FAIL | 23.2156 | PASS | 23115.579 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 5.9855 | FAIL | 46.868 | PASS | 46768.0224 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2343 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2343 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 13.5717 | PASS | 0.3024 | PASS | 202.4304 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 15.5265 | PASS | 5.0446 | PASS | 4944.5721 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 26.0264 | PASS | 1.6867 | PASS | 1586.6503 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 26.0264 | PASS | 1.6867 | PASS | 1586.6503 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 21.1114 | PASS | 2.986 | PASS | 2885.9678 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 24.8225 | PASS | 6.06 | PASS | 5960.0493 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 24.8225 | PASS | 1.7195 | PASS | 1619.4558 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 40.8998 | PASS | 14.72 | PASS | 14620.0451 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 23.9758 | PASS | 5.462 | PASS | 5361.9792 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 23.5562 | PASS | 5.4529 | PASS | 5352.8803 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 9.4871 | PASS | 0.2604 | PASS | 160.4436 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 9.4871 | PASS | 0.2489 | PASS | 148.9368 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 12.327 | PASS | 11.7271 | PASS | 11627.0798 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 532935 [MARMTNW5 161.00] CKT Z1 | 12.327 | PASS | 11.7271 | PASS | 11627.0798 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 139.1171 | PASS | 13.8707 | PASS | 13770.7424 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 14.1552 | PASS | 9.8468 | PASS | 9746.7915 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 27.1991 | PASS | 11.0706 | PASS | 10970.6413 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 20.5341 | PASS | 11.882 | PASS | 11782.0214 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 6.0179 | PASS | 23.2101 | PASS | 23110.1276 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 6.0179 | PASS | 23.2101 | PASS | 23110.1276 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 6.0179 | PASS | 46.7493 | PASS | 46649.3118 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.278 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.278 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 13.5938 | PASS | 0.3025 | PASS | 202.5182 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.4851 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 26.0277 | PASS | 1.6866 | PASS | 1586.6482 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 26.0277 | PASS | 1.6866 | PASS | 1586.6482 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 21.1118 | PASS | 298.6% | PASS | 2886.0757 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9972 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 24.8224 | PASS | 171.9% | PASS | 1619.4593 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 40.9008 | PASS | 14.72 | PASS | 14620.0301 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 23.9766 | PASS | 5.462 | PASS | 5361.9626 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 23.557 | PASS | 5.4528 | PASS | 5352.8383 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 9.4875 | PASS | 0.2604 | PASS | 160.4429 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 9.4875 | PASS | 0.2489 | PASS | 148.9359 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 12.3281 | PASS | 11.7267 | PASS | 11626.6637 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 533639 [MARMATN2 69.000] TO BUS 532955 [MARMATN1 13.200] CKT 1 | 12.3281 | PASS | 11.7267 | PASS | 11626.6637 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 138.8603 | PASS | 13.8652 | PASS | 13765.1582 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 14.1768 | PASS | 9.8586 | PASS | 9758.6102 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 27.279 | PASS | 11.0765 | PASS | 10976.5215 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 20.5338 | PASS | 11.8821 | PASS | 11782.0769 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.0203 | PASS | 23.212 | PASS | 23111.9621 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.0203 | PASS | 23.212 | PASS | 23111.9621 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.0203 | PASS | 46.7735 | PASS | 46673.4842 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 11.0058 | PASS | 36.5449 | PASS | 36444.9146 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 11.0058 | PASS | 36.5449 | PASS | 36444.9146 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5504 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 15.5241 | PASS | 5.0441 | PASS | 4944.0573 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6278 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6278 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 21.1074 | PASS | 2.9853 | PASS | 2885.2561 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9828 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4602 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 40.9012 | PASS | 14.72 | PASS | 14619.9501 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8303 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7644 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.4829 | PASS | 0.2604 | PASS | 160.4461 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.4829 | PASS | 0.2489 | PASS | 148.9398 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 12.1386 | PASS | 11.7209 | PASS | 11620.8706 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 12.1386 | PASS | 11.7209 | PASS | 11620.8706 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 139.0375 | PASS | 13.8701 | PASS | 13770.1319 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 13.4692 | PASS | 9.8446 | PASS | 9744.6366 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 26.9087 | PASS | 11.0715 | PASS | 10971.4577 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 20.5238 | PASS | 11.8809 | PASS | 11780.9368 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 6.0014 | PASS | 23.2102 | PASS | 23110.2143 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 6.0014 | PASS | 23.2102 | PASS | 23110.2143 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 6.0014 | PASS | 46.8685 | PASS | 46768.451 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 11.0061 | PASS | 36.5452 | PASS | 36445.165 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 11.0061 | PASS | 36.5452 | PASS | 36445.165 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 13.5844 | PASS | 0.3026 | PASS | 202.615 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 15.5263 | PASS | 5.0446 | PASS | 4944.577 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6215 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6215 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 21.1106 | PASS | 2.9857 | PASS | 2885.6908 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 24.8223 | PASS | 6.06 | PASS | 5959.9576 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4619 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.9212 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 23.9767 | PASS | 5.4618 | PASS | 5361.7879 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 23.5571 | PASS | 5.4527 | PASS | 5352.7168 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 9.4856 | PASS | 0.2604 | PASS | 160.4439 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 9.4856 | PASS | 0.2489 | PASS | 148.9372 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 12.3249 | PASS | 11.7265 | PASS | 11626.4549 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 12.3249 | PASS | 11.7265 | PASS | 11626.4549 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 138.4331 | PASS | 13.8694 | PASS | 13769.3608 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 13.5373 | PASS | 9.8632 | PASS | 9763.1639 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 26.9158 | PASS | 11.0766 | PASS | 10976.5671 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 20.4054 | PASS | 11.8813 | PASS | 11781.3361 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 6.008 | PASS | 23.2122 | PASS | 23112.2041 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 6.008 | PASS | 23.2122 | PASS | 23112.2041 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 6.008 | PASS | 46.7274 | PASS | 46627.4304 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 11.006 | PASS | 36.5455 | PASS | 36445.4816 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 11.006 | PASS | 36.5455 | PASS | 36445.4816 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 13.5921 | PASS | 0.3025 | PASS | 202.5257 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 15.5238 | PASS | 5.0446 | PASS | 4944.6389 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6296 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6296 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 21.1075 | PASS | 2.9861 | PASS | 2886.1138 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9724 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.461 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9491 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8348 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.717 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 9.4663 | PASS | 0.2605 | PASS | 160.4536 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 9.4663 | PASS | 0.2489 | PASS | 148.9492 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 12.3013 | PASS | 11.7262 | PASS | 11626.1953 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533001 [ALTOONA4 138.00] CKT 1 | 12.3013 | PASS | 11.7262 | PASS | 11626.1953 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 138.9783 | PASS | 13.8644 | PASS | 13764.4264 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 13.6412 | PASS | 9.8971 | PASS | 9797.135 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 27.0792 | PASS | 11.0569 | PASS | 10956.9039 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 20.5269 | PASS | 11.8831 | PASS | 11783.0842 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 6.0083 | PASS | 23.2026 | PASS | 23102.5893 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 6.0083 | PASS | 23.2026 | PASS | 23102.5893 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 6.0083 | PASS | 46.7167 | PASS | 46616.6689 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 11.0054 | PASS | 36.5441 | PASS | 36444.0795 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 11.0054 | PASS | 36.5441 | PASS | 36444.0795 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 13.5771 | PASS | 0.3039 | PASS | 203.8546 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 15.5248 | PASS | 5.0423 | PASS | 4942.2948 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 26.0272 | PASS | 1.6865 | PASS | 1586.5494 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 26.0272 | PASS | 1.6865 | PASS | 1586.5494 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 21.1092 | PASS | 2.9846 | PASS | 2884.6238 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 24.8222 | PASS | 6.0599 | PASS | 5959.8938 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 24.8222 | PASS | 1.7195 | PASS | 1619.4663 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 40.8998 | PASS | 14.7196 | PASS | 14619.592 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 23.9762 | PASS | 5.4614 | PASS | 5361.3705 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 23.5565 | PASS | 5.4523 | PASS | 5352.3085 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 9.4825 | PASS | 0.2604 | PASS | 160.4414 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 9.4825 | PASS | 0.2489 | PASS | 148.9339 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 12.3195 | PASS | 11.7224 | PASS | 11622.3987 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533006 [TAYLOR 4 138.00] CKT 1 | 12.3195 | PASS | 11.7224 | PASS | 11622.3987 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 139.1112 | PASS | 13.87 | PASS | 13770.0148 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 14.1311 | PASS | 9.8369 | PASS | 9736.9122 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 27.2599 | PASS | 11.0704 | PASS | 10970.4055 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 20.5316 | PASS | 11.8809 | PASS | 11780.9409 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 6.0192 | PASS | 23.2094 | PASS | 23109.4168 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 6.0192 | PASS | 23.2094 | PASS | 23109.4168 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 6.0192 | PASS | 46.7679 | PASS | 46667.9313 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 11.0063 | PASS | 36.5454 | PASS | 36445.3858 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 11.0063 | PASS | 36.5454 | PASS | 36445.3858 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 13.5929 | PASS | 0.3026 | PASS | 202.6201 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 15.5267 | PASS | 5.0447 | PASS | 4944.6718 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 26.0284 | PASS | 1.6867 | PASS | 1586.6542 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 26.0284 | PASS | 1.6867 | PASS | 1586.6542 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 21.1119 | PASS | 2.9862 | PASS | 2886.1741 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 24.822 | PASS | 6.0598 | PASS | 5959.8029 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 24.822 | PASS | 1.7195 | PASS | 1619.4723 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 40.9016 | PASS | 14.7201 | PASS | 14620.0629 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 23.9771 | PASS | 5.462 | PASS | 5361.9719 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 23.5574 | PASS | 5.4529 | PASS | 5352.8607 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4431 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9361 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 12.3279 | PASS | 11.7264 | PASS | 11626.4481 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 588660 [GEN-2017-022138.00] CKT 1 | 12.3279 | PASS | 11.7264 | PASS | 11626.4481 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 139.1103 | PASS | 13.8702 | PASS | 13770.1696 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 14.1819 | PASS | 9.8547 | PASS | 9754.6529 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 27.2796 | PASS | 11.0735 | PASS | 10973.4941 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 20.5334 | PASS | 11.8817 | PASS | 11781.6791 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 6.0202 | PASS | 23.2108 | PASS | 23110.8431 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 6.0202 | PASS | 23.2108 | PASS | 23110.8431 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 6.0202 | PASS | 46.7417 | PASS | 46641.6642 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.0061 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.0061 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 13.5925 | PASS | 0.3027 | PASS | 202.6914 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 15.5265 | PASS | 5.0444 | PASS | 4944.4184 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6032 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6032 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 21.1107 | PASS | 2.9855 | PASS | 2885.4553 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 24.8226 | PASS | 6.0601 | PASS | 5960.0566 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 24.8226 | PASS | 1.7195 | PASS | 1619.4553 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 40.9008 | PASS | 14.7198 | PASS | 14619.8381 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 23.9767 | PASS | 5.4617 | PASS | 5361.6878 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 23.5571 | PASS | 5.4526 | PASS | 5352.6245 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4433 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9364 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 12.3277 | PASS | 11.7264 | PASS | 11626.3625 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533674 [ALTOO W2 69.000] TO BUS 533086 [ALTOO1 1 13.200] CKT 1 | 12.3277 | PASS | 11.7264 | PASS | 11626.3625 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 139.1111 | PASS | 13.8705 | PASS | 13770.5367 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 14.1812 | PASS | 9.8595 | PASS | 9759.4642 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 27.2776 | PASS | 11.0751 | PASS | 10975.1047 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 20.534 | PASS | 11.882 | PASS | 11782.004 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 6.0202 | PASS | 23.2116 | PASS | 23111.5581 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 6.0202 | PASS | 23.2116 | PASS | 23111.5581 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 6.0202 | PASS | 46.7409 | PASS | 46640.9078 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36444.9855 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36444.9855 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 13.5923 | PASS | 0.3027 | PASS | 202.6622 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 15.5265 | PASS | 5.0444 | PASS | 4944.4376 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.6005 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.6005 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 21.1106 | PASS | 2.9854 | PASS | 2885.4172 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 24.8226 | PASS | 6.0601 | PASS | 5960.0806 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 24.8226 | PASS | 1.7195 | PASS | 1619.4538 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 40.9008 | PASS | 14.7198 | PASS | 14619.8266 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 23.9767 | PASS | 5.4617 | PASS | 5361.6738 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 23.5571 | PASS | 5.4526 | PASS | 5352.615 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 12.3277 | PASS | 11.7265 | PASS | 11626.5232 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533673 [ALTOO E2 69.000] TO BUS 533087 [ALTOO3 1 13.200] CKT 1 | 12.3277 | PASS | 11.7265 | PASS | 11626.5232 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 138.9992 | PASS | 13.8603 | PASS | 13760.2816 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 13.9954 | PASS | 9.8372 | PASS | 9737.1771 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 26.3228 | PASS | 11.0947 | PASS | 10994.6745 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 20.5292 | PASS | 11.8799 | PASS | 11779.8673 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 5.9752 | FAIL | 23.2189 | PASS | 23118.9089 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 5.9752 | FAIL | 23.2189 | PASS | 23118.9089 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 5.9752 | FAIL | 46.9427 | PASS | 46842.7311 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.15 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.15 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 13.5618 | PASS | 0.303 | PASS | 202.9928 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 15.5253 | PASS | 5.043 | PASS | 4943.0314 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 26.0272 | PASS | 1.6866 | PASS | 1586.5742 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 26.0272 | PASS | 1.6866 | PASS | 1586.5742 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 21.1117 | PASS | 2.9862 | PASS | 2886.1792 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 24.8221 | PASS | 6.0599 | PASS | 5959.8859 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 24.8221 | PASS | 1.7195 | PASS | 1619.4668 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 40.8998 | PASS | 14.7197 | PASS | 14619.6863 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 23.9762 | PASS | 5.4615 | PASS | 5361.5187 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 23.5563 | PASS | 5.4523 | PASS | 5352.3353 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 9.4834 | PASS | 0.2604 | PASS | 160.4392 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 9.4834 | PASS | 0.2489 | PASS | 148.931 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 12.3199 | PASS | 11.7208 | PASS | 11620.8165 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 12.3199 | PASS | 11.7208 | PASS | 11620.8165 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 139.1066 | PASS | 13.8707 | PASS | 13770.6641 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 13.3948 | PASS | 9.8718 | PASS | 9771.7651 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 26.5838 | PASS | 11.0698 | PASS | 10969.7508 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 20.5338 | PASS | 11.8821 | PASS | 11782.08 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 6.0157 | PASS | 23.2133 | PASS | 23113.2667 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 6.0157 | PASS | 23.2133 | PASS | 23113.2667 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 6.0157 | PASS | 46.8235 | PASS | 46723.5333 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0994 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0994 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 13.5898 | PASS | 0.3026 | PASS | 202.5636 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 15.5265 | PASS | 5.0445 | PASS | 4944.4833 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6214 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6214 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 21.1111 | PASS | 2.9857 | PASS | 2885.6903 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 24.8224 | PASS | 6.06 | PASS | 5959.9777 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4606 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9194 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7916 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7175 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 9.4875 | PASS | 26.04% | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 9.4875 | PASS | 0.2489 | PASS | 148.9365 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 12.3276 | PASS | 1173% | PASS | 11626.5822 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533020 [NEOSHOS4 138.00] TO BUS 533021 [NEOSHO 4 138.00] CKT Z1 | 12.3276 | PASS | 11.7266 | PASS | 11626.5822 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 139.1162 | PASS | 13.8719 | PASS | 13771.8901 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 6.9297 | PASS | 9.9812 | PASS | 9881.1615 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 26.6925 | PASS | 11.0615 | PASS | 10961.5456 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 20.5352 | PASS | 11.8842 | PASS | 11784.1815 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 5.9913 | FAIL | 23.2059 | PASS | 23105.8589 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 5.9913 | FAIL | 23.2059 | PASS | 23105.8589 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 5.9913 | FAIL | 46.4831 | PASS | 46383.0931 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1733 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1733 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 13.5787 | PASS | 0.303 | PASS | 203.0151 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 15.5266 | PASS | 5.0446 | PASS | 4944.6264 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 26.0279 | PASS | 1.6866 | PASS | 1586.6086 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 26.0279 | PASS | 1.6866 | PASS | 1586.6086 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 21.1113 | PASS | 2.9858 | PASS | 2885.8432 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9336 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4635 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 40.9008 | PASS | 14.7199 | PASS | 14619.8537 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 23.9766 | PASS | 5.4617 | PASS | 5361.7039 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 23.557 | PASS | 5.4526 | PASS | 5352.5985 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 9.4876 | PASS | 0.2604 | PASS | 160.4437 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 9.4876 | PASS | 0.2489 | PASS | 148.937 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 12.3283 | PASS | 11.7272 | PASS | 11627.16 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533021 [NEOSHO 4 138.00] TO BUS 533022 [NEOSHON4 138.00] CKT Z1 | 12.3283 | PASS | 11.7272 | PASS | 11627.16 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 116.5274 | PASS | 13.8478 | PASS | 13747.7591 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 14.1755 | PASS | 9.8592 | PASS | 9759.2473 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 27.2723 | PASS | 11.0771 | PASS | 10977.0918 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 20.5349 | PASS | 11.8824 | PASS | 11782.4093 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 6.0192 | PASS | 23.2127 | PASS | 23112.7358 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 6.0192 | PASS | 23.2127 | PASS | 23112.7358 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 6.0192 | PASS | 46.7812 | PASS | 46681.2064 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 11.006 | PASS | 36.5452 | PASS | 36445.2135 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 11.006 | PASS | 36.5452 | PASS | 36445.2135 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 13.5887 | PASS | 0.3025 | PASS | 202.5327 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 15.5251 | PASS | 5.0445 | PASS | 4944.5194 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6269 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6269 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 21.1092 | PASS | 2.9858 | PASS | 2885.7687 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9839 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4602 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9435 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8241 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7456 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 9.4839 | PASS | 0.2604 | PASS | 160.4442 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 9.4839 | PASS | 0.2489 | PASS | 148.9376 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 11.7327 | PASS | 11.7198 | PASS | 11619.7886 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533046 [GILL S 4 138.00] CKT 1 | 11.7327 | PASS | 11.7198 | PASS | 11619.7886 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 127.3271 | PASS | 13.844 | PASS | 13744.013 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 14.1765 | PASS | 9.8586 | PASS | 9758.6053 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 27.2785 | PASS | 11.0765 | PASS | 10976.5342 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 20.5341 | PASS | 11.8819 | PASS | 11781.9352 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 6.0202 | PASS | 23.2119 | PASS | 23111.921 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 6.0202 | PASS | 23.2119 | PASS | 23111.921 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 6.0202 | PASS | 46.7811 | PASS | 46681.1461 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1212 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1212 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 13.5926 | PASS | 0.3025 | PASS | 202.5295 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.4575 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6298 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6298 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 21.111 | PASS | 2.9856 | PASS | 2885.6177 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9778 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4606 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 40.9012 | PASS | 14.72 | PASS | 14619.9559 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8393 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7595 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 9.4891 | PASS | 0.2604 | PASS | 160.4407 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 9.4891 | PASS | 0.2489 | PASS | 148.9331 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 12.3307 | PASS | 11.7235 | PASS | 11623.5287 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533047 [GILL 4 138.00] CKT 1 | 12.3307 | PASS | 11.7235 | PASS | 11623.5287 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 127.2669 | PASS | 13.8575 | PASS | 13757.5094 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 14.1768 | PASS | 9.8587 | PASS | 9758.7181 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 27.2789 | PASS | 11.0766 | PASS | 10976.6397 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 20.5343 | PASS | 11.882 | PASS | 11781.9964 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.0202 | PASS | 23.212 | PASS | 23112.0305 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.0202 | PASS | 23.212 | PASS | 23112.0305 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 6.0202 | PASS | 46.7822 | PASS | 46682.1562 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0696 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0696 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 13.5928 | PASS | 0.3025 | PASS | 202.5129 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 15.5266 | PASS | 5.0443 | PASS | 4944.2786 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6311 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6311 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 21.1111 | PASS | 2.9855 | PASS | 2885.4946 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.978 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4606 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 40.9013 | PASS | 14.72 | PASS | 14619.9618 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8476 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7678 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.4893 | PASS | 0.2604 | PASS | 160.4403 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 9.4893 | PASS | 0.2489 | PASS | 148.9326 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 12.3316 | PASS | 11.7215 | PASS | 11621.5338 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533036 [CLEARWT4 138.00] TO BUS 533075 [VIOLA 4 138.00] CKT 1 | 12.3316 | PASS | 11.7215 | PASS | 11621.5338 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 126.2811 | PASS | 13.8754 | PASS | 13775.4485 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8603 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 27.2806 | PASS | 11.0767 | PASS | 10976.7364 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 20.534 | PASS | 11.8822 | PASS | 11782.2111 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2507 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2507 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 6.0206 | PASS | 46.7717 | PASS | 46671.6846 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1947 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1947 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 13.5934 | PASS | 0.3025 | PASS | 202.5449 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.5223 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6268 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6268 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7575 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9804 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9426 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8226 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7406 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 9.4859 | PASS | 0.2604 | PASS | 160.4431 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 9.4859 | PASS | 0.2489 | PASS | 148.9362 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 12.009 | PASS | 11.7297 | PASS | 11629.708 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533051 [INTERST4 138.00] CKT 1 | 12.009 | PASS | 11.7297 | PASS | 11629.708 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 139.1198 | PASS | 13.8712 | PASS | 13771.175 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8689 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7287 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2811 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2497 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2497 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 6.0206 | PASS | 46.772 | PASS | 46672.0205 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1627 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1627 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 13.5932 | PASS | 0.3025 | PASS | 202.55 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6241 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7655 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 24.8224 | PASS | 6.06 | PASS | 5959.9817 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9404 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8199 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7411 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 12.3228 | PASS | 11.727 | PASS | 11626.9575 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533047 [GILL 4 138.00] CKT Z1 | 12.3228 | PASS | 11.727 | PASS | 11626.9575 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 138.0912 | PASS | 13.8614 | PASS | 13761.3875 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.7927 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 27.2803 | PASS | 11.0767 | PASS | 10976.6678 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 20.5346 | PASS | 11.8822 | PASS | 11782.2052 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1628 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1628 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 6.0205 | PASS | 46.7723 | PASS | 46672.2635 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1185 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1185 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.55 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.4514 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6265 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6265 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 21.1111 | PASS | 2.9857 | PASS | 2885.6547 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9805 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9421 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8213 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7435 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4431 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9361 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 12.2998 | PASS | 11.7233 | PASS | 11623.2522 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533796 [GILL W 2 69.000] TO BUS 533107 [GILL S 2 13.200] CKT 1 | 12.2998 | PASS | 11.7233 | PASS | 11623.2522 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 137.8593 | PASS | 13.8718 | PASS | 13771.7546 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 14.1773 | PASS | 9.8587 | PASS | 9758.6995 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 27.2801 | PASS | 11.0766 | PASS | 10976.5918 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 20.5344 | PASS | 11.8821 | PASS | 11782.1307 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.0716 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.0716 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 6.0205 | PASS | 46.772 | PASS | 46671.9542 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1139 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1139 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 13.5933 | PASS | 0.3026 | PASS | 202.5559 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 15.5265 | PASS | 5.0444 | PASS | 4944.4221 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6261 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6261 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 21.111 | PASS | 2.9856 | PASS | 2885.6378 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9803 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9406 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8189 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7415 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.443 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.936 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 12.2959 | PASS | 11.7272 | PASS | 11627.1874 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533795 [GILL E 2 69.000] TO BUS 533106 [GILL S 1 13.200] CKT 1 | 12.2959 | PASS | 11.7272 | PASS | 11627.1874 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 127.0297 | PASS | 13.8879 | PASS | 13787.9185 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 14.1775 | PASS | 9.8588 | PASS | 9758.8338 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 27.28 | PASS | 11.0767 | PASS | 10976.6898 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 20.5335 | PASS | 11.8822 | PASS | 11782.2287 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2164 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2164 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 6.0205 | PASS | 46.7724 | PASS | 46672.4063 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0995 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0995 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 13.5931 | PASS | 0.3026 | PASS | 202.5579 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 15.526 | PASS | 5.0445 | PASS | 4944.5023 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6248 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6248 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 21.1103 | PASS | 2.9857 | PASS | 2885.6662 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 24.8224 | PASS | 6.06 | PASS | 5959.9842 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4602 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9357 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 23.9768 | PASS | 5.4618 | PASS | 5361.8126 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 23.5573 | PASS | 5.4527 | PASS | 5352.742 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 9.4832 | PASS | 0.2604 | PASS | 160.4457 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 9.4832 | PASS | 0.2489 | PASS | 148.9394 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 12.0368 | PASS | 11.734 | PASS | 11633.9759 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533072 [WACO 4 138.00] CKT Z1 | 12.0368 | PASS | 11.734 | PASS | 11633.9759 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 138.814 | PASS | 13.8721 | PASS | 13772.0911 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8899 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 27.2801 | PASS | 1108% | PASS | 10976.7447 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2953 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 6.0205 | PASS | 2321% | PASS | 23112.274 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.274 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 6.0205 | PASS | 46.7726 | PASS | 46672.5594 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 11.0057 | PASS | 36.5456 | PASS | 36445.5511 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 11.0057 | PASS | 36.5456 | PASS | 36445.5511 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5526 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 15.5222 | PASS | 5.044 | PASS | 4944.0403 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6238 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6238 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 21.1055 | PASS | 2.9858 | PASS | 2885.8347 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9799 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9299 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.8067 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7283 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 9.4877 | PASS | 0.2604 | PASS | 160.4437 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 9.4877 | PASS | 0.2489 | PASS | 148.9369 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 12.28 | PASS | 11.728 | PASS | 11628.0107 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539008 [MILAN_GOAB 138.00] CKT 1 | 12.28 | PASS | 11.728 | PASS | 11628.0107 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 138.3894 | PASS | 13.8724 | PASS | 13772.3737 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 14.1774 | PASS | 9.8589 | PASS | 9758.8986 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 27.2796 | PASS | 11.0768 | PASS | 10976.7524 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.303 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 6.0204 | PASS | 23.2123 | PASS | 23112.2848 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 6.0204 | PASS | 23.2123 | PASS | 23112.2848 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 6.0204 | PASS | 46.7727 | PASS | 46672.7057 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 11.0048 | PASS | 36.5454 | PASS | 36445.4293 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 11.0048 | PASS | 36.5454 | PASS | 36445.4293 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 13.5927 | PASS | 0.3026 | PASS | 202.5534 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 15.5149 | PASS | 5.0441 | PASS | 4944.0677 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6233 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6233 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 21.0957 | PASS | 2.9857 | PASS | 2885.6519 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9805 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9283 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.8042 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.726 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 9.4872 | PASS | 0.2604 | PASS | 160.4442 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 9.4872 | PASS | 0.2489 | PASS | 148.9375 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 12.2145 | PASS | 11.7288 | PASS | 11628.8041 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 539009 [CONWAY 138.00] CKT 1 | 12.2145 | PASS | 11.7288 | PASS | 11628.8041 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 139.0742 | PASS | 13.8707 | PASS | 13770.7441 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 14.1769 | PASS | 9.8589 | PASS | 9758.861 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 27.2795 | PASS | 11.0767 | PASS | 10976.7272 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 18.5618 | PASS | 11.9068 | PASS | 11806.8248 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.3322 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.3322 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 6.0205 | PASS | 46.7719 | PASS | 46671.8923 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 11.006 | PASS | 36.545 | PASS | 36444.9617 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 11.006 | PASS | 36.545 | PASS | 36444.9617 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 13.593 | PASS | 0.3025 | PASS | 202.5492 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 15.5259 | PASS | 5.0444 | PASS | 4944.353 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 26.0267 | PASS | 1.6865 | PASS | 1586.5184 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 26.0267 | PASS | 1.6865 | PASS | 1586.5184 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 21.1095 | PASS | 2.9852 | PASS | 2885.1815 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 24.8222 | PASS | 6.0599 | PASS | 5959.8806 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 24.8222 | PASS | 1.7195 | PASS | 1619.4672 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 40.8995 | PASS | 14.7195 | PASS | 14619.5233 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 23.9759 | PASS | 5.4612 | PASS | 5361.2029 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 23.5566 | PASS | 5.4523 | PASS | 5352.2816 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 9.4622 | PASS | 0.2605 | PASS | 160.4648 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 9.4622 | PASS | 0.249 | PASS | 148.9628 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 12.3259 | PASS | 11.7266 | PASS | 11626.6018 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533306 [READING3 115.00] CKT 1 | 12.3259 | PASS | 11.7266 | PASS | 11626.6018 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 139.1014 | PASS | 13.8702 | PASS | 13770.2334 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 14.1748 | PASS | 9.8585 | PASS | 9758.5356 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 27.2788 | PASS | 11.0767 | PASS | 10976.7198 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 19.8092 | PASS | 11.8845 | PASS | 11784.5474 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 6.0204 | PASS | 23.2121 | PASS | 23112.0547 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 6.0204 | PASS | 23.2121 | PASS | 23112.0547 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 6.0204 | PASS | 46.7724 | PASS | 46672.3621 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2422 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2422 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5643 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 15.5262 | PASS | 5.0443 | PASS | 4944.3154 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.6069 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.6069 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 21.1111 | PASS | 2.9858 | PASS | 2885.8363 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9802 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 40.9008 | PASS | 14.7199 | PASS | 14619.8654 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 23.9767 | PASS | 5.4617 | PASS | 5361.7154 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 23.5571 | PASS | 5.4527 | PASS | 5352.6795 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 9.4839 | PASS | 0.2604 | PASS | 160.4493 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 9.4839 | PASS | 0.2489 | PASS | 148.9438 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 12.3274 | PASS | 11.7264 | PASS | 11626.3697 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533304 [LANG 3 115.00] CKT 1 | 12.3274 | PASS | 11.7264 | PASS | 11626.3697 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 139.0982 | PASS | 13.8702 | PASS | 13770.2063 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 14.1743 | PASS | 9.8585 | PASS | 9758.4898 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 27.2784 | PASS | 11.0767 | PASS | 10976.6859 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 19.7422 | PASS | 11.8887 | PASS | 11788.6828 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 6.0203 | PASS | 23.2121 | PASS | 23112.0504 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 6.0203 | PASS | 23.2121 | PASS | 23112.0504 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 6.0203 | PASS | 46.7725 | PASS | 46672.505 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2333 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2333 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5651 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 15.5262 | PASS | 5.0443 | PASS | 4944.2953 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.609 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.609 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 21.111 | PASS | 2.9858 | PASS | 2885.8095 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9818 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 40.9008 | PASS | 14.7199 | PASS | 14619.8733 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 23.9767 | PASS | 5.4617 | PASS | 5361.7266 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 23.5571 | PASS | 5.4527 | PASS | 5352.6867 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 9.4836 | PASS | 0.2604 | PASS | 160.4486 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 9.4836 | PASS | 0.2489 | PASS | 148.9429 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 12.3273 | PASS | 11.7264 | PASS | 11626.3621 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 533307 [PRAIRIE3 115.00] CKT 1 | 12.3273 | PASS | 11.7264 | PASS | 11626.3621 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 139.1195 | PASS | 13.8712 | PASS | 13771.2213 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 14.1717 | PASS | 9.8588 | PASS | 9758.7527 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 27.2677 | PASS | 11.0766 | PASS | 10976.647 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2744 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 6.0199 | PASS | 23.2122 | PASS | 23112.2178 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 6.0199 | PASS | 23.2122 | PASS | 23112.2178 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 6.0199 | PASS | 46.7706 | PASS | 46670.5996 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1591 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1591 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 13.5928 | PASS | 0.3026 | PASS | 202.5589 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6201 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6255 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6255 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7611 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 24.8224 | PASS | 6.06 | PASS | 5959.9804 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9372 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8148 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 23.5573 | PASS | 5.4527 | PASS | 5352.737 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 9.4879 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 12.3283 | PASS | 11.7269 | PASS | 11626.9109 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533778 [NEOSHOS2 69.000] CKT Z1 | 12.3283 | PASS | 11.7269 | PASS | 11626.9109 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 138.7126 | PASS | 13.8708 | PASS | 13770.7998 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8879 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 27.2803 | PASS | 11.0767 | PASS | 10976.7451 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2961 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2689 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2689 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 6.0206 | PASS | 46.7724 | PASS | 46672.3505 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1649 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1649 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 13.5931 | PASS | 0.3025 | PASS | 202.5489 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6421 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6263 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6263 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7757 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 24.8224 | PASS | 6.06 | PASS | 5959.9819 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 40.9012 | PASS | 14.7199 | PASS | 14619.941 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8201 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7416 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 9.488 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 12.3186 | PASS | 11.7268 | PASS | 11626.802 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533796 [GILL W 2 69.000] CKT Z1 | 12.3186 | PASS | 11.7268 | PASS | 11626.802 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 139.1171 | PASS | 13.8703 | PASS | 13770.3098 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.799 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 27.2802 | PASS | 11.0767 | PASS | 10976.6637 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 20.5345 | PASS | 11.8821 | PASS | 11782.1071 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.174 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.174 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 6.0205 | PASS | 46.7718 | PASS | 46671.8399 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 11.0046 | PASS | 36.5455 | PASS | 36445.5 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 11.0046 | PASS | 36.5455 | PASS | 36445.5 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5547 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 15.4346 | PASS | 5.0371 | PASS | 4937.129 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6293 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6293 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 21.074 | PASS | 2.9786 | PASS | 2878.5806 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9796 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4605 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 40.9012 | PASS | 14.72 | PASS | 14619.9548 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8356 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7576 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4427 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9357 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 12.3279 | PASS | 11.7263 | PASS | 11626.3254 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539679 [GRTBEND6 230.00] TO BUS 539920 [GRTBNDTT 13.800] CKT 1 | 12.3279 | PASS | 11.7263 | PASS | 11626.3254 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 139.0332 | PASS | 13.8721 | PASS | 13772.1408 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 14.1771 | PASS | 9.8588 | PASS | 9758.7887 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 27.2789 | PASS | 11.0766 | PASS | 10976.6201 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 20.5233 | PASS | 11.8827 | PASS | 11782.699 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 6.0203 | PASS | 23.2122 | PASS | 23112.1867 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 6.0203 | PASS | 23.2122 | PASS | 23112.1867 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 6.0203 | PASS | 46.7747 | PASS | 46674.7121 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 10.9803 | PASS | 36.5559 | PASS | 36455.9429 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 10.9803 | PASS | 36.5559 | PASS | 36455.9429 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 13.5921 | PASS | 0.3026 | PASS | 202.5905 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 14.3303 | PASS | 4.9211 | PASS | 4821.0576 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 26.0273 | PASS | 1.6866 | PASS | 1586.573 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 26.0273 | PASS | 1.6866 | PASS | 1586.573 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 20.6193 | PASS | 2.9696 | PASS | 2869.6394 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.983 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4602 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 40.9002 | PASS | 14.7197 | PASS | 14619.7237 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 23.9763 | PASS | 5.4615 | PASS | 5361.543 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 23.5569 | PASS | 5.4525 | PASS | 5352.5311 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 9.4782 | PASS | 0.2604 | PASS | 160.447 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 9.4782 | PASS | 0.2489 | PASS | 148.9411 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 12.325 | PASS | 11.7273 | PASS | 11627.2777 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 763862 [G19-054-TAP 230.00] CKT 1 | 12.325 | PASS | 11.7273 | PASS | 11627.2777 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 139.1147 | PASS | 13.8686 | PASS | 13768.6383 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 14.176 | PASS | 9.8581 | PASS | 9758.0871 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 27.2779 | PASS | 11.076 | PASS | 10975.9563 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 20.5311 | PASS | 11.8815 | PASS | 11781.5283 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 6.0202 | PASS | 23.2115 | PASS | 23111.512 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 6.0202 | PASS | 23.2115 | PASS | 23111.512 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 6.0202 | PASS | 46.7711 | PASS | 46671.083 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 11.0034 | PASS | 36.5452 | PASS | 36445.1858 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 11.0034 | PASS | 3655% | PASS | 36445.1858 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 13.5927 | PASS | 0.3026 | PASS | 202.6467 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 6.8294 | PASS | 502.3% | PASS | 4923.1032 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 26.0276 | PASS | 1.6866 | PASS | 1586.5721 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 26.0276 | PASS | 1.6866 | PASS | 1586.5721 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 21.1158 | PASS | 2.9776 | PASS | 2877.6267 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9744 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4609 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 40.9005 | PASS | 14.7197 | PASS | 14619.7333 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 23.9765 | PASS | 5.4615 | PASS | 5361.5428 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 23.5571 | PASS | 5.4526 | PASS | 5352.5964 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 9.4865 | PASS | 0.2604 | PASS | 160.4402 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 9.4865 | PASS | 0.2489 | PASS | 148.9325 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 12.3279 | PASS | 11.7256 | PASS | 11625.6108 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 12.3279 | PASS | 11.7256 | PASS | 11625.6108 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 139.1204 | PASS | 13.8712 | PASS | 13771.2136 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 14.1776 | PASS | 9.8588 | PASS | 9758.8208 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 27.2802 | PASS | 11.0767 | PASS | 10976.657 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 20.5346 | PASS | 11.8822 | PASS | 11782.1599 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 6.0205 | PASS | 23.2121 | PASS | 23112.1472 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 6.0205 | PASS | 23.2121 | PASS | 23112.1472 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 6.0205 | PASS | 46.7716 | PASS | 46671.6191 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 11.0061 | PASS | 36.5451 | PASS | 36445.1241 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 11.0061 | PASS | 36.5451 | PASS | 36445.1241 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 13.5932 | PASS | 0.3026 | PASS | 202.5618 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 15.5266 | PASS | 5.0446 | PASS | 4944.5743 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 26.0791 | PASS | 1.6741 | PASS | 1574.0623 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 26.0791 | PASS | 1.6741 | PASS | 1574.0623 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 21.1111 | PASS | 2.9857 | PASS | 2885.6698 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 24.8193 | PASS | 6.0584 | PASS | 5958.3819 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 24.8193 | PASS | 1.7196 | PASS | 1619.5672 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 40.8502 | PASS | 14.6775 | PASS | 14577.4985 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 23.9581 | PASS | 5.41 | PASS | 5310.0289 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 23.5451 | PASS | 5.4394 | PASS | 5339.3647 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 12.3284 | PASS | 11.7269 | PASS | 11626.9055 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541144 [NASHUA_CAP5 161.00] TO BUS 541203 [NASHUA 5 161.00] CKT R | 12.3284 | PASS | 11.7269 | PASS | 11626.9055 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 139.121 | PASS | 13.8713 | PASS | 13771.298 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.86 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 27.2803 | PASS | 11.0767 | PASS | 10976.7216 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2889 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2433 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2433 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 6.0206 | PASS | 46.7719 | PASS | 46671.9448 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1868 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1868 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 13.5932 | PASS | 0.3025 | PASS | 202.548 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 15.5267 | PASS | 5.0447 | PASS | 4944.6761 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 24.436 | PASS | 1.6851 | PASS | 1585.145 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 24.436 | PASS | 1.6851 | PASS | 1585.145 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 21.1113 | PASS | 2.9858 | PASS | 2885.8195 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 24.8219 | PASS | 6.0599 | PASS | 5959.9112 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 24.8219 | PASS | 1.7195 | PASS | 1619.465 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 40.0548 | PASS | 14.7149 | PASS | 14614.8832 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 23.5531 | PASS | 5.4519 | PASS | 5351.8948 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 23.5452 | PASS | 5.4515 | PASS | 5351.5075 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 12.3284 | PASS | 11.727 | PASS | 11626.9626 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541204 [SMTHVL 5 161.00] CKT 1 | 12.3284 | PASS | 11.727 | PASS | 11626.9626 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 139.1223 | PASS | 13.8715 | PASS | 13771.4577 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 14.1777 | PASS | 9.859 | PASS | 9758.9758 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 27.2801 | PASS | 11.0768 | PASS | 10976.847 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2926 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.3453 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.3453 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 6.0205 | PASS | 46.7727 | PASS | 46672.7469 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2284 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2284 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 13.593 | PASS | 0.3025 | PASS | 202.5348 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 15.5267 | PASS | 5.0447 | PASS | 4944.7152 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 26.0212 | PASS | 1.6864 | PASS | 1586.4243 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 26.0212 | PASS | 1.6864 | PASS | 1586.4243 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 21.1114 | PASS | 2.9859 | PASS | 2885.9026 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 15.4693 | PASS | 6.087 | PASS | 5986.9921 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 15.4693 | PASS | 1.7119 | PASS | 1611.9226 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 40.8838 | PASS | 14.7182 | PASS | 14618.1872 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 23.9725 | PASS | 5.4606 | PASS | 5360.5552 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 23.5348 | PASS | 5.4491 | PASS | 5349.1436 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4436 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9368 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 12.3285 | PASS | 11.7271 | PASS | 11627.0532 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541241 [SEDEAST5 161.00] CKT 1 | 12.3285 | PASS | 11.7271 | PASS | 11627.0532 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 139.1194 | PASS | 13.8711 | PASS | 13771.1371 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8539 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 27.2801 | PASS | 11.0767 | PASS | 10976.6981 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2592 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2197 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2197 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 6.0205 | PASS | 46.7719 | PASS | 46671.9336 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1325 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1325 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5647 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.5353 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 23.5589 | PASS | 1.6842 | PASS | 1584.1933 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 23.5589 | PASS | 1.6842 | PASS | 1584.1933 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 21.1112 | PASS | 2.9857 | PASS | 2885.7222 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 24.8119 | PASS | 6.0604 | PASS | 5960.3746 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 24.8119 | PASS | 1.7194 | PASS | 1619.4313 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 28.6616 | PASS | 14.7055 | PASS | 14605.4748 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 23.336 | PASS | 5.4465 | PASS | 5346.5075 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 23.2101 | PASS | 5.4571 | PASS | 5357.0835 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4433 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9365 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 12.3283 | PASS | 11.7268 | PASS | 11626.8435 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541250 [SIBLEYPL 161.00] CKT 1 | 12.3283 | PASS | 11.7268 | PASS | 11626.8435 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 139.125 | PASS | 13.8717 | PASS | 13771.6956 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 14.1784 | PASS | 9.8592 | PASS | 9759.1872 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 27.2818 | PASS | 11.0771 | PASS | 10977.1103 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 20.5347 | PASS | 11.8822 | PASS | 11782.2341 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 6.0208 | PASS | 23.2126 | PASS | 23112.5808 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 6.0208 | PASS | 23.2126 | PASS | 23112.5808 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 6.0208 | PASS | 46.7729 | PASS | 46672.9096 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 11.0063 | PASS | 36.5454 | PASS | 36445.3813 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 11.0063 | PASS | 36.5454 | PASS | 36445.3813 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 13.5938 | PASS | 0.3025 | PASS | 202.4748 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 15.5268 | PASS | 5.0448 | PASS | 4944.7964 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 22.1864 | PASS | 1.6886 | PASS | 1588.6283 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 22.1864 | PASS | 1.6886 | PASS | 1588.6283 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 21.1122 | PASS | 2.9864 | PASS | 2886.3576 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 24.8199 | PASS | 6.059 | PASS | 5959.0431 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 24.8199 | PASS | 1.7195 | PASS | 1619.5229 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 38.8571 | PASS | 14.7234 | PASS | 14623.4303 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 23.0926 | PASS | 5.4487 | PASS | 5348.6634 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 23.5378 | PASS | 5.4432 | PASS | 5343.2161 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 9.4883 | PASS | 0.2604 | PASS | 160.4437 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 9.4883 | PASS | 0.2489 | PASS | 148.937 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 12.3287 | PASS | 11.7272 | PASS | 11627.1788 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543039 [FRSTCRK5 161.00] CKT 1 | 12.3287 | PASS | 11.7272 | PASS | 11627.1788 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 139.0999 | PASS | 13.8691 | PASS | 13769.1469 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 14.1752 | PASS | 9.8578 | PASS | 9757.7543 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 27.276 | PASS | 11.0755 | PASS | 10975.4946 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 20.5344 | PASS | 11.8821 | PASS | 11782.1309 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 6.0199 | PASS | 23.2111 | PASS | 23111.11 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 6.0199 | PASS | 23.2111 | PASS | 23111.11 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 6.0199 | PASS | 46.7694 | PASS | 46669.3703 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.9274 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.9274 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 13.5917 | PASS | 0.3028 | PASS | 202.7597 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 15.5262 | PASS | 5.0438 | PASS | 4943.8331 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 26.0276 | PASS | 1.6867 | PASS | 1586.6857 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 26.0276 | PASS | 1.6867 | PASS | 1586.6857 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 21.1113 | PASS | 2.9857 | PASS | 2885.7021 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 24.8015 | PASS | 6.062 | PASS | 5962.0273 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 24.8015 | PASS | 1.7192 | PASS | 1619.2301 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 40.9013 | PASS | 14.7204 | PASS | 14620.3958 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 23.9768 | PASS | 5.4623 | PASS | 5362.2505 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 23.5568 | PASS | 5.4534 | PASS | 5353.3804 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 9.4867 | PASS | 0.2604 | PASS | 160.4422 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 9.4867 | PASS | 0.2489 | PASS | 148.9349 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 12.3266 | PASS | 11.7256 | PASS | 11625.585 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 541395 [NUCOR5 161.00] CKT 1 | 12.3266 | PASS | 11.7256 | PASS | 11625.585 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 139.12 | PASS | 13.8713 | PASS | 13771.2677 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8803 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 27.28 | PASS | 11.0767 | PASS | 10976.7433 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 20.5344 | PASS | 11.8823 | PASS | 11782.2801 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.2643 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.2643 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 6.0205 | PASS | 46.7727 | PASS | 46672.6794 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1686 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1686 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 13.5931 | PASS | 0.3025 | PASS | 202.5454 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.629 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 25.9048 | PASS | 1.6864 | PASS | 1586.3776 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 25.9048 | PASS | 1.6864 | PASS | 1586.3776 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7733 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 24.8143 | PASS | 6.0591 | PASS | 5959.0873 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 24.8143 | PASS | 1.7195 | PASS | 1619.5185 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 39.93 | PASS | 14.7164 | PASS | 14616.3952 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 23.9645 | PASS | 5.4612 | PASS | 5361.1515 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 18.8597 | PASS | 5.4353 | PASS | 5335.3402 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.936 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 548808 [ECKLES-161 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.936 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 139.1204 | PASS | 13.8712 | PASS | 13771.2179 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 14.1776 | PASS | 9.8588 | PASS | 9758.8135 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 27.2802 | PASS | 11.0766 | PASS | 10976.6466 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 20.5346 | PASS | 11.8822 | PASS | 11782.1727 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 6.0205 | PASS | 23.2121 | PASS | 23112.1317 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 6.0205 | PASS | 23.2121 | PASS | 23112.1317 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 6.0205 | PASS | 46.7716 | PASS | 46671.5819 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 11.0061 | PASS | 36.5451 | PASS | 36445.1348 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 11.0061 | PASS | 36.5451 | PASS | 36445.1348 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 13.5932 | PASS | 0.3026 | PASS | 202.5631 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 15.5267 | PASS | 5.0446 | PASS | 4944.5854 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 26.0261 | PASS | 1.6803 | PASS | 1580.3099 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 26.0261 | PASS | 1.6803 | PASS | 1580.3099 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 21.1111 | PASS | 2.9857 | PASS | 2885.6902 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 24.8191 | PASS | 6.0583 | PASS | 5958.3239 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 24.8191 | PASS | 1.7196 | PASS | 1619.571 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 40.8603 | PASS | 14.6977 | PASS | 14597.7132 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 23.9747 | PASS | 5.3605 | PASS | 5260.4696 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 23.5419 | PASS | 5.4365 | PASS | 5336.4643 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 12.3284 | PASS | 11.7269 | PASS | 11626.9088 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542946 [GLADSTN_CAP5161.00] TO BUS 543016 [GLADSTN5 161.00] CKT R | 12.3284 | PASS | 11.7269 | PASS | 11626.9088 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 139.1159 | PASS | 13.8708 | PASS | 13770.7986 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 14.1778 | PASS | 9.859 | PASS | 9759.0184 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 27.2794 | PASS | 11.0768 | PASS | 10976.7659 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 20.5343 | PASS | 11.8825 | PASS | 11782.4691 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 6.0203 | PASS | 23.2121 | PASS | 23112.1297 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 6.0203 | PASS | 23.2121 | PASS | 23112.1297 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 6.0203 | PASS | 46.7734 | PASS | 46673.4242 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 11.0063 | PASS | 36.5454 | PASS | 36445.3671 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 11.0063 | PASS | 36.5454 | PASS | 36445.3671 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 13.5924 | PASS | 0.3026 | PASS | 202.5986 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 15.5263 | PASS | 5.0442 | PASS | 4944.2078 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 25.1911 | PASS | 1.6945 | PASS | 1594.4824 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 25.1911 | PASS | 1.6945 | PASS | 1594.4824 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 21.1124 | PASS | 2.9866 | PASS | 2886.6442 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 24.7811 | PASS | 604.9% | PASS | 5949.0505 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 24.7811 | PASS | 1.7202 | PASS | 1620.1853 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 40.6985 | PASS | 1473% | PASS | 14630.1506 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 23.9032 | PASS | 5.455 | PASS | 5355.045 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 23.2273 | PASS | 5.4495 | PASS | 5349.4746 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 9.487 | PASS | 0.2604 | PASS | 160.4428 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 9.487 | PASS | 0.2489 | PASS | 148.9358 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 12.3278 | PASS | 11.7265 | PASS | 11626.4954 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 542980 [NASHUA 7 345.00] CKT 1 | 12.3278 | PASS | 11.7265 | PASS | 11626.4954 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 139.1038 | PASS | 13.8697 | PASS | 13769.6739 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 14.1774 | PASS | 9.8587 | PASS | 9758.7276 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 27.2794 | PASS | 11.0765 | PASS | 10976.4532 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 20.5313 | PASS | 11.8819 | PASS | 11781.8545 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 6.0204 | PASS | 23.2119 | PASS | 23111.8936 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 6.0204 | PASS | 23.2119 | PASS | 23111.8936 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 6.0204 | PASS | 46.7717 | PASS | 46671.678 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 11.0054 | PASS | 36.5441 | PASS | 36444.0799 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 11.0054 | PASS | 36.5441 | PASS | 36444.0799 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 13.5922 | PASS | 0.3027 | PASS | 202.6918 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 15.5255 | PASS | 5.043 | PASS | 4942.9692 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 24.8473 | PASS | 1.6818 | PASS | 1581.784 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 24.8473 | PASS | 1.6818 | PASS | 1581.784 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 21.1069 | PASS | 2.9831 | PASS | 2883.077 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 24.809 | PASS | 6.0576 | PASS | 5957.5677 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 24.809 | PASS | 1.7196 | PASS | 1619.6198 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 40.1107 | PASS | 14.7025 | PASS | 14602.5337 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 23.5049 | PASS | 5.4363 | PASS | 5336.2802 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 23.3667 | PASS | 5.4389 | PASS | 5338.8681 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 9.4852 | PASS | 0.2604 | PASS | 160.4421 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 9.4852 | PASS | 0.2489 | PASS | 148.9348 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 12.3268 | PASS | 11.7258 | PASS | 11625.8109 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 542982 [IATAN 7 345.00] CKT 1 | 12.3268 | PASS | 11.7258 | PASS | 11625.8109 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 139.1184 | PASS | 13.8711 | PASS | 13771.0792 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 14.177 | PASS | 9.8587 | PASS | 9758.6781 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 27.2785 | PASS | 11.0765 | PASS | 10976.49 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 20.5342 | PASS | 11.8821 | PASS | 11782.1481 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 6.0203 | PASS | 23.212 | PASS | 23111.9837 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 6.0203 | PASS | 23.212 | PASS | 23111.9837 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 6.0203 | PASS | 46.7742 | PASS | 46674.1897 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 11.006 | PASS | 36.5451 | PASS | 36445.0834 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 11.006 | PASS | 36.5451 | PASS | 36445.0834 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 13.5925 | PASS | 0.3026 | PASS | 202.5882 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.5231 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 25.1735 | PASS | 1.682 | PASS | 1582.0128 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 25.1735 | PASS | 1.682 | PASS | 1582.0128 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 21.1101 | PASS | 2.9852 | PASS | 2885.2304 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 24.8145 | PASS | 6.0583 | PASS | 5958.2765 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 24.8145 | PASS | 1.7196 | PASS | 1619.5731 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 40.3388 | PASS | 14.703 | PASS | 14603.0446 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 23.6303 | PASS | 5.4362 | PASS | 5336.1692 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 23.4384 | PASS | 5.439 | PASS | 5339.0461 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 9.4877 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 9.4877 | PASS | 0.2489 | PASS | 148.9365 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 12.3283 | PASS | 11.7268 | PASS | 11626.8453 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 761383 [G17-183-TAP 345.00] CKT 1 | 12.3283 | PASS | 11.7268 | PASS | 11626.8453 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 139.1209 | PASS | 13.8713 | PASS | 13771.2817 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 14.1778 | PASS | 9.8589 | PASS | 9758.9358 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 27.2806 | PASS | 11.0768 | PASS | 10976.8039 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2737 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.3145 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.3145 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46672.0448 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1947 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1947 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.5402 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6103 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 22.7965 | PASS | 1.6869 | PASS | 1586.9067 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 22.7965 | PASS | 1.6869 | PASS | 1586.9067 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 21.1114 | PASS | 2.9859 | PASS | 2885.8687 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 24.8217 | PASS | 6.0597 | PASS | 5959.6673 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 24.8217 | PASS | 1.7195 | PASS | 1619.4813 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 39.2666 | PASS | 14.7198 | PASS | 14619.8188 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 14.0655 | PASS | 5.3783 | PASS | 5278.2844 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 23.5502 | PASS | 5.4502 | PASS | 5350.1606 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9323 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543016 [GLADSTN5 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9323 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 138.7675 | PASS | 13.8556 | PASS | 13755.5777 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.1534 | PASS | 9.8387 | PASS | 9738.6521 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.6249 | PASS | 11.0861 | PASS | 10986.1019 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 20.5234 | PASS | 11.8797 | PASS | 11779.6939 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 5.7915 | FAIL | 23.2075 | PASS | 23107.4711 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 5.7915 | FAIL | 23.2075 | PASS | 23107.4711 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 5.7915 | FAIL | 47.8726 | PASS | 47772.6062 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 11.0054 | PASS | 36.5446 | PASS | 36444.5924 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 11.0054 | PASS | 36.5446 | PASS | 36444.5924 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.4304 | PASS | 0.3067 | PASS | 206.75 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 15.5237 | PASS | 5.0422 | PASS | 4942.2186 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 26.0231 | PASS | 1.6863 | PASS | 1586.3111 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 26.0231 | PASS | 1.6863 | PASS | 1586.3111 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.1067 | PASS | 2.9842 | PASS | 2884.1654 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 24.8204 | PASS | 6.0591 | PASS | 5959.1158 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 24.8204 | PASS | 1.7195 | PASS | 1619.5182 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 40.8943 | PASS | 14.7185 | PASS | 14618.4856 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 23.9731 | PASS | 5.4599 | PASS | 5359.9038 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 23.5535 | PASS | 5.451 | PASS | 5350.9501 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 9.4764 | PASS | 0.2604 | PASS | 160.4391 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 9.4764 | PASS | 0.2489 | PASS | 148.9308 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.3084 | PASS | 11.718 | PASS | 11618.0288 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 547469 [RIV4525 161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.3084 | PASS | 11.718 | PASS | 11618.0288 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 139.1209 | PASS | 13.8713 | PASS | 13771.2975 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8962 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 27.2804 | PASS | 11.0768 | PASS | 10976.7617 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2785 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2796 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2796 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46672.0322 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1722 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1722 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.5431 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6413 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 26.0224 | PASS | 1.6864 | PASS | 1586.3791 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 26.0224 | PASS | 1.6864 | PASS | 1586.3791 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7907 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 24.8215 | PASS | 6.0597 | PASS | 5959.712 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 24.8215 | PASS | 1.7195 | PASS | 1619.4783 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 40.8909 | PASS | 14.7191 | PASS | 14619.0839 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 23.9721 | PASS | 5.46 | PASS | 5359.9576 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 23.2024 | PASS | 5.4645 | PASS | 5364.5144 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 12.3284 | PASS | 11.727 | PASS | 11626.9543 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 1 | 12.3284 | PASS | 11.727 | PASS | 11626.9543 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 139.121 | PASS | 13.8713 | PASS | 13771.299 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 14.1777 | PASS | 9.8589 | PASS | 9758.8972 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 27.2804 | PASS | 11.0768 | PASS | 10976.7627 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 20.5347 | PASS | 11.8823 | PASS | 11782.2782 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 6.0206 | PASS | 23.2123 | PASS | 23112.2792 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 6.0206 | PASS | 23.2123 | PASS | 23112.2792 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 6.0206 | PASS | 46.772 | PASS | 46672.0345 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.1728 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.1728 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 13.5933 | PASS | 0.3025 | PASS | 202.5428 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 15.5267 | PASS | 5.0446 | PASS | 4944.6419 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 26.0222 | PASS | 1.6864 | PASS | 1586.3694 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 26.0222 | PASS | 1.6864 | PASS | 1586.3694 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 21.1112 | PASS | 2.9858 | PASS | 2885.7917 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 24.8215 | PASS | 6.0597 | PASS | 5959.702 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 24.8215 | PASS | 1.7195 | PASS | 1619.479 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 40.8905 | PASS | 14.719 | PASS | 14619.0495 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 23.9719 | PASS | 5.4599 | PASS | 5359.8856 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 23.1896 | PASS | 5.465 | PASS | 5364.9536 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 9.488 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 12.3284 | PASS | 11.727 | PASS | 11626.9561 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 548806 [BLUVLY 69.000] TO BUS 548807 [BLUVLY-161 161.00] CKT 2 | 12.3284 | PASS | 11.727 | PASS | 11626.9561 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 139.1218 | PASS | 13.8714 | PASS | 13771.3848 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 14.1778 | PASS | 9.8589 | PASS | 9758.9346 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 27.2807 | PASS | 11.0768 | PASS | 10976.819 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.3079 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.3424 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.3424 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 6.0206 | PASS | 46.7722 | PASS | 46672.1608 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.203 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.203 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 13.5934 | PASS | 0.3025 | PASS | 202.5289 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 15.5267 | PASS | 5.0447 | PASS | 4944.7003 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 26.0294 | PASS | 1.6868 | PASS | 1586.7645 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 26.0294 | PASS | 1.6868 | PASS | 1586.7645 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 21.1113 | PASS | 2.9859 | PASS | 2885.8515 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 24.8158 | PASS | 6.0594 | PASS | 5959.3578 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 24.8158 | PASS | 1.7195 | PASS | 1619.501 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 40.8313 | PASS | 14.7177 | PASS | 14617.6726 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 23.9698 | PASS | 5.4655 | PASS | 5365.4742 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 17.1747 | PASS | 5.4134 | PASS | 5313.4091 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 9.4881 | PASS | 0.2604 | PASS | 160.4436 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 9.4881 | PASS | 0.2489 | PASS | 148.9368 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 12.3285 | PASS | 11.727 | PASS | 11627.0127 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 548814 [SUB M-161 161.00] CKT 1 | 12.3285 | PASS | 11.727 | PASS | 11627.0127 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 139.1689 | PASS | 13.8762 | PASS | 13776.2134 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 14.1833 | PASS | 9.8615 | PASS | 9761.497 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 27.2912 | PASS | 11.0798 | PASS | 10979.8069 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 20.5354 | PASS | 11.8826 | PASS | 11782.5943 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 6.0221 | PASS | 23.2152 | PASS | 23115.156 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 6.0221 | PASS | 23.2152 | PASS | 23115.156 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 6.0221 | PASS | 46.7782 | PASS | 46678.2226 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 11.0066 | PASS | 36.5458 | PASS | 36445.8087 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 11.0066 | PASS | 36.5458 | PASS | 36445.8087 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 13.5976 | PASS | 0.3019 | PASS | 201.9391 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 15.5279 | PASS | 5.0466 | PASS | 4946.5865 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 26.0213 | PASS | 1.6853 | PASS | 1585.3317 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 26.0213 | PASS | 1.6853 | PASS | 1585.3317 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 21.1115 | PASS | 2.9862 | PASS | 2886.2122 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 24.8161 | PASS | 6.057 | PASS | 5956.9883 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 24.8161 | PASS | 1.7197 | PASS | 1619.66 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 40.8834 | PASS | 14.7129 | PASS | 14612.8514 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 23.9672 | PASS | 5.4519 | PASS | 5351.9474 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 23.5454 | PASS | 5.4698 | PASS | 5369.7561 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 9.4911 | PASS | 0.2604 | PASS | 160.4467 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 9.4911 | PASS | 0.2489 | PASS | 148.9409 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 12.3326 | PASS | 11.7301 | PASS | 11630.0992 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 548807 [BLUVLY-161 161.00] TO BUS 762669 [GEN-2018-031161.00] CKT 1 | 12.3326 | PASS | 11.7301 | PASS | 11630.0992 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 139.0886 | PASS | 13.8717 | PASS | 13771.6608 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 14.1784 | PASS | 9.8593 | PASS | 9759.2739 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 27.2815 | PASS | 11.0771 | PASS | 10977.1101 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 20.534 | PASS | 11.8823 | PASS | 11782.2842 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 6.0207 | PASS | 23.2126 | PASS | 23112.6189 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 6.0207 | PASS | 23.2126 | PASS | 23112.6189 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 6.0207 | PASS | 46.7728 | PASS | 46672.8031 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 6.9654 | PASS | 45.1985 | PASS | 45098.5433 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 6.9654 | PASS | 45.1985 | PASS | 45098.5433 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 13.5931 | PASS | 0.3025 | PASS | 202.532 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 15.4458 | PASS | 5.0407 | PASS | 4940.6814 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 26.0271 | PASS | 1.6865 | PASS | 1586.5034 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 26.0271 | PASS | 1.6865 | PASS | 1586.5034 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 21.0083 | PASS | 2.979 | PASS | 2878.9795 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9522 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4623 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 40.8995 | PASS | 14.7194 | PASS | 14619.4361 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 23.976 | PASS | 5.4612 | PASS | 5361.1766 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 23.5565 | PASS | 5.4522 | PASS | 5352.1977 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 9.4861 | PASS | 0.2604 | PASS | 160.4441 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 9.4861 | PASS | 24.89% | PASS | 148.9375 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 12.3263 | PASS | 11.727 | PASS | 11627.0261 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 640183 [GENTLMN3 345.00] TO BUS 640325 [REDWILO3 345.00] CKT 1 | 12.3263 | PASS | 1173% | PASS | 11627.0261 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 139.1165 | PASS | 13.872 | PASS | 13772.0034 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 14.1789 | PASS | 9.8595 | PASS | 9759.4741 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 27.2824 | PASS | 11.0773 | PASS | 10977.3302 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 20.5345 | PASS | 11.8823 | PASS | 11782.2896 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 6.0209 | PASS | 23.2128 | PASS | 23112.8266 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 6.0209 | PASS | 23.2128 | PASS | 23112.8266 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 6.0209 | PASS | 46.7731 | PASS | 46673.1363 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 10.0192 | PASS | 36.1748 | PASS | 36074.8141 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 10.0192 | PASS | 36.1748 | PASS | 36074.8141 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 13.5935 | PASS | 0.3025 | PASS | 202.4964 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 15.5053 | PASS | 5.0398 | PASS | 4939.7636 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 26.0265 | PASS | 1.6864 | PASS | 1586.4471 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 26.0265 | PASS | 1.6864 | PASS | 1586.4471 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 21.0631 | PASS | 2.9736 | PASS | 2873.6039 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 24.8222 | PASS | 6.0599 | PASS | 5959.8962 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 24.8222 | PASS | 1.7195 | PASS | 1619.4661 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 40.8987 | PASS | 14.7192 | PASS | 14619.2072 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 23.9756 | PASS | 5.4609 | PASS | 5360.8849 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 23.5562 | PASS | 5.4519 | PASS | 5351.9474 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 9.4882 | PASS | 0.2604 | PASS | 160.4444 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 9.4882 | PASS | 0.2489 | PASS | 148.9378 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 12.3281 | PASS | 11.7272 | PASS | 11627.2268 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 640325 [REDWILO3 345.00] TO BUS 640326 [REDWILO7 115.00] TO BUS 640327 [REDWILO9 13.800] CKT 1 | 12.3281 | PASS | 11.7272 | PASS | 11627.2268 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 139.1888 | PASS | 13.8778 | PASS | 13777.8116 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 14.1815 | PASS | 9.8607 | PASS | 9760.6654 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 27.2898 | PASS | 11.0794 | PASS | 10979.4214 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 20.5353 | PASS | 11.8826 | PASS | 11782.5547 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 6.0219 | PASS | 23.2147 | PASS | 23114.674 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 6.0219 | PASS | 23.2147 | PASS | 23114.674 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 6.0219 | PASS | 46.7769 | PASS | 46676.8832 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 11.015 | PASS | 36.5579 | PASS | 36457.9357 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 11.015 | PASS | 36.5579 | PASS | 36457.9357 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 13.6002 | PASS | 0.3016 | PASS | 201.5836 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 15.4025 | PASS | 4.8835 | PASS | 4783.5371 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 26.0286 | PASS | 1.6867 | PASS | 1586.6739 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 26.0286 | PASS | 1.6867 | PASS | 1586.6739 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 21.1395 | PASS | 3.0015 | PASS | 2901.5299 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 24.8194 | PASS | 6.0587 | PASS | 5958.674 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 24.8194 | PASS | 1.7195 | PASS | 1619.5474 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 40.9018 | PASS | 14.7201 | PASS | 14620.141 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 23.9772 | PASS | 5.4621 | PASS | 5362.1292 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 23.5571 | PASS | 5.4526 | PASS | 5352.6366 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 9.489 | PASS | 0.2604 | PASS | 160.4449 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 9.489 | PASS | 0.2489 | PASS | 148.9385 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 12.3363 | PASS | 11.7326 | PASS | 11632.5904 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 763846 [G19-053/055 230.00] TO BUS 763850 [G19-055-TAP 230.00] CKT 1 | 12.3363 | PASS | 11.7326 | PASS | 11632.5904 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 139.1532 | PASS | 13.8747 | PASS | 13774.7318 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 14.1728 | PASS | 9.8571 | PASS | 9757.1465 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 27.2332 | PASS | 11.0654 | PASS | 10965.3993 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 20.5359 | PASS | 11.8828 | PASS | 11782.8324 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 6.0176 | PASS | 23.2073 | PASS | 23107.332 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 6.0176 | PASS | 23.2073 | PASS | 23107.332 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 6.0176 | PASS | 46.8818 | PASS | 46781.7902 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 11.0071 | PASS | 36.5465 | PASS | 36446.4952 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 11.0071 | PASS | 36.5465 | PASS | 36446.4952 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 13.5912 | PASS | 0.3028 | PASS | 202.8035 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 15.5275 | PASS | 5.0458 | PASS | 4945.8223 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 26.0299 | PASS | 1.6868 | PASS | 1586.8224 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 26.0299 | PASS | 1.6868 | PASS | 1586.8224 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 21.1156 | PASS | 2.9885 | PASS | 2888.482 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 24.819 | PASS | 6.0585 | PASS | 5958.5146 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 24.819 | PASS | 1.7196 | PASS | 1619.5582 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 40.904 | PASS | 14.7208 | PASS | 14620.8061 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 23.9782 | PASS | 5.4629 | PASS | 5362.8901 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 23.5585 | PASS | 5.4537 | PASS | 5353.6954 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 9.4885 | PASS | 0.2604 | PASS | 160.4443 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 9.4885 | PASS | 0.2489 | PASS | 148.9378 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.331 | PASS | 11.729 | PASS | 11628.9829 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 764300 [GEN-2020-079161.00] TO BUS 764310 [G20-079-TAP 161.00] CKT 1 | 12.331 | PASS | 11.729 | PASS | 11628.9829 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 139.2337 | PASS | 13.8827 | PASS | 13782.7046 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 14.194 | PASS | 9.8661 | PASS | 9766.0521 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 27.3114 | PASS | 11.0846 | PASS | 10984.6235 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 20.5363 | PASS | 11.8831 | PASS | 11783.0565 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 6.0258 | PASS | 23.2209 | PASS | 23120.8615 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 6.0258 | PASS | 23.2209 | PASS | 23120.8615 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 6.0258 | PASS | 46.8463 | PASS | 46746.2724 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 11.0076 | PASS | 36.5472 | PASS | 36447.2497 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 11.0076 | PASS | 36.5472 | PASS | 36447.2497 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 13.6525 | PASS | 0.3006 | PASS | 200.5633 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 15.5285 | PASS | 5.0474 | PASS | 4947.4415 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 26.0308 | PASS | 1.6869 | PASS | 1586.9323 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 26.0308 | PASS | 1.6869 | PASS | 1586.9323 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 21.117 | PASS | 2.9896 | PASS | 2889.5584 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 24.8198 | PASS | 6.0589 | PASS | 5958.8563 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 24.8198 | PASS | 1.7195 | PASS | 1619.5352 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 40.9057 | PASS | 14.7213 | PASS | 14621.3085 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 23.9791 | PASS | 5.4636 | PASS | 5363.5834 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 23.5594 | PASS | 5.4543 | PASS | 5354.3475 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 9.4908 | PASS | 0.2604 | PASS | 160.4473 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 9.4908 | PASS | 0.2489 | PASS | 148.9416 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 12.3369 | PASS | 11.7335 | PASS | 11633.471 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 765190 [GEN-2020-090345.00] TO BUS 765193 [G20-090-XFM134.500] CKT 1 | 12.3369 | PASS | 11.7335 | PASS | 11633.471 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 139.1234 | PASS | 13.8715 | PASS | 13771.5415 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 14.1778 | PASS | 9.859 | PASS | 9758.9737 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 27.2805 | PASS | 11.0769 | PASS | 10976.8974 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2631 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.4203 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.4203 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 6.0206 | PASS | 46.7721 | PASS | 46672.1308 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1691 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1691 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.488 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 15.5268 | PASS | 5.0448 | PASS | 4944.754 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 25.9298 | PASS | 1.6855 | PASS | 1585.5364 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 25.9298 | PASS | 1.6855 | PASS | 1585.5364 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 21.111 | PASS | 2.9857 | PASS | 2885.6785 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 24.7999 | PASS | 6.0576 | PASS | 5957.6285 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 24.7999 | PASS | 1.7196 | PASS | 1619.6138 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 40.689 | PASS | 14.7113 | PASS | 14611.2658 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 23.9225 | PASS | 5.4548 | PASS | 5354.7862 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 22.9009 | PASS | 5.4201 | PASS | 5320.1058 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 9.4882 | PASS | 0.2604 | PASS | 160.4437 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 9.4882 | PASS | 0.2489 | PASS | 148.937 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 12.3287 | PASS | 11.7271 | PASS | 11627.1258 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300320 [5LEVASY 161.00] TO BUS 300110 [5PITTSV 161.00] CKT 1 | 12.3287 | PASS | 11.7271 | PASS | 11627.1258 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 138.3315 | PASS | 13.8154 | PASS | 13715.4406 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 14.0563 | PASS | 9.8494 | PASS | 9749.364 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 26.6832 | PASS | 11.0519 | PASS | 10951.8778 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 20.5295 | PASS | 11.8804 | PASS | 11780.383 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 5.8964 | FAIL | 23.1791 | PASS | 23079.0628 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 5.8964 | FAIL | 23.1791 | PASS | 23079.0628 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 5.8964 | FAIL | 47.4343 | PASS | 47334.3223 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 11.0036 | PASS | 36.5424 | PASS | 36442.3796 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 11.0036 | PASS | 36.5424 | PASS | 36442.3796 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 6.9019 | PASS | 0.3166 | PASS | 216.5925 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 15.5193 | PASS | 5.0376 | PASS | 4937.6349 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 26.0193 | PASS | 1.6856 | PASS | 1585.5955 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 26.0193 | PASS | 1.6856 | PASS | 1585.5955 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.0965 | PASS | 2.9789 | PASS | 2878.8759 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 24.8182 | PASS | 6.0583 | PASS | 5958.3233 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 24.8182 | PASS | 1.7196 | PASS | 1619.5709 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 40.886 | PASS | 14.7153 | PASS | 14615.2519 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 23.9688 | PASS | 5.4554 | PASS | 5355.3574 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 23.5497 | PASS | 5.447 | PASS | 5347.0255 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 9.4654 | PASS | 0.2604 | PASS | 160.4287 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 9.4654 | PASS | 0.2489 | PASS | 148.9173 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.2787 | PASS | 11.6969 | PASS | 11596.9259 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300739 [7BLACKBERRY 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.2787 | PASS | 11.6969 | PASS | 11596.9259 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 139.1172 | PASS | 13.8713 | PASS | 13771.3253 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 14.1751 | PASS | 9.8586 | PASS | 9758.6121 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 27.27 | PASS | 11.0762 | PASS | 10976.2393 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2847 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 6.0185 | PASS | 23.2114 | PASS | 23111.4321 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 6.0185 | PASS | 23.2114 | PASS | 23111.4321 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 6.0185 | PASS | 46.7783 | PASS | 46678.291 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1824 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1824 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 13.5823 | PASS | 0.3029 | PASS | 202.8954 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 15.5267 | PASS | 5.0447 | PASS | 4944.6646 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6249 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6249 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7791 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9455 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4628 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9324 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.8096 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7244 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.3283 | PASS | 11.727 | PASS | 11626.9831 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 1 | 12.3283 | PASS | 11.727 | PASS | 11626.9831 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 139.1172 | PASS | 13.8713 | PASS | 13771.3251 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 14.1751 | PASS | 9.8586 | PASS | 9758.6123 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 27.27 | PASS | 11.0762 | PASS | 10976.2387 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 20.5346 | PASS | 11.8823 | PASS | 11782.2847 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 6.0185 | PASS | 23.2114 | PASS | 23111.4316 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 6.0185 | PASS | 23.2114 | PASS | 23111.4316 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 6.0185 | PASS | 46.7783 | PASS | 46678.2981 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.1824 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.1824 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 13.5823 | PASS | 0.3029 | PASS | 202.8955 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 15.5267 | PASS | 5.0447 | PASS | 4944.6646 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 26.0281 | PASS | 1.6866 | PASS | 1586.6248 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 26.0281 | PASS | 1.6866 | PASS | 1586.6248 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 21.1112 | PASS | 2.9858 | PASS | 2885.7791 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 24.8223 | PASS | 6.0599 | PASS | 5959.9454 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 24.8223 | PASS | 1.7195 | PASS | 1619.4628 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 40.9011 | PASS | 14.7199 | PASS | 14619.9324 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 23.9768 | PASS | 5.4618 | PASS | 5361.8096 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 23.5572 | PASS | 5.4527 | PASS | 5352.7243 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 9.4879 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.3283 | PASS | 11.727 | PASS | 11626.983 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 300741 [5SPORTSMAN 161.00] CKT 2 | 12.3283 | PASS | 11.727 | PASS | 11626.983 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 138.8897 | PASS | 13.8507 | PASS | 13750.6885 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 14.1268 | PASS | 9.8489 | PASS | 9748.8769 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 27.1227 | PASS | 11.0714 | PASS | 10971.3573 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 20.5307 | PASS | 11.8807 | PASS | 11780.6807 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 5.9914 | FAIL | 23.2152 | PASS | 23115.1857 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 5.9914 | FAIL | 23.2152 | PASS | 23115.1857 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 5.9914 | FAIL | 46.83 | PASS | 46730.0274 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 11.0056 | PASS | 36.5447 | PASS | 36444.6572 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 11.0056 | PASS | 36.5447 | PASS | 36444.6572 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 13.4447 | PASS | 0.2983 | PASS | 198.2718 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 15.5235 | PASS | 5.0407 | PASS | 4940.6703 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 26.0263 | PASS | 1.6865 | PASS | 1586.4779 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 26.0263 | PASS | 1.6865 | PASS | 1586.4779 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 21.1104 | PASS | 2.9854 | PASS | 2885.3582 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 24.822 | PASS | 6.0599 | PASS | 5959.8627 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 24.822 | PASS | 1.7195 | PASS | 1619.4682 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 40.8983 | PASS | 14.7192 | PASS | 14619.2445 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 23.9754 | PASS | 5.461 | PASS | 5360.9589 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 23.5554 | PASS | 5.4517 | PASS | 5351.7321 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 9.4791 | PASS | 0.2604 | PASS | 160.4351 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 9.4791 | PASS | 0.2489 | PASS | 148.9257 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.3115 | PASS | 11.7148 | PASS | 11614.846 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300740 [7SPORTSMAN 345.00] TO BUS 512650 [GRDA1 7 345.00] CKT 1 | 12.3115 | PASS | 11.7148 | PASS | 11614.846 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 139.0852 | PASS | 13.871 | PASS | 13770.9731 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 14.1563 | PASS | 9.858 | PASS | 9757.9587 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 27.1884 | PASS | 11.0758 | PASS | 10975.849 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 20.5345 | PASS | 1188% | PASS | 11782.2492 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 5.9976 | FAIL | 23.2117 | PASS | 23111.7264 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 5.9976 | FAIL | 2321% | PASS | 23111.7264 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 5.9976 | FAIL | 46.7557 | PASS | 46655.7394 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.036 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.036 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 13.4481 | PASS | 0.3029 | PASS | 202.9056 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 15.5266 | PASS | 5.0448 | PASS | 4944.8111 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 26.0256 | PASS | 1.6865 | PASS | 1586.5442 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 26.0256 | PASS | 1.6865 | PASS | 1586.5442 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 21.1102 | PASS | 2.9853 | PASS | 2885.3066 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 24.8161 | PASS | 6.0597 | PASS | 5959.6709 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 24.8161 | PASS | 1.7195 | PASS | 1619.4801 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 40.8975 | PASS | 14.7196 | PASS | 14619.6038 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 23.9751 | PASS | 5.4612 | PASS | 5361.2308 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 23.5534 | PASS | 5.4525 | PASS | 5352.5009 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4443 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9377 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 12.3269 | PASS | 11.7269 | PASS | 11626.8843 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 300950 [5JASPER 161.00] CKT 1 | 12.3269 | PASS | 11.7269 | PASS | 11626.8843 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 138.7141 | PASS | 13.8564 | PASS | 13756.4238 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 13.9704 | PASS | 9.8443 | PASS | 9744.2981 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 26.4365 | PASS | 11.0615 | PASS | 10961.5179 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 20.5275 | PASS | 11.881 | PASS | 11780.9792 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 5.8447 | FAIL | 23.2051 | PASS | 23105.0886 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 5.8447 | FAIL | 23.2051 | PASS | 23105.0886 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 5.8447 | FAIL | 47.3255 | PASS | 47225.5406 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 11.0041 | PASS | 36.5425 | PASS | 36442.5269 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 11.0041 | PASS | 36.5425 | PASS | 36442.5269 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 12.6374 | PASS | 0.3034 | PASS | 203.3789 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 15.5235 | PASS | 5.0424 | PASS | 4942.3759 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 26.0201 | PASS | 1.6858 | PASS | 1585.8377 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 26.0201 | PASS | 1.6858 | PASS | 1585.8377 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 21.0983 | PASS | 2.9794 | PASS | 2879.3645 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 24.8144 | PASS | 6.0574 | PASS | 5957.4253 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 24.8144 | PASS | 1.7196 | PASS | 1619.6306 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 40.8881 | PASS | 14.7162 | PASS | 14616.2045 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 23.9702 | PASS | 5.4571 | PASS | 5357.0715 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 23.5507 | PASS | 5.448 | PASS | 5348.0358 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 9.4773 | PASS | 0.2604 | PASS | 160.443 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 9.4773 | PASS | 0.2489 | PASS | 148.9358 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 12.3067 | PASS | 11.7189 | PASS | 11618.9411 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 300949 [7JASPER 345.00] TO BUS 709500 [GI-95_POI 345.00] CKT 1 | 12.3067 | PASS | 11.7189 | PASS | 11618.9411 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 139.1195 | PASS | 13.8712 | PASS | 13771.1829 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 14.1773 | PASS | 9.8588 | PASS | 9758.7851 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 27.2794 | PASS | 11.0766 | PASS | 10976.6345 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 20.5345 | PASS | 11.8823 | PASS | 11782.2658 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 6.0204 | PASS | 23.2122 | PASS | 23112.1628 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 6.0204 | PASS | 23.2122 | PASS | 23112.1628 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 6.0204 | PASS | 46.7727 | PASS | 46672.7069 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.0421 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.0421 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 13.5928 | PASS | 0.3026 | PASS | 202.5636 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 15.5266 | PASS | 5.0446 | PASS | 4944.5776 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 25.991 | PASS | 1.6867 | PASS | 1586.7036 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 25.991 | PASS | 1.6867 | PASS | 1586.7036 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 21.1106 | PASS | 2.9854 | PASS | 2885.388 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 24.8175 | PASS | 6.0604 | PASS | 5960.3946 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 24.8175 | PASS | 1.7194 | PASS | 1619.4315 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 40.8084 | PASS | 14.7206 | PASS | 14620.633 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 23.9473 | PASS | 5.4622 | PASS | 5362.2301 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 23.1892 | PASS | 5.4527 | PASS | 5352.7272 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.9006 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300091 [5LATHRP 161.00] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.9006 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 139.1206 | PASS | 13.8713 | PASS | 13771.2646 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8758 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7378 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2952 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2597 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2597 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 6.0206 | PASS | 46.772 | PASS | 46671.9738 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1798 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1798 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 13.5932 | PASS | 0.3026 | PASS | 202.5502 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6396 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 26.0236 | PASS | 1.6866 | PASS | 1586.6416 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 26.0236 | PASS | 1.6866 | PASS | 1586.6416 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 21.1113 | PASS | 2.9858 | PASS | 2885.8221 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 24.8225 | PASS | 6.06 | PASS | 5960.0379 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 24.8225 | PASS | 1.7195 | PASS | 1619.4566 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 40.7841 | PASS | 14.7172 | PASS | 14617.2376 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 23.9764 | PASS | 5.4645 | PASS | 5364.5393 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 22.8522 | PASS | 5.4359 | PASS | 5335.8642 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 9.488 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9334 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300098 [5MOCITYB2 161.00] CKT Z1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9334 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 139.1204 | PASS | 13.8712 | PASS | 13771.2385 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8543 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 27.2803 | PASS | 11.0767 | PASS | 10976.7129 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2772 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.238 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.238 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 6.0206 | PASS | 46.7719 | PASS | 46671.9171 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1388 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1388 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5524 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.616 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 26.0246 | PASS | 1.6864 | PASS | 1586.3632 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 26.0246 | PASS | 1.6864 | PASS | 1586.3632 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 21.1111 | PASS | 2.9857 | PASS | 2885.7007 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 24.8229 | PASS | 6.0604 | PASS | 5960.3836 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 24.8229 | PASS | 1.7194 | PASS | 1619.4334 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 40.9009 | PASS | 14.7198 | PASS | 14619.8471 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 23.9763 | PASS | 5.4613 | PASS | 5361.2854 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 23.5371 | PASS | 5.4565 | PASS | 5356.5367 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.921 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.921 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 139.1204 | PASS | 13.8712 | PASS | 13771.2385 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 14.1776 | PASS | 9.8589 | PASS | 9758.8544 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 27.2803 | PASS | 11.0767 | PASS | 10976.713 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 20.5347 | PASS | 11.8823 | PASS | 11782.2773 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 6.0206 | PASS | 23.2122 | PASS | 23112.2381 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 6.0206 | PASS | 23.2122 | PASS | 23112.2381 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 6.0206 | PASS | 46.7719 | PASS | 46671.9173 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 11.0061 | PASS | 36.5451 | PASS | 36445.139 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 11.0061 | PASS | 36.5451 | PASS | 36445.139 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 13.5932 | PASS | 0.3026 | PASS | 202.5524 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 15.5267 | PASS | 5.0446 | PASS | 4944.6161 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 26.0246 | PASS | 1.6864 | PASS | 1586.365 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 26.0246 | PASS | 1.6864 | PASS | 1586.365 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 21.1111 | PASS | 2.9857 | PASS | 2885.7011 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 24.8229 | PASS | 6.0604 | PASS | 5960.3804 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 24.8229 | PASS | 1.7194 | PASS | 1619.4336 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 40.9009 | PASS | 14.7198 | PASS | 14619.847 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 23.9763 | PASS | 5.4613 | PASS | 5361.2891 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 23.5372 | PASS | 5.4565 | PASS | 5356.5073 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 12.3284 | PASS | 11.7269 | PASS | 11626.9211 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 301563 [5MOCITYB1 161.00] TO BUS 300304 [2MOCITY 69.000] CKT 2 | 12.3284 | PASS | 11.7269 | PASS | 11626.9211 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 139.1141 | PASS | 13.8706 | PASS | 13770.6022 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 14.1767 | PASS | 9.8584 | PASS | 9758.4499 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 27.2779 | PASS | 11.0761 | PASS | 10976.0879 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 20.5346 | PASS | 11.8822 | PASS | 11782.2447 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 6.0202 | PASS | 23.2116 | PASS | 23111.5631 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 6.0202 | PASS | 23.2116 | PASS | 23111.5631 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 6.0202 | PASS | 46.7713 | PASS | 46671.2559 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 11.0062 | PASS | 36.5452 | PASS | 36445.1574 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 11.0062 | PASS | 36.5452 | PASS | 36445.1574 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 13.5915 | PASS | 0.3028 | PASS | 202.7544 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 15.5265 | PASS | 5.0444 | PASS | 4944.3658 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 26.0262 | PASS | 1.6867 | PASS | 1586.7039 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 26.0262 | PASS | 1.6867 | PASS | 1586.7039 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 21.1116 | PASS | 2.9859 | PASS | 2885.9387 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 24.5151 | PASS | 6.058 | PASS | 5957.9989 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 24.5151 | PASS | 1.7194 | PASS | 1619.4455 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 40.8997 | PASS | 14.7204 | PASS | 14620.4022 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 23.9761 | PASS | 5.4623 | PASS | 5362.3044 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 23.5562 | PASS | 5.4535 | PASS | 5353.5051 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 9.4875 | PASS | 0.2604 | PASS | 160.443 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 9.4875 | PASS | 0.2489 | PASS | 148.936 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 12.3278 | PASS | 11.7265 | PASS | 11626.4963 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 344234 [5CALIF UE 2 161.00] CKT Z | 12.3278 | PASS | 11.7265 | PASS | 11626.4963 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 139.1205 | PASS | 13.8713 | PASS | 13771.2533 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8694 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7292 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2826 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2503 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2503 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46671.9642 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1636 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1636 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5508 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6259 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6237 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6237 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7678 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 24.8218 | PASS | 6.0597 | PASS | 5959.6551 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 24.8218 | PASS | 1.7195 | PASS | 1619.4822 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9247 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.8041 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7131 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9273 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 344233 [5CALIF UE 1 161.00] TO BUS 346027 [1CALIF 34.500] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9273 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 139.1205 | PASS | 13.8713 | PASS | 13771.2589 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8904 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 27.2803 | PASS | 11.0768 | PASS | 10976.7695 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2882 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.3077 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.3077 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 6.0206 | PASS | 46.7724 | PASS | 46672.3812 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 11.0062 | PASS | 36.5451 | PASS | 36445.1491 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 11.0062 | PASS | 36.5451 | PASS | 36445.1491 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 13.5932 | PASS | 0.3025 | PASS | 202.5333 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6262 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 26.0281 | PASS | 1.6868 | PASS | 1586.7709 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 26.0281 | PASS | 1.6868 | PASS | 1586.7709 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 21.1111 | PASS | 2.9857 | PASS | 2885.7259 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 24.6434 | PASS | 6.0813 | PASS | 5981.3314 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 24.6434 | PASS | 1.7179 | PASS | 1617.9478 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 40.9024 | PASS | 14.7208 | PASS | 14620.8112 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 23.9773 | PASS | 5.4627 | PASS | 5362.7174 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 23.5577 | PASS | 5.4542 | PASS | 5354.1779 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9321 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 301489 [5MCBAINB2 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9321 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 139.1189 | PASS | 13.8711 | PASS | 13771.0903 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 14.1774 | PASS | 9.8588 | PASS | 9758.7729 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 27.2799 | PASS | 11.0766 | PASS | 10976.5982 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2703 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.121 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.121 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 6.0205 | PASS | 46.7718 | PASS | 46671.761 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 11.0062 | PASS | 36.5451 | PASS | 36445.1423 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 11.0062 | PASS | 36.5451 | PASS | 36445.1423 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 13.5929 | PASS | 30.26% | PASS | 202.5835 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 15.5266 | PASS | 5.0446 | PASS | 4944.5567 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 26.0258 | PASS | 168.7% | PASS | 1586.6151 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 26.0258 | PASS | 1.6866 | PASS | 1586.6151 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 21.1112 | PASS | 2.9857 | PASS | 2885.7478 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 24.6461 | PASS | 6.0568 | PASS | 5956.8462 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 24.6461 | PASS | 1.7196 | PASS | 1619.6013 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 40.8982 | PASS | 14.7199 | PASS | 14619.8851 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 23.9756 | PASS | 5.4618 | PASS | 5361.754 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 23.5545 | PASS | 5.4526 | PASS | 5352.631 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4433 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9365 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 12.3282 | PASS | 11.7268 | PASS | 11626.8226 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345071 [5MCBAIN T 161.00] TO BUS 344041 [5LOYMART 2 161.00] CKT 1 | 12.3282 | PASS | 11.7268 | PASS | 11626.8226 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 139.1198 | PASS | 13.8712 | PASS | 13771.1905 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.829 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 27.28 | PASS | 11.0767 | PASS | 10976.679 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2812 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2077 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2077 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 6.0205 | PASS | 46.772 | PASS | 46671.993 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1171 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1171 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5615 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 15.5266 | PASS | 5.0446 | PASS | 4944.5901 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 26.0271 | PASS | 1.6868 | PASS | 1586.7858 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 26.0271 | PASS | 1.6868 | PASS | 1586.7858 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 21.111 | PASS | 2.9856 | PASS | 2885.6421 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 24.652 | PASS | 6.0774 | PASS | 5977.3668 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 24.652 | PASS | 1.7182 | PASS | 1618.2138 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 40.9013 | PASS | 14.7209 | PASS | 14620.8975 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 23.9768 | PASS | 5.4628 | PASS | 5362.8187 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 23.5567 | PASS | 5.4543 | PASS | 5354.2898 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.8911 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 300500 [5HUNTSDL 161.00] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.8911 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 139.1203 | PASS | 13.8712 | PASS | 13771.2385 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8615 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 27.2801 | PASS | 11.0767 | PASS | 10976.7124 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2813 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2321 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2321 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 6.0205 | PASS | 46.7722 | PASS | 46672.1838 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1797 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1797 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5579 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6226 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 26.0269 | PASS | 1.6866 | PASS | 1586.5819 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 26.0269 | PASS | 1.6866 | PASS | 1586.5819 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 21.1113 | PASS | 2.9858 | PASS | 2885.8262 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 24.509 | PASS | 6.0568 | PASS | 5956.8041 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 24.509 | PASS | 1.7195 | PASS | 1619.5414 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 40.8993 | PASS | 14.7197 | PASS | 14619.6703 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 23.976 | PASS | 5.4615 | PASS | 5361.5354 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 23.5563 | PASS | 5.4522 | PASS | 5352.2489 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9152 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345221 [5MOBERLY 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9152 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 139.1108 | PASS | 13.8703 | PASS | 13770.2733 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 14.1763 | PASS | 9.8582 | PASS | 9758.217 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 27.2769 | PASS | 11.0757 | PASS | 10975.7098 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 20.5345 | PASS | 11.8823 | PASS | 11782.25 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 6.02 | PASS | 23.2111 | PASS | 23111.1279 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 6.02 | PASS | 23.2111 | PASS | 23111.1279 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 6.02 | PASS | 46.7696 | PASS | 46669.5748 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1034 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1034 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 13.5907 | PASS | 0.3029 | PASS | 202.9033 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 15.5264 | PASS | 5.0442 | PASS | 4944.2134 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 26.0236 | PASS | 1.6874 | PASS | 1587.4107 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 26.0236 | PASS | 1.6874 | PASS | 1587.4107 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 21.1115 | PASS | 2.9859 | PASS | 2885.8679 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 22.2636 | PASS | 5.9126 | PASS | 5812.6086 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 22.2636 | PASS | 1.7286 | PASS | 1628.6046 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 40.9032 | PASS | 14.7236 | PASS | 14623.628 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 23.977 | PASS | 5.4667 | PASS | 5366.6837 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 23.5598 | PASS | 5.4577 | PASS | 5357.6729 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 9.4871 | PASS | 0.2604 | PASS | 160.4427 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 9.4871 | PASS | 0.2489 | PASS | 148.9357 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 12.3275 | PASS | 11.7263 | PASS | 11626.2828 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345409 [5OVERTON 161.00] TO BUS 345408 [7OVERTON 345.00] CKT 1 | 12.3275 | PASS | 11.7263 | PASS | 11626.2828 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 139.1224 | PASS | 13.8714 | PASS | 13771.447 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 14.1778 | PASS | 9.859 | PASS | 9758.988 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 27.2804 | PASS | 11.0769 | PASS | 10976.8692 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.298 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.3792 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.3792 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 6.0206 | PASS | 46.7732 | PASS | 46673.2047 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2216 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2216 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 13.5932 | PASS | 0.3025 | PASS | 202.525 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 15.5267 | PASS | 5.0447 | PASS | 4944.7098 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 26.0245 | PASS | 1.6866 | PASS | 1586.5687 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 26.0245 | PASS | 1.6866 | PASS | 1586.5687 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 21.1114 | PASS | 2.9859 | PASS | 2885.8936 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 10.1418 | PASS | 5.9034 | PASS | 5803.3532 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 10.1418 | PASS | 1.7174 | PASS | 1617.4088 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 40.8907 | PASS | 14.7194 | PASS | 14619.3621 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 23.9748 | PASS | 5.4614 | PASS | 5361.442 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 23.5416 | PASS | 5.4515 | PASS | 5351.5257 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 9.4881 | PASS | 0.2604 | PASS | 160.4436 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 9.4881 | PASS | 0.2489 | PASS | 148.9368 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 12.3285 | PASS | 11.727 | PASS | 11627.0465 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 345411 [5OVERTON 2 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 12.3285 | PASS | 11.727 | PASS | 11627.0465 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 139.1398 | PASS | 13.8723 | PASS | 13772.3404 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 14.1789 | PASS | 9.8595 | PASS | 9759.4564 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 27.2834 | PASS | 11.0776 | PASS | 10977.5651 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 20.5347 | PASS | 11.8821 | PASS | 11782.1274 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 6.021 | PASS | 23.213 | PASS | 23112.9995 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 6.021 | PASS | 23.213 | PASS | 23112.9995 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 6.021 | PASS | 46.7741 | PASS | 46674.1041 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 11.0064 | PASS | 36.558 | PASS | 36458.0168 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 11.0064 | PASS | 36.558 | PASS | 36458.0168 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 13.5953 | PASS | 0.3023 | PASS | 202.2761 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 15.5179 | PASS | 5.0145 | PASS | 4914.4566 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6111 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6111 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 21.0944 | PASS | 2.9773 | PASS | 2877.3493 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 24.8216 | PASS | 6.0596 | PASS | 5959.6361 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 24.8216 | PASS | 1.7195 | PASS | 1619.4833 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.884 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7575 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 23.5571 | PASS | 5.4526 | PASS | 5352.595 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 9.4887 | PASS | 0.2604 | PASS | 160.4439 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 9.4887 | PASS | 0.2489 | PASS | 148.9371 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 12.3303 | PASS | 11.728 | PASS | 11627.9747 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530610 [SHAYS_230 230.00] CKT 1 | 12.3303 | PASS | 11.728 | PASS | 11627.9747 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 139.1131 | PASS | 13.8711 | PASS | 13771.1207 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.889 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7492 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 20.5345 | PASS | 11.8822 | PASS | 11782.2329 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2712 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2712 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46672.0017 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 11.0039 | PASS | 36.5497 | PASS | 36449.7059 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 11.0039 | PASS | 36.5497 | PASS | 36449.7059 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 13.5932 | PASS | 0.3025 | PASS | 202.55 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 15.4938 | PASS | 5.045 | PASS | 4945.0151 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6151 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6151 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 21.0953 | PASS | 2.9723 | PASS | 2872.2654 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9741 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4608 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.8949 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7611 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.6915 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 9.4876 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 9.4876 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 12.3279 | PASS | 11.7268 | PASS | 11626.8247 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530582 [S HAYS6 230.00] TO BUS 530553 [S HAYS 3 115.00] TO BUS 530632 [SHYS1 1 12.470] CKT 1 | 12.3279 | PASS | 11.7268 | PASS | 11626.8247 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 139.0022 | PASS | 13.8748 | PASS | 13774.8428 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 14.1834 | PASS | 9.8617 | PASS | 9761.7099 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 27.289 | PASS | 11.0795 | PASS | 10979.5166 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 20.5358 | PASS | 11.8829 | PASS | 11782.9223 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 6.0218 | PASS | 23.2149 | PASS | 23114.9131 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 6.0218 | PASS | 23.2149 | PASS | 23114.9131 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 6.0218 | PASS | 46.7774 | PASS | 46677.4073 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 10.9789 | PASS | 36.5217 | PASS | 36421.7015 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 10.9789 | PASS | 36.5217 | PASS | 36421.7015 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 13.5941 | PASS | 0.3023 | PASS | 202.2994 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 15.36 | PASS | 4.9998 | PASS | 4899.7505 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 26.0246 | PASS | 1.6862 | PASS | 1586.2428 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 26.0246 | PASS | 1.6862 | PASS | 1586.2428 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 10.3428 | PASS | 3.333 | PASS | 3233.0312 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 24.8219 | PASS | 6.0597 | PASS | 5959.7466 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 24.8219 | PASS | 1.7195 | PASS | 1619.476 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 40.8958 | PASS | 14.7183 | PASS | 14618.3348 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 23.9742 | PASS | 5.4598 | PASS | 5359.7946 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 23.5546 | PASS | 5.4508 | PASS | 5350.8224 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4495 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9445 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 12.3193 | PASS | 11.7281 | PASS | 11628.0865 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530583 [POSTROCK7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 12.3193 | PASS | 11.7281 | PASS | 11628.0865 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 139.1206 | PASS | 13.8712 | PASS | 13771.2499 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.871 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7312 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.281 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2529 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2529 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46671.9732 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 11.0062 | PASS | 36.5451 | PASS | 36445.1434 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 11.0062 | PASS | 36.5451 | PASS | 36445.1434 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5501 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 15.5262 | PASS | 5.0445 | PASS | 4944.5394 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6264 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6264 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 21.1041 | PASS | 2.9856 | PASS | 2885.6238 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9817 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9408 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8204 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7413 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9252 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530558 [KNOLL N 6 230.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9252 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 139.1484 | PASS | 13.8743 | PASS | 13774.315 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 14.1797 | PASS | 9.8598 | PASS | 9759.8328 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 27.285 | PASS | 11.0781 | PASS | 10978.0512 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 20.5349 | PASS | 11.8824 | PASS | 11782.4365 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 6.0212 | PASS | 23.2135 | PASS | 23113.4621 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 6.0212 | PASS | 23.2135 | PASS | 23113.4621 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 6.0212 | PASS | 46.7751 | PASS | 46675.0719 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 11.0077 | PASS | 36.567 | PASS | 36467.0233 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 11.0077 | PASS | 36.567 | PASS | 36467.0233 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 13.5961 | PASS | 0.3021 | PASS | 202.1399 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 15.5173 | PASS | 5.0443 | PASS | 4944.2822 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6129 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6129 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 21.0439 | PASS | 3.0339 | PASS | 2933.8572 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 24.8213 | PASS | 6.0595 | PASS | 5959.4732 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 24.8213 | PASS | 171.9% | PASS | 1619.4942 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.8893 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 23.9768 | PASS | 546.2% | PASS | 5361.775 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 23.557 | PASS | 5.4526 | PASS | 5352.5503 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 9.4886 | PASS | 0.2604 | PASS | 160.4451 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 9.4886 | PASS | 0.2489 | PASS | 148.9388 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 12.3316 | PASS | 11.7294 | PASS | 11629.3692 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530702 [BUCKEYE_230 230.00] CKT 1 | 12.3316 | PASS | 11.7294 | PASS | 11629.3692 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 139.1205 | PASS | 13.8712 | PASS | 13771.2497 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 14.1777 | PASS | 9.8589 | PASS | 9758.8709 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 27.2804 | PASS | 11.0767 | PASS | 10976.7311 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 20.5347 | PASS | 11.8823 | PASS | 11782.2813 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 6.0206 | PASS | 23.2123 | PASS | 23112.2528 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 6.0206 | PASS | 23.2123 | PASS | 23112.2528 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 6.0206 | PASS | 46.772 | PASS | 46671.9731 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 11.0062 | PASS | 36.5451 | PASS | 36445.1415 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 11.0062 | PASS | 36.5451 | PASS | 36445.1415 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 13.5932 | PASS | 0.3026 | PASS | 202.5501 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 15.5263 | PASS | 5.0445 | PASS | 4944.5353 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 26.0282 | PASS | 1.6866 | PASS | 1586.6264 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 26.0282 | PASS | 1.6866 | PASS | 1586.6264 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 21.1049 | PASS | 2.9856 | PASS | 2885.5957 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 24.8224 | PASS | 6.06 | PASS | 5959.9817 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 40.9012 | PASS | 14.7199 | PASS | 14619.9407 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 23.9769 | PASS | 5.4618 | PASS | 5361.8203 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 23.5573 | PASS | 5.4527 | PASS | 5352.7413 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 12.3284 | PASS | 11.7269 | PASS | 11626.9251 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530584 [POSTROCK6 230.00] TO BUS 530720 [KNOLL S 6 230.00] CKT 2 | 12.3284 | PASS | 11.7269 | PASS | 11626.9251 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 139.1167 | PASS | 13.8703 | PASS | 13770.3088 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.796 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 27.2802 | PASS | 11.0767 | PASS | 10976.6611 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 20.5345 | PASS | 11.8821 | PASS | 11782.1092 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1729 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1729 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 6.0205 | PASS | 46.7718 | PASS | 46671.8354 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 11.0044 | PASS | 36.5458 | PASS | 36445.842 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 11.0044 | PASS | 36.5458 | PASS | 36445.842 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5554 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 15.4341 | PASS | 5.0373 | PASS | 4937.3153 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6285 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6285 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 21.0738 | PASS | 2.9786 | PASS | 2878.6101 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9801 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 40.9012 | PASS | 14.72 | PASS | 14619.9507 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8311 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.754 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4427 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9357 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 12.3279 | PASS | 11.7263 | PASS | 11626.3235 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 530680 [HEIZER 6 230.00] TO BUS 530601 [HEIZER 3 115.00] TO BUS 530626 [HZRT1 1 12.500] CKT 1 | 12.3279 | PASS | 11.7263 | PASS | 11626.3235 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 139.1238 | PASS | 13.8711 | PASS | 13771.1149 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.9333 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 27.2807 | PASS | 11.0768 | PASS | 10976.827 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 20.5343 | PASS | 11.8822 | PASS | 11782.1706 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.3299 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.3299 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 6.0206 | PASS | 46.7722 | PASS | 46672.1757 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 10.8173 | PASS | 36.3273 | PASS | 36227.3438 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 10.8173 | PASS | 36.3273 | PASS | 36227.3438 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 13.5935 | PASS | 0.3025 | PASS | 202.5126 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 15.5216 | PASS | 5.0326 | PASS | 4932.5963 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 26.0284 | PASS | 1.6867 | PASS | 1586.6524 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 26.0284 | PASS | 1.6867 | PASS | 1586.6524 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 21.0919 | PASS | 2.9752 | PASS | 2875.1502 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9482 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4625 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 40.9015 | PASS | 14.72 | PASS | 14620.0479 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 23.977 | PASS | 5.462 | PASS | 5361.9566 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 23.5574 | PASS | 5.4528 | PASS | 5352.8402 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 9.4881 | PASS | 0.2604 | PASS | 160.4432 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 9.4881 | PASS | 0.2489 | PASS | 148.9363 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 12.3285 | PASS | 11.7269 | PASS | 11626.8925 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530555 [COLBY 3 115.00] CKT 1 | 12.3285 | PASS | 11.7269 | PASS | 11626.8925 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 139.1214 | PASS | 13.8711 | PASS | 13771.1132 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8786 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 27.2804 | PASS | 11.0768 | PASS | 10976.7524 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 20.5345 | PASS | 11.8822 | PASS | 11782.2254 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2651 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2651 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 6.0206 | PASS | 46.7721 | PASS | 46672.0563 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 10.8997 | PASS | 36.4531 | PASS | 36353.1166 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 10.8997 | PASS | 36.4531 | PASS | 36353.1166 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.536 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 15.514 | PASS | 5.0366 | PASS | 4936.5946 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6418 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6418 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 21.0958 | PASS | 2.9825 | PASS | 2882.5246 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9708 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.461 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 40.9014 | PASS | 14.72 | PASS | 14620.0053 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 23.977 | PASS | 5.4619 | PASS | 5361.9011 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.8036 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4432 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9363 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.8668 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 530559 [PH RUN 3 115.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.8668 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 139.1187 | PASS | 13.871 | PASS | 13770.9938 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.8256 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 27.2802 | PASS | 11.0767 | PASS | 10976.7054 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 20.5345 | PASS | 11.8822 | PASS | 11782.2281 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2243 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2243 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 6.0205 | PASS | 46.7719 | PASS | 46671.9223 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 10.951 | PASS | 36.4063 | PASS | 36306.3434 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 10.951 | PASS | 36.4063 | PASS | 36306.3434 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.5389 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 15.5261 | PASS | 5.0406 | PASS | 4940.5686 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6407 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6407 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 21.1113 | PASS | 2.9819 | PASS | 2881.9239 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9614 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4617 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 40.9013 | PASS | 14.72 | PASS | 14620.0003 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 23.9769 | PASS | 5.4619 | PASS | 5361.8963 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.8017 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4432 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9363 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 12.3282 | PASS | 11.7268 | PASS | 11626.7927 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531351 [BREWSTR3 115.00] CKT 1 | 12.3282 | PASS | 11.7268 | PASS | 11626.7927 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 139.1255 | PASS | 13.8719 | PASS | 13771.864 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 14.178 | PASS | 9.859 | PASS | 9759.0423 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 27.2812 | PASS | 11.077 | PASS | 10976.969 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 20.5348 | PASS | 11.8823 | PASS | 11782.3245 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 6.0207 | PASS | 23.2125 | PASS | 23112.4742 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 6.0207 | PASS | 23.2125 | PASS | 23112.4742 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 6.0207 | PASS | 46.7724 | PASS | 46672.4201 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 10.9992 | PASS | 36.5999 | PASS | 36499.9044 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 10.9992 | PASS | 36.5999 | PASS | 36499.9044 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 13.5938 | PASS | 0.3025 | PASS | 202.4765 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 15.527 | PASS | 5.0476 | PASS | 4947.6471 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6143 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6143 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 21.1117 | PASS | 2.9885 | PASS | 2888.486 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 24.8222 | PASS | 6.0599 | PASS | 5959.8875 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 24.8222 | PASS | 1.7195 | PASS | 1619.4667 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.8929 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7624 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.6675 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 9.4881 | PASS | 0.2604 | PASS | 160.4437 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 9.4881 | PASS | 0.2489 | PASS | 148.937 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 12.329 | PASS | 11.7274 | PASS | 11627.4064 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531429 [MINGO 3 115.00] TO BUS 531623 [EASTFORK3 115.00] CKT 1 | 12.329 | PASS | 11.7274 | PASS | 11627.4064 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 139.0098 | PASS | 13.8688 | PASS | 13768.8411 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 14.1755 | PASS | 9.858 | PASS | 9758.0031 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 27.2769 | PASS | 11.0759 | PASS | 10975.9205 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 20.5324 | PASS | 11.882 | PASS | 11782.0491 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 6.02 | PASS | 23.2115 | PASS | 23111.4542 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 6.02 | PASS | 23.2115 | PASS | 23111.4542 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 6.02 | PASS | 46.7707 | PASS | 46670.683 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 6.1688 | PASS | 47.0011 | PASS | 46901.0742 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 6.1688 | PASS | 47.0011 | PASS | 46901.0742 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 13.5924 | PASS | 0.3026 | PASS | 202.593 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 15.3465 | PASS | 5.0264 | PASS | 4926.3745 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 26.0301 | PASS | 1.6868 | PASS | 1586.8363 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 26.0301 | PASS | 1.6868 | PASS | 1586.8363 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 20.8952 | PASS | 2.9809 | PASS | 2880.8871 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 24.8225 | PASS | 6.06 | PASS | 5960.0037 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 24.8225 | PASS | 1.7195 | PASS | 1619.4589 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 40.904 | PASS | 14.7208 | PASS | 14620.8045 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 23.9783 | PASS | 5.4629 | PASS | 5362.9182 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 23.5585 | PASS | 5.4537 | PASS | 5353.6725 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 9.4799 | PASS | 0.2604 | PASS | 160.4416 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 9.4799 | PASS | 0.2489 | PASS | 148.9342 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 12.3213 | PASS | 11.7256 | PASS | 11625.6099 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531451 [MINGO 7 345.00] TO BUS 767280 [G22-015-TAP 345.00] CKT 1 | 12.3213 | PASS | 11.7256 | PASS | 11625.6099 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 139.0289 | PASS | 13.8712 | PASS | 13771.2215 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 14.1783 | PASS | 9.8593 | PASS | 9759.3147 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 27.2811 | PASS | 11.0772 | PASS | 10977.1542 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.5337 | PASS | 11.8823 | PASS | 11782.2954 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.0206 | PASS | 23.2127 | PASS | 23112.6548 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.0206 | PASS | 23.2127 | PASS | 23112.6548 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 6.0206 | PASS | 46.7729 | PASS | 46672.927 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.5882 | PASS | 40.8453 | PASS | 40745.2519 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 8.5882 | PASS | 40.8453 | PASS | 40745.2519 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 13.5928 | PASS | 0.3025 | PASS | 202.5267 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 15.4298 | PASS | 5.0297 | PASS | 4929.6533 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 26.027 | PASS | 1.6865 | PASS | 1586.5026 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 26.027 | PASS | 1.6865 | PASS | 1586.5026 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 20.9778 | PASS | 2.968 | PASS | 2868.0307 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9419 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.463 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 40.8995 | PASS | 14.7194 | PASS | 14619.431 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 23.976 | PASS | 5.4612 | PASS | 5361.1712 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 23.5565 | PASS | 5.4522 | PASS | 5352.1818 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 9.4836 | PASS | 0.2604 | PASS | 160.4445 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 9.4836 | PASS | 0.2489 | PASS | 148.938 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 12.3223 | PASS | 11.7267 | PASS | 11626.672 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531449 [HOLCOMB7 345.00] CKT 1 | 12.3223 | PASS | 11.7267 | PASS | 11626.672 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 139.1169 | PASS | 13.8711 | PASS | 13771.1299 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 14.1776 | PASS | 9.8588 | PASS | 9758.8486 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 27.2803 | PASS | 11.0767 | PASS | 10976.7203 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 20.5347 | PASS | 11.8822 | PASS | 11782.249 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2379 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2379 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 6.0206 | PASS | 46.7719 | PASS | 46671.9443 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 10.8843 | PASS | 36.544 | PASS | 36443.9819 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 10.8843 | PASS | 36.544 | PASS | 36443.9819 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.5417 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 15.5247 | PASS | 5.0396 | PASS | 4939.6224 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6426 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6426 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 21.1039 | PASS | 2.9849 | PASS | 2884.9313 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9735 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4608 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 40.9014 | PASS | 14.72 | PASS | 14620.0076 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 23.977 | PASS | 5.4619 | PASS | 5361.9051 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 23.5574 | PASS | 5.4528 | PASS | 5352.8084 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4433 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9365 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 12.3282 | PASS | 1173% | PASS | 11626.8765 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531465 [SETAB 7 345.00] TO BUS 531464 [SETAB 3 115.00] TO BUS 531259 [SETAB 1 13.800] CKT 1 | 12.3282 | PASS | 11.7269 | PASS | 11626.8765 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 139.0064 | PASS | 1387% | PASS | 13773.2934 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 14.1799 | PASS | 9.86 | PASS | 9760.0273 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 27.2834 | PASS | 11.0779 | PASS | 10977.8582 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 20.5353 | PASS | 11.8825 | PASS | 11782.4816 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 6.021 | PASS | 23.2133 | PASS | 23113.3334 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 6.021 | PASS | 23.2133 | PASS | 23113.3334 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 6.021 | PASS | 46.7743 | PASS | 46674.3253 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 10.9919 | PASS | 36.5317 | PASS | 36431.7244 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 10.9919 | PASS | 36.5317 | PASS | 36431.7244 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 13.5932 | PASS | 0.3024 | PASS | 202.4498 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 15.4081 | PASS | 5.0189 | PASS | 4918.8669 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 26.0266 | PASS | 1.6865 | PASS | 1586.4736 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 26.0266 | PASS | 1.6865 | PASS | 1586.4736 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 12.3333 | PASS | 3.3932 | PASS | 3293.1943 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9097 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4653 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 40.899 | PASS | 14.7193 | PASS | 14619.3042 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 23.9758 | PASS | 5.461 | PASS | 5361.0147 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 23.5562 | PASS | 5.452 | PASS | 5351.992 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 9.4861 | PASS | 0.2604 | PASS | 160.4469 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 9.4861 | PASS | 0.2489 | PASS | 148.9411 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 12.3204 | PASS | 11.7279 | PASS | 11627.9124 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531469 [SPERVIL7 345.00] TO BUS 768480 [G22-075-TAP 345.00] CKT 1 | 12.3204 | PASS | 11.7279 | PASS | 11627.9124 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 139.1204 | PASS | 13.8713 | PASS | 13771.2791 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8701 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7283 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2874 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2516 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2516 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46671.9735 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 11.0033 | PASS | 36.5878 | PASS | 36487.8326 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 11.0033 | PASS | 36.5878 | PASS | 36487.8326 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5513 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 15.5266 | PASS | 5.0452 | PASS | 4945.1742 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6269 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6269 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 21.111 | PASS | 2.9863 | PASS | 2886.2984 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9836 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4602 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9432 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8228 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7437 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9435 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9435 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 139.1183 | PASS | 13.871 | PASS | 13770.9893 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 14.1776 | PASS | 9.8588 | PASS | 9758.8438 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 27.2803 | PASS | 11.0767 | PASS | 10976.702 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 20.5347 | PASS | 11.8822 | PASS | 11782.2492 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2233 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2233 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 6.0206 | PASS | 46.7719 | PASS | 46671.9277 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 10.9567 | PASS | 36.5472 | PASS | 36447.1578 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 10.9567 | PASS | 36.5472 | PASS | 36447.1578 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5549 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 15.5236 | PASS | 5.0409 | PASS | 4940.9113 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6243 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6243 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 21.1055 | PASS | 2.9827 | PASS | 2882.6555 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9813 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9329 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8092 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7343 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4433 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9364 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 12.3282 | PASS | 11.7267 | PASS | 11626.7445 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531631 [G15-065XFMR134.500] TO BUS 531633 [SOLO_WND-T3 13.800] CKT 1 | 12.3282 | PASS | 11.7267 | PASS | 11626.7445 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 139.1228 | PASS | 13.8714 | PASS | 13771.3942 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 14.1779 | PASS | 9.859 | PASS | 9758.9707 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 27.2809 | PASS | 11.0769 | PASS | 10976.8803 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2689 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.3881 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.3881 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 6.0206 | PASS | 46.7723 | PASS | 46672.2704 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 11.0081 | PASS | 36.738 | PASS | 36637.9891 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 11.0081 | PASS | 36.738 | PASS | 36637.9891 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 13.5936 | PASS | 0.3025 | PASS | 202.4994 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 15.5265 | PASS | 5.042 | PASS | 4941.9961 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6138 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6138 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 21.1112 | PASS | 2.9839 | PASS | 2883.8556 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9098 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4652 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.8911 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.759 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.6739 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 12.3286 | PASS | 11.7271 | PASS | 11627.0676 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 531632 [GEN-2015-065345.00] TO BUS 531627 [G16-067XFMR134.500] TO BUS 531628 [SOLO_WIND-T213.800] CKT 1 | 12.3286 | PASS | 11.7271 | PASS | 11627.0676 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 134.9823 | PASS | 13.8673 | PASS | 13767.2812 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 14.1627 | PASS | 9.8545 | PASS | 9754.5392 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 27.2472 | PASS | 11.0725 | PASS | 10972.5498 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 19.9115 | PASS | 11.8806 | PASS | 11780.5967 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 6.0146 | PASS | 23.208 | PASS | 23108.0376 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 6.0146 | PASS | 23.208 | PASS | 23108.0376 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 6.0146 | PASS | 46.7787 | PASS | 46678.6811 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 11.0032 | PASS | 36.5475 | PASS | 36447.4928 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 11.0032 | PASS | 36.5475 | PASS | 36447.4928 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 13.5715 | PASS | 0.3028 | PASS | 202.7597 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 15.4867 | PASS | 5.041 | PASS | 4941.0039 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 26.0188 | PASS | 1.6864 | PASS | 1586.3637 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 26.0188 | PASS | 1.6864 | PASS | 1586.3637 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 21.0651 | PASS | 2.9882 | PASS | 2888.1606 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 24.8226 | PASS | 6.0601 | PASS | 5960.113 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 24.8226 | PASS | 1.7195 | PASS | 1619.4516 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 40.8926 | PASS | 14.7189 | PASS | 14618.9206 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 23.9715 | PASS | 5.4604 | PASS | 5360.4474 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 23.554 | PASS | 5.452 | PASS | 5352.0487 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 5.0969 | FAIL | 0.2677 | PASS | 167.6754 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 5.0969 | FAIL | 0.258 | PASS | 157.9715 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 12.0999 | PASS | 11.7263 | PASS | 11626.3287 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532768 [EMPEC 7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 12.0999 | PASS | 11.7263 | PASS | 11626.3287 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 138.9244 | PASS | 13.8728 | PASS | 13772.8026 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 14.1754 | PASS | 9.859 | PASS | 9758.9978 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 27.2748 | PASS | 11.0768 | PASS | 10976.8363 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 19.8819 | PASS | 11.8819 | PASS | 11781.855 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 6.0197 | PASS | 23.2123 | PASS | 23112.2598 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 6.0197 | PASS | 23.2123 | PASS | 23112.2598 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 6.0197 | PASS | 46.7755 | PASS | 46675.5109 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 11.006 | PASS | 36.5455 | PASS | 36445.473 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 11.006 | PASS | 36.5455 | PASS | 36445.473 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 13.5906 | PASS | 0.3025 | PASS | 202.4921 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 15.5225 | PASS | 5.0436 | PASS | 4943.6331 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 26.0247 | PASS | 1.6862 | PASS | 1586.1856 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 26.0247 | PASS | 1.6862 | PASS | 1586.1856 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 21.1061 | PASS | 2.9861 | PASS | 2886.1128 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 24.8222 | PASS | 6.0599 | PASS | 5959.8983 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 24.8222 | PASS | 1.7195 | PASS | 1619.4659 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 40.8964 | PASS | 14.7184 | PASS | 14618.3812 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 23.9742 | PASS | 5.4596 | PASS | 5359.5728 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 23.556 | PASS | 5.4518 | PASS | 5351.8229 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 9.2355 | PASS | 0.2607 | PASS | 160.6792 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 9.2355 | PASS | 0.2492 | PASS | 149.2284 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 12.3188 | PASS | 11.728 | PASS | 11627.9755 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532766 [JEC N 7 345.00] CKT 1 | 12.3188 | PASS | 11.728 | PASS | 11627.9755 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 139.1112 | PASS | 13.8701 | PASS | 13770.0553 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 14.1771 | PASS | 9.8587 | PASS | 9758.7103 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 27.2796 | PASS | 11.0766 | PASS | 10976.5648 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 20.5311 | PASS | 11.8815 | PASS | 11781.4899 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 6.0204 | PASS | 23.212 | PASS | 23112.0106 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 6.0204 | PASS | 23.212 | PASS | 23112.0106 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 6.0204 | PASS | 46.7718 | PASS | 46671.8295 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 11.006 | PASS | 36.5463 | PASS | 36446.2505 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 11.006 | PASS | 36.5463 | PASS | 36446.2505 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5757 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 15.5167 | PASS | 5.046 | PASS | 4946.038 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 26.0274 | PASS | 1.6865 | PASS | 1586.5232 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 26.0274 | PASS | 1.6865 | PASS | 1586.5232 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 21.0918 | PASS | 2.9884 | PASS | 2888.3854 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9457 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4628 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 40.9 | PASS | 14.7195 | PASS | 14619.5453 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 23.9762 | PASS | 5.4613 | PASS | 5361.265 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 23.5568 | PASS | 5.4524 | PASS | 5352.391 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 9.4556 | PASS | 0.2605 | PASS | 160.4953 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 9.4556 | PASS | 0.249 | PASS | 149.0003 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 12.3277 | PASS | 11.7262 | PASS | 11626.2429 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532770 [MORRIS 7 345.00] TO BUS 532863 [MORRIS 6 230.00] TO BUS 532809 [MORRIS1X1 14.400] CKT 1 | 12.3277 | PASS | 11.7262 | PASS | 11626.2429 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 136.9032 | PASS | 13.8342 | PASS | 13734.1758 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 14.1572 | PASS | 9.8513 | PASS | 9751.2837 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 27.2428 | PASS | 11.0696 | PASS | 10969.6116 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 20.5184 | PASS | 11.8753 | PASS | 11775.3144 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 6.0141 | PASS | 23.2046 | PASS | 23104.6106 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 6.0141 | PASS | 23.2046 | PASS | 23104.6106 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 6.0141 | PASS | 46.7789 | PASS | 46678.9201 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 11.0046 | PASS | 36.5434 | PASS | 36443.4337 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 11.0046 | PASS | 36.5434 | PASS | 36443.4337 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 13.5811 | PASS | 0.3028 | PASS | 202.791 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 15.4929 | PASS | 5.0038 | PASS | 4903.8007 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 26.0219 | PASS | 1.6862 | PASS | 1586.1976 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 26.0219 | PASS | 1.6862 | PASS | 1586.1976 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 21.0956 | PASS | 2.9717 | PASS | 2871.7316 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 24.8228 | PASS | 6.0601 | PASS | 5960.1257 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 24.8228 | PASS | 1.7195 | PASS | 1619.4509 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 40.8946 | PASS | 14.7184 | PASS | 14618.4189 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 23.9731 | PASS | 5.4597 | PASS | 5359.7089 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 23.5563 | PASS | 5.4523 | PASS | 5352.2919 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 9.3784 | PASS | 0.2605 | PASS | 160.4523 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 9.3784 | PASS | 0.2489 | PASS | 148.9448 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 12.2058 | PASS | 11.7083 | PASS | 11608.2618 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 587884 [G16-111-TAP 345.00] CKT 1 | 12.2058 | PASS | 11.7083 | PASS | 11608.2618 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 139.0789 | PASS | 13.87 | PASS | 13770.0074 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 14.1775 | PASS | 9.8589 | PASS | 9758.8772 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 27.2798 | PASS | 11.0768 | PASS | 10976.7579 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 20.5318 | PASS | 11.881 | PASS | 11781.0001 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.2799 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.2799 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 6.0205 | PASS | 46.7717 | PASS | 46671.667 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 11.0058 | PASS | 36.546 | PASS | 36446.0414 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 11.0058 | PASS | 36.546 | PASS | 36446.0414 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 13.5926 | PASS | 0.3026 | PASS | 202.5663 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 15.4912 | PASS | 5.0325 | PASS | 4932.5138 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.603 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.603 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 21.0962 | PASS | 2.9838 | PASS | 2883.7568 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9679 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4612 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 40.9009 | PASS | 14.7198 | PASS | 14619.846 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 23.9767 | PASS | 5.4617 | PASS | 5361.6955 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 23.5571 | PASS | 5.4526 | PASS | 5352.6345 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 9.4844 | PASS | 0.2605 | PASS | 160.4517 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 9.4844 | PASS | 0.2489 | PASS | 148.9469 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 12.3252 | PASS | 11.7264 | PASS | 11626.4062 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532807 [RENO 1X1 14.400] CKT 1 | 12.3252 | PASS | 11.7264 | PASS | 11626.4062 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 139.0776 | PASS | 13.8698 | PASS | 13769.8408 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 14.1775 | PASS | 9.8589 | PASS | 9758.8681 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 27.2798 | PASS | 11.0767 | PASS | 10976.7493 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 20.5318 | PASS | 11.881 | PASS | 11780.9533 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 6.0205 | PASS | 2321% | PASS | 23112.2692 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.2692 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 6.0205 | PASS | 4677% | PASS | 46671.6264 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 11.0058 | PASS | 36.5461 | PASS | 36446.0547 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 11.0058 | PASS | 36.5461 | PASS | 36446.0547 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 13.5926 | PASS | 0.3026 | PASS | 202.5679 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 15.4902 | PASS | 5.0321 | PASS | 4932.1288 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.602 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.602 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 21.0957 | PASS | 2.9837 | PASS | 2883.6608 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9669 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4613 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 40.9008 | PASS | 14.7198 | PASS | 14619.8414 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 23.9767 | PASS | 5.4617 | PASS | 5361.6893 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 23.5571 | PASS | 5.4526 | PASS | 5352.6304 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 9.4843 | PASS | 0.2605 | PASS | 160.4518 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 9.4843 | PASS | 0.2489 | PASS | 148.947 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 12.3251 | PASS | 11.7263 | PASS | 11626.314 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532771 [RENO 7 345.00] TO BUS 533416 [RENO 3 115.00] TO BUS 532810 [RENO 2X1 14.400] CKT 1 | 12.3251 | PASS | 11.7263 | PASS | 11626.314 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 138.9504 | PASS | 13.8733 | PASS | 13773.3052 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 14.1722 | PASS | 9.8572 | PASS | 9757.23 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 27.2578 | PASS | 11.0747 | PASS | 10974.7079 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 19.8667 | PASS | 11.8832 | PASS | 11783.2183 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 6.0164 | PASS | 23.2098 | PASS | 23109.8209 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 6.0164 | PASS | 23.2098 | PASS | 23109.8209 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 6.0164 | PASS | 46.7748 | PASS | 46674.8173 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 11.0064 | PASS | 36.5468 | PASS | 36446.785 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 11.0064 | PASS | 36.5468 | PASS | 36446.785 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 13.5852 | PASS | 0.3028 | PASS | 202.8079 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 15.5191 | PASS | 5.0469 | PASS | 4946.8584 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 25.9684 | PASS | 1.6863 | PASS | 1586.3059 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 25.9684 | PASS | 1.6863 | PASS | 1586.3059 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 21.1013 | PASS | 2.9892 | PASS | 2889.1981 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 24.8171 | PASS | 6.0596 | PASS | 5959.6155 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 24.8171 | PASS | 1.7195 | PASS | 1619.4843 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 40.844 | PASS | 14.7184 | PASS | 14618.4205 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 23.9384 | PASS | 5.4595 | PASS | 5359.4788 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 23.516 | PASS | 5.4501 | PASS | 5350.1213 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 9.227 | PASS | 0.2607 | PASS | 160.6795 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 9.227 | PASS | 0.2492 | PASS | 149.2287 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 12.3201 | PASS | 11.7286 | PASS | 11628.6421 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 12.3201 | PASS | 11.7286 | PASS | 11628.6421 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 139.1126 | PASS | 13.8711 | PASS | 13771.0797 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 14.1769 | PASS | 9.8587 | PASS | 9758.7292 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 27.2779 | PASS | 11.0766 | PASS | 10976.5704 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 20.5276 | PASS | 11.8818 | PASS | 11781.8192 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 6.0201 | PASS | 23.2121 | PASS | 23112.076 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 6.0201 | PASS | 23.2121 | PASS | 23112.076 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 6.0201 | PASS | 46.7717 | PASS | 46671.6663 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2211 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2211 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 13.5921 | PASS | 0.3026 | PASS | 202.5807 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 15.5267 | PASS | 5.0448 | PASS | 4944.7886 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 26.0274 | PASS | 1.6866 | PASS | 1586.6175 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 26.0274 | PASS | 1.6866 | PASS | 1586.6175 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 21.1113 | PASS | 2.9859 | PASS | 2885.8815 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 24.8222 | PASS | 6.06 | PASS | 5959.9742 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 24.8222 | PASS | 1.7195 | PASS | 1619.4609 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 40.9002 | PASS | 14.7199 | PASS | 14619.8961 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 23.9762 | PASS | 5.4618 | PASS | 5361.7693 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 23.5562 | PASS | 5.4526 | PASS | 5352.6298 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 9.4774 | PASS | 0.2605 | PASS | 160.4559 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 9.4774 | PASS | 0.249 | PASS | 148.9519 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 12.328 | PASS | 11.7268 | PASS | 11626.848 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532815 [SWISV1X1 14.400] CKT 1 | 12.328 | PASS | 11.7268 | PASS | 11626.848 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 139.1129 | PASS | 13.8711 | PASS | 13771.0849 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 14.1769 | PASS | 9.8587 | PASS | 9758.7324 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 27.278 | PASS | 11.0766 | PASS | 10976.5746 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 20.5277 | PASS | 11.8818 | PASS | 11781.801 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 6.0202 | PASS | 23.2121 | PASS | 23112.0814 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 6.0202 | PASS | 23.2121 | PASS | 23112.0814 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 6.0202 | PASS | 46.7717 | PASS | 46671.7056 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.2212 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.2212 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 13.5921 | PASS | 0.3026 | PASS | 202.5797 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 15.5267 | PASS | 5.0448 | PASS | 4944.7836 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 26.0274 | PASS | 1.6866 | PASS | 1586.6153 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 26.0274 | PASS | 1.6866 | PASS | 1586.6153 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 21.1113 | PASS | 2.9859 | PASS | 2885.8777 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 24.8222 | PASS | 6.06 | PASS | 5959.9719 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 24.8222 | PASS | 1.7195 | PASS | 1619.461 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 40.9002 | PASS | 14.7199 | PASS | 14619.8874 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 23.9762 | PASS | 5.4618 | PASS | 5361.7569 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 23.5562 | PASS | 5.4526 | PASS | 5352.6221 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 9.4776 | PASS | 0.2605 | PASS | 160.4555 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 9.4776 | PASS | 0.249 | PASS | 148.9515 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 12.328 | PASS | 11.7269 | PASS | 11626.852 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532774 [SWISVAL7 345.00] TO BUS 532856 [SWISVAL6 230.00] TO BUS 532819 [SWISV2X2 14.400] CKT 2 | 12.328 | PASS | 11.7269 | PASS | 11626.852 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 139.1516 | PASS | 13.8744 | PASS | 13774.4056 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 14.18 | PASS | 9.86 | PASS | 9759.9502 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 27.2849 | PASS | 11.078 | PASS | 10978.0195 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 20.5355 | PASS | 11.8826 | PASS | 11782.6488 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 6.0212 | PASS | 23.2135 | PASS | 23113.4695 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 6.0212 | PASS | 23.2135 | PASS | 23113.4695 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 6.0212 | PASS | 46.7756 | PASS | 46675.5992 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 11.0067 | PASS | 36.546 | PASS | 36445.9847 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 11.0067 | PASS | 36.546 | PASS | 36445.9847 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 13.5954 | PASS | 0.3022 | PASS | 202.2496 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 15.5276 | PASS | 5.0461 | PASS | 4946.126 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 26.029 | PASS | 1.6867 | PASS | 1586.7179 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 26.029 | PASS | 1.6867 | PASS | 1586.7179 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 21.1133 | PASS | 2.9873 | PASS | 2887.2535 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 24.8218 | PASS | 6.0597 | PASS | 5959.6994 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 24.8218 | PASS | 1.7195 | PASS | 1619.4792 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 40.9024 | PASS | 14.7203 | PASS | 14620.3147 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 23.9775 | PASS | 5.4623 | PASS | 5362.3091 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 23.5576 | PASS | 5.453 | PASS | 5353.0244 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 9.4917 | PASS | 0.2605 | PASS | 160.477 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 9.4917 | PASS | 0.249 | PASS | 148.9783 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 12.3312 | PASS | 11.729 | PASS | 11629.0101 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532776 [READWF 7 345.00] TO BUS 534040 [R1 WFTX1 34.500] TO BUS 534043 [R1 LV 1 13.800] CKT 1 | 12.3312 | PASS | 11.729 | PASS | 11629.0101 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 139.107 | PASS | 13.8686 | PASS | 13768.6162 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 14.1726 | PASS | 9.8535 | PASS | 9753.5281 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 27.2812 | PASS | 11.0684 | PASS | 10968.3639 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 20.5344 | PASS | 11.8821 | PASS | 11782.0796 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 6.0201 | PASS | 23.2007 | PASS | 23100.7239 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 6.0201 | PASS | 23.2007 | PASS | 23100.7239 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 6.0201 | PASS | 46.988 | PASS | 46887.9705 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2484 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2484 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 13.5931 | PASS | 0.3033 | PASS | 203.2952 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 15.5266 | PASS | 5.0444 | PASS | 4944.4287 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6193 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6193 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 21.1115 | PASS | 2.9858 | PASS | 2885.8383 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 24.8221 | PASS | 6.0598 | PASS | 5959.842 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 24.8221 | PASS | 1.7195 | PASS | 1619.4697 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9034 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7593 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.6572 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 9.4877 | PASS | 0.2604 | PASS | 160.4438 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 9.4877 | PASS | 0.2489 | PASS | 148.937 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 12.3274 | PASS | 11.7257 | PASS | 11625.7205 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532778 [GEN-2017-009345.00] CKT 1 | 12.3274 | PASS | 11.7257 | PASS | 11625.7205 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 136.2482 | PASS | 13.8606 | PASS | 13760.6128 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 13.7862 | PASS | 9.8459 | PASS | 9745.8614 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 25.4539 | PASS | 11.0723 | PASS | 10972.2527 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 20.5203 | PASS | 11.8792 | PASS | 11779.2221 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 5.6358 | FAIL | 23.2199 | PASS | 23119.8739 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 5.6358 | FAIL | 23.2199 | PASS | 23119.8739 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 5.6358 | FAIL | 48.5702 | PASS | 48470.1674 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 11.0071 | PASS | 36.5486 | PASS | 36448.5836 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 11.0071 | PASS | 36.5486 | PASS | 36448.5836 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 13.5161 | PASS | 0.302 | PASS | 202.0104 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 15.5146 | PASS | 5.0436 | PASS | 4943.608 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 26.027 | PASS | 1.6866 | PASS | 1586.5854 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 26.027 | PASS | 1.6866 | PASS | 1586.5854 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 21.1034 | PASS | 2.991 | PASS | 2891.0111 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 24.8213 | PASS | 6.0597 | PASS | 5959.7317 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 24.8213 | PASS | 1.7195 | PASS | 1619.4771 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 40.8994 | PASS | 14.7197 | PASS | 14619.6737 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 23.976 | PASS | 5.4616 | PASS | 5361.5552 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 23.5553 | PASS | 5.4519 | PASS | 5351.949 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 9.4176 | PASS | 0.2605 | PASS | 160.4516 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 9.4176 | PASS | 0.2489 | PASS | 148.946 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 12.2063 | PASS | 11.7232 | PASS | 11623.1656 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532777 [G17-009-TAP 345.00] TO BUS 532780 [CANEYRV7 345.00] CKT 1 | 12.2063 | PASS | 11.7232 | PASS | 11623.1656 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 139.1179 | PASS | 13.8442 | PASS | 13744.1612 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 14.1779 | PASS | 9.8585 | PASS | 9758.548 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 27.2868 | PASS | 11.0778 | PASS | 10977.8265 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 20.5336 | PASS | 11.8801 | PASS | 11780.0975 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 6.0211 | PASS | 23.2124 | PASS | 23112.3951 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 6.0211 | PASS | 23.2124 | PASS | 23112.3951 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 6.0211 | PASS | 46.7929 | PASS | 46692.8593 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 11.0096 | PASS | 36.5507 | PASS | 36450.6715 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 11.0096 | PASS | 36.5507 | PASS | 36450.6715 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 13.6047 | PASS | 0.3013 | PASS | 201.2876 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 15.5276 | PASS | 5.0384 | PASS | 4938.4373 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 26.0306 | PASS | 1.6869 | PASS | 1586.8914 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 26.0306 | PASS | 1.6869 | PASS | 1586.8914 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 21.1265 | PASS | 2.9908 | PASS | 2890.8121 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 24.8183 | PASS | 6.0582 | PASS | 5958.2171 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 24.8183 | PASS | 1.7196 | PASS | 1619.5779 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 40.905 | PASS | 14.7211 | PASS | 14621.0596 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 23.9788 | PASS | 5.4633 | PASS | 5363.297 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 23.5585 | PASS | 5.4536 | PASS | 5353.6194 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 9.4786 | PASS | 0.2605 | PASS | 160.4688 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 9.4786 | PASS | 0.249 | PASS | 148.9661 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 12.326 | PASS | 11.7136 | PASS | 11613.5809 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 532783 [KINGMAN7 345.00] CKT 1 | 12.326 | PASS | 11.7136 | PASS | 11613.5809 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 137.929 | PASS | 13.8743 | PASS | 13774.3053 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 14.1706 | PASS | 9.8577 | PASS | 9757.6951 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 27.2617 | PASS | 11.0754 | PASS | 10975.3803 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 20.5176 | PASS | 11.8827 | PASS | 11782.7385 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 6.0176 | PASS | 23.2114 | PASS | 23111.4026 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 6.0176 | PASS | 23.2114 | PASS | 23111.4026 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 6.0176 | PASS | 46.7889 | PASS | 46688.8865 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 10.996 | PASS | 36.5509 | PASS | 36450.9167 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 10.996 | PASS | 36.5509 | PASS | 36450.9167 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 13.5783 | PASS | 0.3031 | PASS | 203.0588 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 15.4555 | PASS | 5.0418 | PASS | 4941.8038 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 26.0263 | PASS | 1.6865 | PASS | 1586.4756 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 26.0263 | PASS | 1.6865 | PASS | 1586.4756 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 20.9979 | PASS | 2.9881 | PASS | 2888.1064 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.975 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4608 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 40.8986 | PASS | 14.7193 | PASS | 14619.3109 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 23.9755 | PASS | 5.461 | PASS | 5361.0088 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 23.5561 | PASS | 5.4521 | PASS | 5352.0764 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 9.3856 | PASS | 0.2605 | PASS | 160.5267 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 9.3856 | PASS | 0.249 | PASS | 149.0401 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 12.2776 | PASS | 11.7274 | PASS | 11627.3818 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 1 | 12.2776 | PASS | 11.7274 | PASS | 11627.3818 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 137.929 | PASS | 13.8743 | PASS | 13774.3053 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 14.1706 | PASS | 9.8577 | PASS | 9757.6951 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 27.2617 | PASS | 11.0754 | PASS | 10975.3803 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 20.5176 | PASS | 11.8827 | PASS | 11782.7385 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 6.0176 | PASS | 23.2114 | PASS | 23111.4026 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 6.0176 | PASS | 23.2114 | PASS | 23111.4026 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 6.0176 | PASS | 46.7889 | PASS | 46688.8865 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 10.996 | PASS | 36.5509 | PASS | 36450.9167 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 10.996 | PASS | 36.5509 | PASS | 36450.9167 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 13.5783 | PASS | 0.3031 | PASS | 203.0588 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 15.4555 | PASS | 504.2% | PASS | 4941.8038 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 26.0263 | PASS | 1.6865 | PASS | 1586.4756 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 26.0263 | PASS | 168.7% | PASS | 1586.4756 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 20.9979 | PASS | 2.9881 | PASS | 2888.1064 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 24.8224 | PASS | 6.06 | PASS | 5959.975 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 24.8224 | PASS | 1.7195 | PASS | 1619.4608 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 40.8986 | PASS | 14.7193 | PASS | 14619.3109 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 23.9755 | PASS | 5.461 | PASS | 5361.0088 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 23.5561 | PASS | 5.4521 | PASS | 5352.0764 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 9.3856 | PASS | 0.2605 | PASS | 160.5267 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 9.3856 | PASS | 0.249 | PASS | 149.0401 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 12.2776 | PASS | 11.7274 | PASS | 11627.3818 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 539801 [THISTLE7 345.00] CKT 2 | 12.2776 | PASS | 11.7274 | PASS | 11627.3818 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 139.0666 | PASS | 13.8645 | PASS | 13764.5439 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 14.1795 | PASS | 9.8597 | PASS | 9759.6677 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 27.2879 | PASS | 11.0788 | PASS | 10978.7728 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 20.5327 | PASS | 11.8813 | PASS | 11781.3115 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 6.0213 | PASS | 23.2136 | PASS | 23113.5783 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 6.0213 | PASS | 23.2136 | PASS | 23113.5783 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 6.0213 | PASS | 46.7855 | PASS | 46685.4514 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 11.0096 | PASS | 36.5509 | PASS | 36450.8536 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 11.0096 | PASS | 36.5509 | PASS | 36450.8536 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 13.6028 | PASS | 0.3013 | PASS | 201.2624 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 15.5272 | PASS | 5.0448 | PASS | 4944.7824 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 26.0305 | PASS | 1.6869 | PASS | 1586.889 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 26.0305 | PASS | 1.6869 | PASS | 1586.889 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 21.1239 | PASS | 2.9935 | PASS | 2893.4717 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 24.8187 | PASS | 6.0584 | PASS | 5958.3715 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 24.8187 | PASS | 1.7196 | PASS | 1619.5676 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 40.9048 | PASS | 14.721 | PASS | 14621.0467 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 23.9787 | PASS | 5.4633 | PASS | 5363.2833 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 23.5584 | PASS | 5.4536 | PASS | 5353.623 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 9.4755 | PASS | 0.2605 | PASS | 160.4572 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 9.4755 | PASS | 0.249 | PASS | 148.9527 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 12.3278 | PASS | 11.7255 | PASS | 11625.5489 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532782 [BUFFALO7 345.00] TO BUS 760284 [GEN-2017-220345.00] CKT 1 | 12.3278 | PASS | 11.7255 | PASS | 11625.5489 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 138.3456 | PASS | 13.8507 | PASS | 13750.718 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 14.1716 | PASS | 9.8561 | PASS | 9756.1128 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 27.2776 | PASS | 11.0755 | PASS | 10975.4809 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 20.5297 | PASS | 11.8799 | PASS | 11779.9242 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 6.02 | PASS | 23.2108 | PASS | 23110.8227 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 6.02 | PASS | 23.2108 | PASS | 23110.8227 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 6.02 | PASS | 46.7653 | PASS | 46665.2975 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36444.9693 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36444.9693 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 13.5902 | PASS | 0.3028 | PASS | 202.8078 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 15.5264 | PASS | 5.0433 | PASS | 4943.2835 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6128 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6128 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 21.1114 | PASS | 2.9852 | PASS | 2885.2027 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9495 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4625 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 40.9009 | PASS | 14.7199 | PASS | 14619.8788 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 23.9767 | PASS | 5.4617 | PASS | 5361.7355 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 23.5571 | PASS | 5.4526 | PASS | 5352.6491 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 9.4882 | PASS | 0.2604 | PASS | 160.4426 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 9.4882 | PASS | 0.2489 | PASS | 148.9354 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 12.3081 | PASS | 11.7178 | PASS | 11617.7523 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532821 [BENTN1 1 13.800] CKT 1 | 12.3081 | PASS | 11.7178 | PASS | 11617.7523 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 138.4043 | PASS | 13.8518 | PASS | 13751.8141 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 14.172 | PASS | 9.8563 | PASS | 9756.2875 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 27.2777 | PASS | 11.0756 | PASS | 10975.5567 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 20.53 | PASS | 11.8801 | PASS | 11780.0717 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 6.02 | PASS | 23.2109 | PASS | 23110.9129 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 6.02 | PASS | 23.2109 | PASS | 23110.9129 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 6.02 | PASS | 46.7658 | PASS | 46665.7672 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36444.9847 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36444.9847 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 13.5904 | PASS | 0.3028 | PASS | 202.7881 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 15.5264 | PASS | 5.0434 | PASS | 4943.3698 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.614 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.614 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 21.1114 | PASS | 2.9852 | PASS | 2885.2413 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 24.8223 | PASS | 6.06 | PASS | 5959.9509 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4624 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.8839 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 23.9767 | PASS | 5.4617 | PASS | 5361.7427 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 23.5571 | PASS | 5.4527 | PASS | 5352.6565 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 9.4882 | PASS | 0.2604 | PASS | 160.4426 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 9.4882 | PASS | 0.2489 | PASS | 148.9354 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 12.3095 | PASS | 11.7183 | PASS | 11618.2576 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532791 [BENTON 7 345.00] TO BUS 532986 [BENTON 4 138.00] TO BUS 532822 [BENTN2 1 13.800] CKT 1 | 12.3095 | PASS | 11.7183 | PASS | 11618.2576 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 139.3291 | PASS | 13.8922 | PASS | 13792.2254 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 14.2371 | PASS | 9.8814 | PASS | 9781.3752 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 27.3909 | PASS | 11.094 | PASS | 10994.043 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 20.5397 | PASS | 11.8845 | PASS | 11784.5083 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 11.0092 | PASS | 36.5497 | PASS | 36449.6637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 11.0092 | PASS | 36.5497 | PASS | 36449.6637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 13.6178 | PASS | 0.3001 | PASS | 200.095 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 15.5304 | PASS | 5.0503 | PASS | 4950.3385 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 26.0337 | PASS | 1.6873 | PASS | 1587.2568 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 26.0337 | PASS | 1.6873 | PASS | 1587.2568 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 21.124 | PASS | 2.994 | PASS | 2893.9944 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 24.814 | PASS | 6.0564 | PASS | 5956.3596 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 24.814 | PASS | 1.7197 | PASS | 1619.7017 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 40.9103 | PASS | 14.7227 | PASS | 14622.7158 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 23.9814 | PASS | 5.4654 | PASS | 5365.3739 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 23.5614 | PASS | 5.4558 | PASS | 5355.8005 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 9.4933 | PASS | 0.2605 | PASS | 160.4502 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 9.4933 | PASS | 0.2489 | PASS | 148.9454 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 12.3443 | PASS | 11.7391 | PASS | 11639.1148 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 767240 [G22-013-TAP 345.00] CKT 1 | 12.3443 | PASS | 11.7391 | PASS | 11639.1148 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 139.0182 | PASS | 13.8691 | PASS | 13769.0896 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 13.247 | PASS | 9.8307 | PASS | 9730.6615 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 19.7406 | PASS | 11.0024 | PASS | 10902.3921 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 20.5351 | PASS | 11.8825 | PASS | 11782.4712 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 5.8439 | FAIL | 23.2381 | PASS | 23138.1024 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 5.8439 | FAIL | 23.2381 | PASS | 23138.1024 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 5.8439 | FAIL | 46.8157 | PASS | 46715.6596 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 11.0059 | PASS | 36.5448 | PASS | 36444.7554 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 11.0059 | PASS | 36.5448 | PASS | 36444.7554 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 13.4915 | PASS | 0.3022 | PASS | 202.2253 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 15.5258 | PASS | 5.0439 | PASS | 4943.8991 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 26.0271 | PASS | 1.6866 | PASS | 1586.5797 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 26.0271 | PASS | 1.6866 | PASS | 1586.5797 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 21.1098 | PASS | 2.9853 | PASS | 2885.2686 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 24.8223 | PASS | 6.06 | PASS | 5959.9898 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4598 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 40.8999 | PASS | 14.7197 | PASS | 14619.7339 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 23.9761 | PASS | 5.4615 | PASS | 5361.5447 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 23.5565 | PASS | 5.4525 | PASS | 5352.507 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 9.4847 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 9.4847 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 12.3229 | PASS | 11.7255 | PASS | 11625.474 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532793 [NEOSHO 7 345.00] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 532825 [N345 2 1 13.800] CKT 1 | 12.3229 | PASS | 11.7255 | PASS | 11625.474 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 136.0986 | PASS | 13.8256 | PASS | 13725.5526 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 13.7684 | PASS | 9.8516 | PASS | 9751.6171 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 25.3744 | PASS | 11.0877 | PASS | 10987.7065 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 20.5164 | PASS | 11.8769 | PASS | 11776.865 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 5.6217 | FAIL | 23.2453 | PASS | 23145.2797 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 5.6217 | FAIL | 23.2453 | PASS | 23145.2797 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 5.6217 | FAIL | 48.0757 | PASS | 47975.6635 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 11.0074 | PASS | 36.549 | PASS | 36449.0076 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 11.0074 | PASS | 36.549 | PASS | 36449.0076 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 13.5118 | PASS | 0.3005 | PASS | 200.5209 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 15.5135 | PASS | 5.0399 | PASS | 4939.9218 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 26.0269 | PASS | 1.6866 | PASS | 1586.5983 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 26.0269 | PASS | 1.6866 | PASS | 1586.5983 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 21.1051 | PASS | 2.9907 | PASS | 2890.7007 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 24.8214 | PASS | 6.0598 | PASS | 5959.7932 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 24.8214 | PASS | 1.7195 | PASS | 1619.4729 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 40.8994 | PASS | 14.7197 | PASS | 14619.7252 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 23.976 | PASS | 5.4617 | PASS | 5361.6578 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 23.5552 | PASS | 5.452 | PASS | 5351.954 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 9.412 | PASS | 0.2604 | PASS | 160.4432 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 9.412 | PASS | 0.2489 | PASS | 148.9348 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 12.1944 | PASS | 11.7068 | PASS | 11606.799 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 532800 [LATHAMS7 345.00] CKT 1 | 12.1944 | PASS | 11.7068 | PASS | 11606.799 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 135.0574 | PASS | 13.8177 | PASS | 13717.6966 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 14.0779 | PASS | 9.8312 | PASS | 9731.1592 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 27.0391 | PASS | 11.0484 | PASS | 10948.3974 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 20.5085 | PASS | 11.8811 | PASS | 11781.0957 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 5.9804 | FAIL | 23.1896 | PASS | 23089.5926 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 5.9804 | FAIL | 23.1896 | PASS | 23089.5926 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 5.9804 | FAIL | 46.9258 | PASS | 46825.7732 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 10.9985 | PASS | 36.5358 | PASS | 36435.8066 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 10.9985 | PASS | 36.5358 | PASS | 36435.8066 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 13.4364 | PASS | 0.3108 | PASS | 210.8277 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 15.5023 | PASS | 5.0299 | PASS | 4929.8787 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 26.0218 | PASS | 1.6861 | PASS | 1586.1001 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 26.0218 | PASS | 1.6861 | PASS | 1586.1001 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 21.0765 | PASS | 2.9766 | PASS | 2876.6291 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 24.8211 | PASS | 6.0594 | PASS | 5959.3652 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 24.8211 | PASS | 1.7195 | PASS | 1619.5016 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 40.892 | PASS | 14.7176 | PASS | 14617.5947 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 23.972 | PASS | 5.4587 | PASS | 5358.7293 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 23.5527 | PASS | 5.45 | PASS | 5350.0027 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 9.386 | PASS | 0.2605 | PASS | 160.4581 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 9.386 | PASS | 0.249 | PASS | 148.9538 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 12.1483 | PASS | 11.6877 | PASS | 11587.6748 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 560053 [G15052_T 345.00] CKT 1 | 12.1483 | PASS | 11.6877 | PASS | 11587.6748 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 137.8694 | PASS | 13.862 | PASS | 13762.0467 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 14.1758 | PASS | 9.8581 | PASS | 9758.0606 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 27.2757 | PASS | 11.0765 | PASS | 10976.5204 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 20.533 | PASS | 11.8816 | PASS | 11781.5782 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 6.0195 | PASS | 23.2122 | PASS | 23112.1736 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 6.0195 | PASS | 23.2122 | PASS | 23112.1736 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 6.0195 | PASS | 46.7626 | PASS | 46662.5768 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.3255 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.3255 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 13.5898 | PASS | 0.3027 | PASS | 202.652 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 15.5267 | PASS | 5.0441 | PASS | 4944.1162 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6186 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6186 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 21.1119 | PASS | 2.9858 | PASS | 2885.8272 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9672 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4613 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.9025 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7709 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.6703 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 9.4873 | PASS | 0.2604 | PASS | 160.44 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 9.4873 | PASS | 0.2489 | PASS | 148.9322 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 12.2904 | PASS | 11.7229 | PASS | 11622.9063 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532826 [ROSEH1 1 13.800] CKT 1 | 12.2904 | PASS | 11.7229 | PASS | 11622.9063 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 137.9689 | PASS | 13.8628 | PASS | 13762.7741 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 14.176 | PASS | 9.8581 | PASS | 9758.1274 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 27.2761 | PASS | 11.0765 | PASS | 10976.5387 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 20.5332 | PASS | 11.8816 | PASS | 11781.635 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 6.0196 | PASS | 23.2122 | PASS | 23112.1801 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 6.0196 | PASS | 23.2122 | PASS | 23112.1801 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 6.0196 | PASS | 46.7633 | PASS | 46663.3397 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.3128 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.3128 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 13.5901 | PASS | 0.3026 | PASS | 202.6437 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 15.5267 | PASS | 5.0442 | PASS | 4944.1572 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6192 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6192 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 21.1118 | PASS | 2.9858 | PASS | 2885.8228 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9683 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4612 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.9055 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7756 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.6757 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 9.4874 | PASS | 26.04% | PASS | 160.4403 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 9.4874 | PASS | 0.2489 | PASS | 148.9326 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 12.2935 | PASS | 1172% | PASS | 11623.2256 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532831 [ROSEH3 1 13.800] CKT 1 | 12.2935 | PASS | 11.7232 | PASS | 11623.2256 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 137.8549 | PASS | 13.8619 | PASS | 13761.9197 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 14.1758 | PASS | 9.858 | PASS | 9758.048 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 27.2756 | PASS | 11.0765 | PASS | 10976.5145 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 20.533 | PASS | 11.8816 | PASS | 11781.5689 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 6.0195 | PASS | 23.2122 | PASS | 23112.1676 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 6.0195 | PASS | 23.2122 | PASS | 23112.1676 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 6.0195 | PASS | 46.7625 | PASS | 46662.4536 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.3253 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.3253 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 13.5897 | PASS | 0.3027 | PASS | 202.6535 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 15.5267 | PASS | 5.0441 | PASS | 4944.1077 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6185 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6185 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 21.1119 | PASS | 2.9858 | PASS | 2885.8268 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9669 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4613 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.902 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7703 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.6694 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 9.4873 | PASS | 0.2604 | PASS | 160.4399 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 9.4873 | PASS | 0.2489 | PASS | 148.9322 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 12.29 | PASS | 11.7228 | PASS | 11622.8487 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532794 [ROSEHIL7 345.00] TO BUS 533062 [ROSEHIL4 138.00] TO BUS 532827 [ROSEH5 1 13.800] CKT 1 | 12.29 | PASS | 11.7228 | PASS | 11622.8487 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 135.0551 | PASS | 13.8461 | PASS | 13746.1466 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 14.1332 | PASS | 9.8417 | PASS | 9741.7161 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 27.2002 | PASS | 11.06 | PASS | 10959.9661 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 19.8188 | PASS | 11.8605 | PASS | 11760.4588 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 6.007 | PASS | 23.1942 | PASS | 23094.2339 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 6.007 | PASS | 23.1942 | PASS | 23094.2339 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 6.007 | PASS | 46.7704 | PASS | 46670.4162 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 11.0059 | PASS | 36.552 | PASS | 36452.0206 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 11.0059 | PASS | 36.552 | PASS | 36452.0206 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 13.5688 | PASS | 0.3034 | PASS | 203.3514 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 15.4797 | PASS | 5.0299 | PASS | 4929.8647 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 26.0082 | PASS | 1.6853 | PASS | 1585.2561 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 26.0082 | PASS | 1.6853 | PASS | 1585.2561 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 21.0777 | PASS | 2.9947 | PASS | 2894.6954 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 24.8221 | PASS | 6.0598 | PASS | 5959.8333 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 24.8221 | PASS | 1.7195 | PASS | 1619.4703 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 40.8776 | PASS | 14.7145 | PASS | 14614.5344 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 23.9636 | PASS | 5.4545 | PASS | 5354.5291 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 23.5491 | PASS | 5.4485 | PASS | 5348.5133 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 4.5753 | FAIL | 0.2717 | PASS | 171.7118 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 4.5753 | FAIL | 0.2631 | PASS | 163.1156 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 12.1078 | PASS | 11.7197 | PASS | 11619.6751 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532796 [WICHITA7 345.00] TO BUS 532803 [BURNS 7 345.00] CKT 1 | 12.1078 | PASS | 11.7197 | PASS | 11619.6751 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 138.722 | PASS | 13.8512 | PASS | 13751.1842 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 14.0769 | PASS | 9.862 | PASS | 9762.0265 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 26.7395 | PASS | 11.0769 | PASS | 10976.9134 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 20.5326 | PASS | 11.8818 | PASS | 11781.8301 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 5.9089 | FAIL | 23.214 | PASS | 23114.029 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 5.9089 | FAIL | 23.214 | PASS | 23114.029 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 5.9089 | FAIL | 47.234 | PASS | 47134.0059 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 11.0052 | PASS | 36.5443 | PASS | 36444.3054 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 11.0052 | PASS | 36.5443 | PASS | 36444.3054 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 7.1418 | PASS | 0.3697 | PASS | 269.741 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 15.5232 | PASS | 5.042 | PASS | 4942.0421 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 26.0251 | PASS | 1.6863 | PASS | 1586.2698 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 26.0251 | PASS | 1.6863 | PASS | 1586.2698 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 21.1043 | PASS | 2.983 | PASS | 2882.9835 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 24.8215 | PASS | 6.0599 | PASS | 5959.9428 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 24.8215 | PASS | 1.7195 | PASS | 1619.4629 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 40.8961 | PASS | 14.7184 | PASS | 14618.3605 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 23.9741 | PASS | 5.4596 | PASS | 5359.6134 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 23.555 | PASS | 5.451 | PASS | 5351.0102 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 9.4759 | PASS | 0.2604 | PASS | 160.441 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 9.4759 | PASS | 0.2489 | PASS | 148.9332 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.305 | PASS | 11.7159 | PASS | 11615.8931 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532797 [WOLFCRK7 345.00] TO BUS 765200 [G20-090-TAP 345.00] CKT 1 | 12.305 | PASS | 11.7159 | PASS | 11615.8931 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 138.8722 | PASS | 13.7982 | PASS | 13698.1763 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 14.1732 | PASS | 9.8564 | PASS | 9756.3558 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 27.2824 | PASS | 11.0766 | PASS | 10976.5988 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 20.5304 | PASS | 11.879 | PASS | 11778.9666 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 6.0203 | PASS | 23.211 | PASS | 23111.0176 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 6.0203 | PASS | 23.211 | PASS | 23111.0176 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 6.0203 | PASS | 46.791 | PASS | 46690.9719 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 11.01 | PASS | 36.5509 | PASS | 36450.8852 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 11.01 | PASS | 36.5509 | PASS | 36450.8852 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 13.6074 | PASS | 0.3009 | PASS | 200.9345 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 15.5259 | PASS | 5.038 | PASS | 4937.9761 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 26.0318 | PASS | 1.687 | PASS | 1587.0275 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 26.0318 | PASS | 1.687 | PASS | 1587.0275 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 21.1297 | PASS | 2.9935 | PASS | 2893.5228 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 24.8153 | PASS | 6.0569 | PASS | 5956.9051 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 24.8153 | PASS | 1.7197 | PASS | 1619.6653 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 40.9068 | PASS | 14.7216 | PASS | 14621.6229 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 23.9797 | PASS | 5.464 | PASS | 5364.0461 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 23.559 | PASS | 5.454 | PASS | 5354.0493 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 9.4714 | PASS | 0.2604 | PASS | 160.4379 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 9.4714 | PASS | 0.2489 | PASS | 148.9277 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 12.2887 | PASS | 11.663 | PASS | 11563.0386 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 588364 [G16-153-TAP 345.00] CKT 1 | 12.2887 | PASS | 11.663 | PASS | 11563.0386 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 129.2179 | PASS | 13.8268 | PASS | 13726.7726 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 14.1204 | PASS | 9.8372 | PASS | 9737.2241 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 27.1687 | PASS | 11.053 | PASS | 10952.9837 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 20.4882 | PASS | 11.881 | PASS | 11780.9742 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 6.0044 | PASS | 23.1914 | PASS | 23091.4124 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 6.0044 | PASS | 23.1914 | PASS | 23091.4124 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 6.0044 | PASS | 46.7648 | PASS | 46664.791 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 10.9921 | PASS | 36.5298 | PASS | 36429.8121 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 10.9921 | PASS | 36.5298 | PASS | 36429.8121 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 13.5292 | PASS | 0.3085 | PASS | 208.459 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 15.4786 | PASS | 5.0297 | PASS | 4929.6645 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 26.0228 | PASS | 1.6862 | PASS | 1586.1622 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 26.0228 | PASS | 1.6862 | PASS | 1586.1622 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 21.031 | PASS | 2.9694 | PASS | 2869.4285 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 24.8219 | PASS | 6.0597 | PASS | 5959.6979 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 24.8219 | PASS | 1.7195 | PASS | 1619.4794 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 40.8937 | PASS | 14.718 | PASS | 14617.987 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 23.9729 | PASS | 5.4592 | PASS | 5359.2098 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 23.5545 | PASS | 5.451 | PASS | 5351.0196 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.2693 | PASS | 0.2605 | PASS | 160.5364 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 9.2693 | PASS | 0.2491 | PASS | 149.0514 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 11.2976 | PASS | 11.705 | PASS | 11605.0047 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532798 [VIOLA 7 345.00] TO BUS 763421 [G18-128-TAP 345.00] CKT 1 | 11.2976 | PASS | 11.705 | PASS | 11605.0047 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 139.1845 | PASS | 13.876 | PASS | 13775.9875 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 14.1831 | PASS | 9.861 | PASS | 9760.9547 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 27.2931 | PASS | 11.0793 | PASS | 10979.2736 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 20.5355 | PASS | 11.8826 | PASS | 11782.5512 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 6.0227 | PASS | 23.215 | PASS | 23115.0209 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 6.0227 | PASS | 23.215 | PASS | 23115.0209 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 6.0227 | PASS | 46.7453 | PASS | 46645.2865 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 11.0067 | PASS | 36.5459 | PASS | 36445.9336 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 11.0067 | PASS | 36.5459 | PASS | 36445.9336 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 13.6156 | PASS | 0.3016 | PASS | 201.6142 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 15.5275 | PASS | 5.0458 | PASS | 4945.7758 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 26.0293 | PASS | 1.6867 | PASS | 1586.7356 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 26.0293 | PASS | 1.6867 | PASS | 1586.7356 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 21.1134 | PASS | 2.9871 | PASS | 2887.138 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 24.8217 | PASS | 6.0597 | PASS | 5959.661 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 24.8217 | PASS | 1.7195 | PASS | 1619.4817 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 40.9029 | PASS | 14.7204 | PASS | 14620.4289 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 23.9778 | PASS | 5.4624 | PASS | 5362.4491 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 23.5581 | PASS | 5.4533 | PASS | 5353.2961 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 9.4899 | PASS | 0.2604 | PASS | 160.4469 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 9.4899 | PASS | 0.2489 | PASS | 148.941 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 12.3327 | PASS | 11.7297 | PASS | 11629.6532 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 532802 [WAVERTX7 345.00] CKT 1 | 12.3327 | PASS | 11.7297 | PASS | 11629.6532 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 138.3856 | PASS | 13.8762 | PASS | 13776.1503 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 14.1694 | PASS | 9.8558 | PASS | 9755.7517 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 27.2668 | PASS | 11.0732 | PASS | 10973.198 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 20.5339 | PASS | 11.8818 | PASS | 11781.8329 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 6.0183 | PASS | 23.2081 | PASS | 23108.0685 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 6.0183 | PASS | 23.2081 | PASS | 23108.0685 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 6.0183 | PASS | 46.7588 | PASS | 46658.8136 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 11.0064 | PASS | 36.546 | PASS | 36445.9851 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 11.0064 | PASS | 36.546 | PASS | 36445.9851 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.9449 | PASS | 0.3018 | PASS | 201.8236 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 15.523 | PASS | 5.0441 | PASS | 4944.1159 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 25.9958 | PASS | 1.6863 | PASS | 1586.2764 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 25.9958 | PASS | 1.6863 | PASS | 1586.2764 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 21.1102 | PASS | 2.9878 | PASS | 2887.8219 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 24.8205 | PASS | 6.0598 | PASS | 5959.7622 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 24.8205 | PASS | 1.7195 | PASS | 1619.4747 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 40.8698 | PASS | 14.7183 | PASS | 14618.3174 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 23.9572 | PASS | 5.4595 | PASS | 5359.5244 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 23.5373 | PASS | 5.4504 | PASS | 5350.4305 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 9.4739 | PASS | 0.2604 | PASS | 160.4431 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 9.4739 | PASS | 0.2489 | PASS | 148.936 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.2969 | PASS | 11.7292 | PASS | 11629.1966 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532799 [WAVERLY7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.2969 | PASS | 11.7292 | PASS | 11629.1966 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 139.0827 | PASS | 13.8691 | PASS | 13769.1072 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 14.0424 | PASS | 9.8598 | PASS | 9759.8203 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 26.5767 | PASS | 11.0792 | PASS | 10979.2409 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2776 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 5.9954 | FAIL | 23.2108 | PASS | 23110.7656 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 5.9954 | FAIL | 23.2108 | PASS | 23110.7656 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 5.9954 | FAIL | 46.8846 | PASS | 46784.6308 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0529 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0529 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 13.5755 | PASS | 0.303 | PASS | 202.9755 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 15.5259 | PASS | 5.0435 | PASS | 4943.4721 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 26.0178 | PASS | 1.6867 | PASS | 1586.6543 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 26.0178 | PASS | 1.6867 | PASS | 1586.6543 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 21.1119 | PASS | 2.9861 | PASS | 2886.0692 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 24.8225 | PASS | 6.0602 | PASS | 5960.1939 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 24.8225 | PASS | 1.7194 | PASS | 1619.4462 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 40.8923 | PASS | 14.72 | PASS | 14620.0422 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 23.9707 | PASS | 5.462 | PASS | 5362.0276 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 23.5512 | PASS | 5.4529 | PASS | 5352.8987 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 9.4854 | PASS | 0.2604 | PASS | 160.4411 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 9.4854 | PASS | 0.2489 | PASS | 148.9335 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 12.3257 | PASS | 11.7254 | PASS | 11625.4336 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 543650 [DAKOTA_5 161.00] CKT 1 | 12.3257 | PASS | 11.7254 | PASS | 11625.4336 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 139.0996 | PASS | 13.8699 | PASS | 13769.9058 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 14.1576 | PASS | 9.8568 | PASS | 9756.782 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 27.1347 | PASS | 11.073 | PASS | 10973.0151 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 20.5338 | PASS | 11.8821 | PASS | 11782.1489 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 6.0154 | PASS | 23.2103 | PASS | 23110.2641 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 6.0154 | PASS | 23.2103 | PASS | 23110.2641 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 6.0154 | PASS | 46.7311 | PASS | 46631.1097 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.0155 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.0155 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 13.5881 | PASS | 0.3029 | PASS | 202.9063 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 15.5263 | PASS | 5.0442 | PASS | 4944.2007 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 26.0259 | PASS | 1.6866 | PASS | 1586.6148 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 26.0259 | PASS | 1.6866 | PASS | 1586.6148 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 21.111 | PASS | 2.9856 | PASS | 2885.6147 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9966 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4593 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 40.8991 | PASS | 14.7199 | PASS | 14619.884 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 23.9755 | PASS | 5.4618 | PASS | 5361.7595 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 23.5559 | PASS | 5.4527 | PASS | 5352.6866 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 9.4868 | PASS | 0.2604 | PASS | 160.4429 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 9.4868 | PASS | 0.2489 | PASS | 148.9359 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 12.327 | PASS | 11.7261 | PASS | 11626.1128 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532934 [MARMTNE5 161.00] TO BUS 588504 [G17-005-TAP 161.00] CKT 1 | 12.327 | PASS | 11.7261 | PASS | 11626.1128 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 139.0826 | PASS | 13.8712 | PASS | 13771.2144 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 13.9885 | PASS | 9.86 | PASS | 9759.9792 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 25.6703 | PASS | 1108% | PASS | 10983.6007 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 20.5343 | PASS | 11.8822 | PASS | 11782.2015 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 5.9674 | FAIL | 2321% | PASS | 23114.7015 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 5.9674 | FAIL | 23.2147 | PASS | 23114.7015 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 5.9674 | FAIL | 46.812 | PASS | 46711.9905 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1369 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1369 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 13.5659 | PASS | 0.3026 | PASS | 202.5953 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 15.5266 | PASS | 5.0447 | PASS | 4944.7172 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 26.0272 | PASS | 1.6866 | PASS | 1586.6093 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 26.0272 | PASS | 1.6866 | PASS | 1586.6093 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 21.1108 | PASS | 2.9857 | PASS | 2885.6545 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9237 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4643 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 40.9003 | PASS | 14.7199 | PASS | 14619.8679 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 23.9762 | PASS | 5.4617 | PASS | 5361.7027 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 23.5567 | PASS | 5.4526 | PASS | 5352.6397 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 9.4875 | PASS | 0.2604 | PASS | 160.4442 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 9.4875 | PASS | 0.2489 | PASS | 148.9376 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 12.3268 | PASS | 11.7269 | PASS | 11626.947 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532935 [MARMTNW5 161.00] TO BUS 532937 [NEOSHO 5 161.00] CKT 1 | 12.3268 | PASS | 11.7269 | PASS | 11626.947 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 139.1189 | PASS | 13.8713 | PASS | 13771.2754 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 13.7914 | PASS | 9.8611 | PASS | 9761.0949 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 26.4594 | PASS | 11.078 | PASS | 10978.0056 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 20.5348 | PASS | 11.8824 | PASS | 11782.3897 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 6.0205 | PASS | 23.212 | PASS | 23111.9832 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 6.0205 | PASS | 23.212 | PASS | 23111.9832 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 6.0205 | PASS | 46.7726 | PASS | 46672.596 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1696 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1696 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.555 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6222 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6267 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6267 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7908 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9824 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9423 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8225 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7388 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.932 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532958 [NEOSH4 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533021 [NEOSHO 4 138.00] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.932 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 139.1178 | PASS | 13.8713 | PASS | 13771.2856 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 13.535 | PASS | 9.8625 | PASS | 9762.473 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 25.9096 | PASS | 11.0791 | PASS | 10979.1021 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 20.5348 | PASS | 11.8825 | PASS | 11782.4646 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 6.0205 | PASS | 23.2118 | PASS | 23111.7964 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 6.0205 | PASS | 23.2118 | PASS | 23111.7964 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 6.0205 | PASS | 46.7728 | PASS | 46672.7952 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1773 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1773 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5583 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6177 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6271 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6271 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 21.1113 | PASS | 2.9858 | PASS | 2885.8079 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.983 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4602 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9427 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8247 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7377 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.9332 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532959 [NEOSH5 1 13.200] TO BUS 532937 [NEOSHO 5 161.00] TO BUS 533020 [NEOSHOS4 138.00] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.9332 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 137.5543 | PASS | 13.8595 | PASS | 13759.4825 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 14.171 | PASS | 9.8571 | PASS | 9757.0946 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 27.2656 | PASS | 11.0749 | PASS | 10974.9494 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 20.5305 | PASS | 11.8822 | PASS | 11782.1949 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 6.0183 | PASS | 23.2109 | PASS | 23110.8695 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 6.0183 | PASS | 23.2109 | PASS | 23110.8695 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 6.0183 | PASS | 46.7757 | PASS | 46675.7011 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 11.0053 | PASS | 36.5443 | PASS | 36444.2646 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 11.0053 | PASS | 36.5443 | PASS | 36444.2646 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 13.5842 | PASS | 0.303 | PASS | 202.9648 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 15.523 | PASS | 5.0431 | PASS | 4943.1246 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 26.0277 | PASS | 1.6866 | PASS | 1586.5956 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 26.0277 | PASS | 1.6866 | PASS | 1586.5956 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 21.1056 | PASS | 2.9846 | PASS | 2884.6428 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9778 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4606 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 40.9006 | PASS | 14.7198 | PASS | 14619.8079 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 23.9766 | PASS | 5.4616 | PASS | 5361.6436 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 23.557 | PASS | 5.4526 | PASS | 5352.6081 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 9.4725 | PASS | 0.2604 | PASS | 160.4471 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 9.4725 | PASS | 0.2489 | PASS | 148.9411 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 12.2308 | PASS | 11.7203 | PASS | 11620.297 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532982 [OXFORD 4 138.00] CKT 1 | 12.2308 | PASS | 11.7203 | PASS | 11620.297 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 138.9143 | PASS | 13.8736 | PASS | 13773.5694 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 14.1772 | PASS | 9.8587 | PASS | 9758.6901 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 27.2799 | PASS | 11.0767 | PASS | 10976.7112 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 20.534 | PASS | 11.8821 | PASS | 11782.1067 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2408 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2408 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 6.0205 | PASS | 46.7723 | PASS | 46672.2846 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 11.0061 | PASS | 36.5452 | PASS | 36445.1516 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 11.0061 | PASS | 36.5452 | PASS | 36445.1516 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 13.5929 | PASS | 0.3025 | PASS | 202.546 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 15.5262 | PASS | 5.0447 | PASS | 4944.7136 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6275 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6275 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 21.1104 | PASS | 2.9858 | PASS | 2885.7788 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9799 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4605 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.946 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.826 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7482 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 9.4864 | PASS | 0.2604 | PASS | 160.4444 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 9.4864 | PASS | 0.2489 | PASS | 148.9379 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 12.3118 | PASS | 11.7292 | PASS | 11629.164 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 532992 [TIMBJCT4 138.00] CKT 1 | 12.3118 | PASS | 11.7292 | PASS | 11629.164 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 138.2598 | PASS | 13.8615 | PASS | 13761.5086 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 14.1721 | PASS | 9.8581 | PASS | 9758.0552 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 27.2658 | PASS | 11.076 | PASS | 10975.9521 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 20.5324 | PASS | 11.882 | PASS | 11782.0204 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 6.018 | PASS | 23.2115 | PASS | 23111.5206 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 6.018 | PASS | 23.2115 | PASS | 23111.5206 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 6.018 | PASS | 46.7928 | PASS | 46692.8352 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0602 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0602 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 13.5844 | PASS | 0.3027 | PASS | 202.7023 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 15.5262 | PASS | 5.0441 | PASS | 4944.0611 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.6149 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.6149 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 21.1108 | PASS | 2.9856 | PASS | 2885.5572 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9772 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4606 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 40.9009 | PASS | 14.7199 | PASS | 14619.8904 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 23.9767 | PASS | 5.4618 | PASS | 5361.7534 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 23.5571 | PASS | 5.4527 | PASS | 5352.6798 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 9.4832 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 9.4832 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 12.3263 | PASS | 11.724 | PASS | 11623.9572 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 533063 [SC10BEL4 138.00] CKT 1 | 12.3263 | PASS | 11.724 | PASS | 11623.9572 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 138.9694 | PASS | 13.8509 | PASS | 13750.8785 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 14.1756 | PASS | 9.8578 | PASS | 9757.8128 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 27.2795 | PASS | 11.0763 | PASS | 10976.2616 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 20.5328 | PASS | 11.8813 | PASS | 11781.2792 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 6.0202 | PASS | 23.2113 | PASS | 23111.3499 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 6.0202 | PASS | 23.2113 | PASS | 23111.3499 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 6.0202 | PASS | 46.781 | PASS | 46681.0005 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 11.0069 | PASS | 36.5464 | PASS | 36446.3593 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 11.0069 | PASS | 36.5464 | PASS | 36446.3593 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 13.5962 | PASS | 0.3022 | PASS | 202.2101 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 15.5265 | PASS | 5.0438 | PASS | 4943.8186 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 26.029 | PASS | 1.6867 | PASS | 1586.7196 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 26.029 | PASS | 1.6867 | PASS | 1586.7196 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 21.1146 | PASS | 2.9875 | PASS | 2887.4963 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 24.8213 | PASS | 6.0595 | PASS | 5959.4771 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 24.8213 | PASS | 1.7195 | PASS | 1619.4939 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 40.9025 | PASS | 14.7203 | PASS | 14620.3424 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 23.9775 | PASS | 5.4623 | PASS | 5362.3428 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 23.5578 | PASS | 5.4531 | PASS | 5353.1049 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 9.4845 | PASS | 0.2604 | PASS | 160.4392 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 9.4845 | PASS | 0.2489 | PASS | 148.931 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 12.3164 | PASS | 11.7155 | PASS | 11615.4758 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532984 [SUMNER 4 138.00] TO BUS 761838 [GEN-2017-121138.00] CKT 1 | 12.3164 | PASS | 11.7155 | PASS | 11615.4758 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 139.0382 | PASS | 13.8703 | PASS | 13770.2857 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 13.4684 | PASS | 9.8461 | PASS | 9746.1354 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 26.9079 | PASS | 11.0721 | PASS | 10972.0669 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 20.5241 | PASS | 11.8811 | PASS | 11781.0569 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 6.0014 | PASS | 23.2105 | PASS | 23110.4826 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 6.0014 | PASS | 23.2105 | PASS | 23110.4826 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 6.0014 | PASS | 46.8702 | PASS | 46770.2382 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 11.0061 | PASS | 36.5452 | PASS | 36445.1692 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 11.0061 | PASS | 36.5452 | PASS | 36445.1692 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 13.5844 | PASS | 0.3026 | PASS | 202.5999 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 15.5263 | PASS | 5.0446 | PASS | 4944.5922 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6221 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6221 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 21.1106 | PASS | 2.9857 | PASS | 2885.6968 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 24.8223 | PASS | 6.06 | PASS | 5959.96 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4617 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.9238 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 23.9767 | PASS | 5.4618 | PASS | 5361.7913 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 23.5571 | PASS | 5.4527 | PASS | 5352.7205 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 9.4856 | PASS | 0.2604 | PASS | 160.444 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 9.4856 | PASS | 0.2489 | PASS | 148.9373 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 12.3249 | PASS | 11.7265 | PASS | 11626.5272 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532996 [TIOGA 4 138.00] TO BUS 533646 [TIOGA 2 69.000] TO BUS 533084 [TIOGA 1 13.200] CKT 1 | 12.3249 | PASS | 11.7265 | PASS | 11626.5272 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 137.9251 | PASS | 13.8662 | PASS | 13766.1578 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 13.8901 | PASS | 9.8641 | PASS | 9764.1075 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 27.1305 | PASS | 11.0745 | PASS | 10974.5072 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 20.4099 | PASS | 11.8888 | PASS | 11788.7596 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 6.0166 | PASS | 23.211 | PASS | 23110.9996 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 6.0166 | PASS | 23.211 | PASS | 23110.9996 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 6.0166 | PASS | 46.7461 | PASS | 46646.0845 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 11.0062 | PASS | 36.5456 | PASS | 36445.5728 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 11.0062 | PASS | 36.5456 | PASS | 36445.5728 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 13.5942 | PASS | 0.3025 | PASS | 202.4953 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 15.5244 | PASS | 5.0438 | PASS | 4943.8237 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.6129 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.6129 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 21.1094 | PASS | 2.9861 | PASS | 2886.1049 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 24.8225 | PASS | 6.06 | PASS | 5960.0014 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 24.8225 | PASS | 1.7195 | PASS | 1619.4591 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 40.9009 | PASS | 14.7199 | PASS | 14619.8845 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 23.9767 | PASS | 5.4618 | PASS | 5361.7554 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 23.5571 | PASS | 5.4527 | PASS | 5352.6829 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 9.4801 | PASS | 0.2604 | PASS | 160.4399 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 9.4801 | PASS | 0.2489 | PASS | 148.932 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 12.2821 | PASS | 11.7246 | PASS | 11624.6478 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 532987 [BUTLER 4 138.00] CKT 1 | 12.2821 | PASS | 11.7246 | PASS | 11624.6478 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 138.9442 | PASS | 13.8684 | PASS | 13768.3906 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 14.0918 | PASS | 9.86 | PASS | 9760.0282 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 27.2199 | PASS | 11.0782 | PASS | 10978.1579 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 19.719 | PASS | 11.8921 | PASS | 11792.1136 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 6.0165 | PASS | 23.2122 | PASS | 23112.2353 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 6.0165 | PASS | 23.2122 | PASS | 23112.2353 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 6.0165 | PASS | 46.7631 | PASS | 46663.0728 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.8889 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 11.006 | PASS | 3654% | PASS | 36444.8889 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 13.5881 | PASS | 0.3026 | PASS | 202.5857 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 15.5259 | PASS | 504.3% | PASS | 4943.3475 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 26.0273 | PASS | 1.6866 | PASS | 1586.5962 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 26.0273 | PASS | 1.6866 | PASS | 1586.5962 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 21.1105 | PASS | 2.9852 | PASS | 2885.1807 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 24.8225 | PASS | 6.06 | PASS | 5960.0284 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 24.8225 | PASS | 1.7195 | PASS | 1619.4573 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 40.9004 | PASS | 14.7198 | PASS | 14619.8336 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 23.9764 | PASS | 5.4617 | PASS | 5361.6758 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 23.5571 | PASS | 5.4527 | PASS | 5352.734 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 9.4772 | PASS | 0.2605 | PASS | 160.4504 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 9.4772 | PASS | 0.2489 | PASS | 148.9449 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 12.3213 | PASS | 11.7252 | PASS | 11625.2455 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 532997 [OTTRCRK4 138.00] TO BUS 533315 [OTTRCRK3 115.00] TO BUS 533115 [OTTRX1 1 13.800] CKT 1 | 12.3213 | PASS | 11.7252 | PASS | 11625.2455 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 139.0561 | PASS | 13.8683 | PASS | 13768.2639 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 11.3588 | PASS | 9.8907 | PASS | 9790.689 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 25.8394 | PASS | 11.0443 | PASS | 10944.3092 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 20.5301 | PASS | 11.8854 | PASS | 11785.4285 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 5.9509 | FAIL | 23.1992 | PASS | 23099.1629 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 5.9509 | FAIL | 23.1992 | PASS | 23099.1629 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 5.9509 | FAIL | 46.6642 | PASS | 46564.1829 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 11.0064 | PASS | 36.5455 | PASS | 36445.519 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 11.0064 | PASS | 36.5455 | PASS | 36445.519 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 13.559 | PASS | 0.3035 | PASS | 203.4517 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 15.5263 | PASS | 5.0442 | PASS | 4944.1528 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 26.0276 | PASS | 1.6866 | PASS | 1586.5915 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 26.0276 | PASS | 1.6866 | PASS | 1586.5915 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 21.1128 | PASS | 2.9867 | PASS | 2886.7348 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 24.8218 | PASS | 6.0598 | PASS | 5959.7543 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 24.8218 | PASS | 1.7195 | PASS | 1619.4755 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 40.9002 | PASS | 14.7197 | PASS | 14619.7412 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 23.9764 | PASS | 5.4616 | PASS | 5361.5743 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 23.5564 | PASS | 5.4523 | PASS | 5352.281 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 9.4853 | PASS | 0.2604 | PASS | 160.4425 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 9.4853 | PASS | 0.2489 | PASS | 148.9354 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 12.3249 | PASS | 11.7253 | PASS | 11625.3055 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533001 [ALTOONA4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 12.3249 | PASS | 11.7253 | PASS | 11625.3055 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 138.9855 | PASS | 13.8649 | PASS | 13764.8742 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 13.6441 | PASS | 9.8947 | PASS | 9794.7399 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 27.0853 | PASS | 11.0581 | PASS | 10958.0777 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 20.527 | PASS | 11.8831 | PASS | 11783.0824 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 6.0087 | PASS | 23.2032 | PASS | 23103.1752 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 6.0087 | PASS | 23.2032 | PASS | 23103.1752 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 6.0087 | PASS | 46.7295 | PASS | 46629.4811 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 11.0055 | PASS | 36.5441 | PASS | 36444.1381 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 11.0055 | PASS | 36.5441 | PASS | 36444.1381 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 13.5779 | PASS | 0.3038 | PASS | 203.7751 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 15.5249 | PASS | 5.0424 | PASS | 4942.4341 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 26.0273 | PASS | 1.6866 | PASS | 1586.5533 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 26.0273 | PASS | 1.6866 | PASS | 1586.5533 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 21.1093 | PASS | 2.9847 | PASS | 2884.6841 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9037 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4656 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 40.8999 | PASS | 14.7196 | PASS | 14619.609 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 23.9762 | PASS | 5.4614 | PASS | 5361.3925 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 23.5566 | PASS | 5.4523 | PASS | 5352.3307 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 9.4828 | PASS | 0.2604 | PASS | 160.4415 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 9.4828 | PASS | 0.2489 | PASS | 148.934 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 12.32 | PASS | 11.7227 | PASS | 11622.6845 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533006 [TAYLOR 4 138.00] TO BUS 533004 [MONTGOM4 138.00] CKT 1 | 12.32 | PASS | 11.7227 | PASS | 11622.6845 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 138.993 | PASS | 13.8593 | PASS | 13759.2844 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 13.9973 | PASS | 9.8393 | PASS | 9739.2991 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 26.3227 | PASS | 11.096 | PASS | 10996.0418 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 20.5293 | PASS | 11.8799 | PASS | 11779.9012 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 5.9753 | FAIL | 23.2195 | PASS | 23119.4527 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 5.9753 | FAIL | 23.2195 | PASS | 23119.4527 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 5.9753 | FAIL | 46.9628 | PASS | 46862.7804 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 11.0057 | PASS | 36.5444 | PASS | 36444.3758 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 11.0057 | PASS | 36.5444 | PASS | 36444.3758 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 13.562 | PASS | 0.303 | PASS | 202.9601 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 15.5249 | PASS | 5.0418 | PASS | 4941.8249 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 26.0272 | PASS | 1.6866 | PASS | 1586.5761 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 26.0272 | PASS | 1.6866 | PASS | 1586.5761 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 21.111 | PASS | 2.9853 | PASS | 2885.3028 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 24.8221 | PASS | 6.0599 | PASS | 5959.8909 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 24.8221 | PASS | 1.7195 | PASS | 1619.4665 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 40.8999 | PASS | 14.7197 | PASS | 14619.6966 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 23.9762 | PASS | 5.4615 | PASS | 5361.5301 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 23.5564 | PASS | 5.4524 | PASS | 5352.3526 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 9.4831 | PASS | 0.2604 | PASS | 160.4386 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 9.4831 | PASS | 0.2489 | PASS | 148.9303 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 12.319 | PASS | 11.72 | PASS | 11619.9939 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533008 [TV1MNDV4 138.00] TO BUS 533003 [LIBERTY4 138.00] CKT 1 | 12.319 | PASS | 11.72 | PASS | 11619.9939 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 139.0973 | PASS | 13.8726 | PASS | 13772.567 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 3.4979 | FAIL | 9.942 | PASS | 9841.9802 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 25.9664 | PASS | 11.0529 | PASS | 10952.8729 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 20.5292 | PASS | 11.8857 | PASS | 11785.724 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 5.9571 | FAIL | 23.2024 | PASS | 23102.3684 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 5.9571 | FAIL | 23.2024 | PASS | 23102.3684 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 5.9571 | FAIL | 46.4962 | PASS | 46396.2221 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2224 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2224 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 13.5631 | PASS | 0.3033 | PASS | 203.2675 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 15.5266 | PASS | 5.0447 | PASS | 4944.6592 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 26.0276 | PASS | 1.6866 | PASS | 1586.601 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 26.0276 | PASS | 1.6866 | PASS | 1586.601 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 21.1114 | PASS | 2.986 | PASS | 2885.9758 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 24.8221 | PASS | 6.0599 | PASS | 5959.9021 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 24.8221 | PASS | 1.7195 | PASS | 1619.4657 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 40.9004 | PASS | 14.7198 | PASS | 14619.8138 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 23.9765 | PASS | 5.4617 | PASS | 5361.6526 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 23.5567 | PASS | 5.4525 | PASS | 5352.5197 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 9.4868 | PASS | 0.2604 | PASS | 160.4442 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 9.4868 | PASS | 0.2489 | PASS | 148.9376 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 12.3276 | PASS | 11.7274 | PASS | 11627.4384 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533022 [NEOSHON4 138.00] TO BUS 533005 [NEPARSN4 138.00] CKT 1 | 12.3276 | PASS | 11.7274 | PASS | 11627.4384 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 116.6181 | PASS | 13.8403 | PASS | 13740.2739 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 14.1757 | PASS | 9.8594 | PASS | 9759.3749 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 27.2724 | PASS | 11.0772 | PASS | 10977.2132 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 20.5351 | PASS | 11.8825 | PASS | 11782.4664 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 6.0192 | PASS | 23.2129 | PASS | 23112.9171 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 6.0192 | PASS | 23.2129 | PASS | 23112.9171 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 6.0192 | PASS | 46.7801 | PASS | 46680.0574 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 11.0061 | PASS | 36.5453 | PASS | 36445.2557 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 11.0061 | PASS | 36.5453 | PASS | 36445.2557 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 13.5885 | PASS | 0.3025 | PASS | 202.5334 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 15.5253 | PASS | 5.0445 | PASS | 4944.4932 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6263 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6263 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 21.1095 | PASS | 2.9858 | PASS | 2885.8173 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9833 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4602 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9401 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8204 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7381 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 9.4843 | PASS | 0.2604 | PASS | 160.4436 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 9.4843 | PASS | 0.2489 | PASS | 148.9368 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 11.7366 | PASS | 11.7169 | PASS | 11616.852 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533029 [59TH ST4 138.00] TO BUS 533039 [ELPASO 4 138.00] CKT 1 | 11.7366 | PASS | 11.7169 | PASS | 11616.852 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 139.0941 | PASS | 13.871 | PASS | 13771.0247 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8644 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7251 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2791 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2459 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2459 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 6.0206 | PASS | 46.772 | PASS | 46671.974 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1625 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1625 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 13.5932 | PASS | 0.3026 | PASS | 202.5506 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6207 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7641 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 24.8224 | PASS | 6.06 | PASS | 5959.9817 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9401 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8196 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7408 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 9.4879 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 12.3278 | PASS | 11.7268 | PASS | 11626.8329 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z1 | 12.3278 | PASS | 11.7268 | PASS | 11626.8329 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 139.0941 | PASS | 13.871 | PASS | 13771.0247 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 14.1776 | PASS | 9.8589 | PASS | 9758.8644 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 27.2804 | PASS | 11.0767 | PASS | 10976.7251 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 20.5347 | PASS | 11.8823 | PASS | 11782.2791 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 6.0206 | PASS | 23.2122 | PASS | 23112.2459 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 6.0206 | PASS | 23.2122 | PASS | 23112.2459 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 6.0206 | PASS | 46.772 | PASS | 46671.974 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 11.0062 | PASS | 36.5452 | PASS | 36445.1625 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 11.0062 | PASS | 36.5452 | PASS | 36445.1625 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 13.5932 | PASS | 0.3026 | PASS | 202.5506 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 15.5267 | PASS | 5.0446 | PASS | 4944.6207 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 21.1112 | PASS | 2.9858 | PASS | 2885.7641 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 24.8224 | PASS | 6.06 | PASS | 5959.9817 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 40.9012 | PASS | 14.7199 | PASS | 14619.9401 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 23.9769 | PASS | 5.4618 | PASS | 5361.8196 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 23.5573 | PASS | 5.4527 | PASS | 5352.7408 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 9.4879 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 12.3278 | PASS | 11.7268 | PASS | 11626.8329 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533041 [EVANS S4 138.00] CKT Z2 | 12.3278 | PASS | 11.7268 | PASS | 11626.8329 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 138.8785 | PASS | 13.8466 | PASS | 13746.553 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 14.1708 | PASS | 9.8569 | PASS | 9756.8606 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 27.2703 | PASS | 11.0753 | PASS | 10975.2963 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 20.5294 | PASS | 11.8807 | PASS | 11780.7499 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 6.0187 | PASS | 23.2103 | PASS | 23110.3043 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 6.0187 | PASS | 23.2103 | PASS | 23110.3043 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 6.0187 | PASS | 46.7928 | PASS | 46692.8323 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 11.0052 | PASS | 36.5443 | PASS | 36444.2753 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 11.0052 | PASS | 36.5443 | PASS | 36444.2753 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 13.5907 | PASS | 0.3025 | PASS | 202.5408 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 15.5214 | PASS | 5.0434 | PASS | 4943.3703 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6306 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6306 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 21.1029 | PASS | 2.9843 | PASS | 2884.3105 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9779 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4606 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 40.9013 | PASS | 14.72 | PASS | 14619.9729 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 23.9769 | PASS | 5.4619 | PASS | 5361.8534 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 23.5574 | PASS | 5.4528 | PASS | 5352.8432 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 9.4706 | PASS | 0.2605 | PASS | 160.4538 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 9.4706 | PASS | 0.2489 | PASS | 148.9494 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 12.3116 | PASS | 11.7159 | PASS | 11615.8874 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533054 [MAIZE 4 138.00] CKT 1 | 12.3116 | PASS | 11.7159 | PASS | 11615.8874 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 138.2666 | PASS | 13.8798 | PASS | 13779.8001 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 14.1787 | PASS | 9.8594 | PASS | 9759.4141 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 27.2807 | PASS | 11.0773 | PASS | 10977.2692 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 20.5045 | PASS | 11.8807 | PASS | 11780.6769 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 6.0206 | PASS | 23.2129 | PASS | 23112.8562 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 6.0206 | PASS | 23.2129 | PASS | 23112.8562 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 6.0206 | PASS | 46.773 | PASS | 46672.9962 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 11.0065 | PASS | 36.5456 | PASS | 36445.6351 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 11.0065 | PASS | 36.5456 | PASS | 36445.6351 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 13.5922 | PASS | 0.3025 | PASS | 202.5195 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 15.5218 | PASS | 5.0422 | PASS | 4942.2212 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 26.0284 | PASS | 1.6866 | PASS | 1586.6284 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 26.0284 | PASS | 1.6866 | PASS | 1586.6284 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 21.1096 | PASS | 2.9857 | PASS | 2885.7241 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 24.8225 | PASS | 606% | PASS | 5959.9604 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 24.8225 | PASS | 1.7195 | PASS | 1619.4617 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 40.9015 | PASS | 1472% | PASS | 14619.9444 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 23.9771 | PASS | 5.4618 | PASS | 5361.8255 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 23.5574 | PASS | 5.4527 | PASS | 5352.7116 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 9.4865 | PASS | 0.2604 | PASS | 160.4497 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 9.4865 | PASS | 0.2489 | PASS | 148.9446 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 12.3001 | PASS | 11.7309 | PASS | 11630.8602 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 533065 [SG12COL4 138.00] CKT 1 | 12.3001 | PASS | 11.7309 | PASS | 11630.8602 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 139.0474 | PASS | 13.8618 | PASS | 13761.8153 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 14.1774 | PASS | 9.8587 | PASS | 9758.6963 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 27.2811 | PASS | 11.0768 | PASS | 10976.8389 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 20.5336 | PASS | 11.8817 | PASS | 11781.712 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.1524 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.1524 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 6.0206 | PASS | 46.7773 | PASS | 46677.3226 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 11.0067 | PASS | 36.546 | PASS | 36446.0238 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 11.0067 | PASS | 36.546 | PASS | 36446.0238 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 13.595 | PASS | 0.3023 | PASS | 202.3278 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 15.5265 | PASS | 5.044 | PASS | 4944.0206 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 26.0286 | PASS | 1.6867 | PASS | 1586.6772 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 26.0286 | PASS | 1.6867 | PASS | 1586.6772 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 21.1131 | PASS | 2.9868 | PASS | 2886.7792 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 24.8218 | PASS | 6.0597 | PASS | 5959.7278 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 24.8218 | PASS | 1.7195 | PASS | 1619.4772 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 40.9019 | PASS | 14.7202 | PASS | 14620.1587 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 23.9772 | PASS | 5.4621 | PASS | 5362.1045 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 23.5575 | PASS | 5.4529 | PASS | 5352.9315 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 9.4852 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 9.4852 | PASS | 0.2489 | PASS | 148.9363 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 12.3244 | PASS | 11.723 | PASS | 11623.0153 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 589060 [GEN-2017-068138.00] CKT 1 | 12.3244 | PASS | 11.723 | PASS | 11623.0153 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 138.8824 | PASS | 13.8449 | PASS | 13744.8659 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 14.178 | PASS | 9.8589 | PASS | 9758.9043 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 27.2876 | PASS | 11.0785 | PASS | 10978.538 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 20.5297 | PASS | 11.8798 | PASS | 11779.831 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 6.021 | PASS | 23.2129 | PASS | 23112.8824 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 6.021 | PASS | 23.2129 | PASS | 23112.8824 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 6.021 | PASS | 46.7949 | PASS | 46694.8947 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 11.0098 | PASS | 36.5509 | PASS | 36450.9242 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 11.0098 | PASS | 36.5509 | PASS | 36450.9242 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 13.6053 | PASS | 0.301 | PASS | 200.9729 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 15.5267 | PASS | 5.0435 | PASS | 4943.5103 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 26.0311 | PASS | 1.687 | PASS | 1586.956 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 26.0311 | PASS | 1.687 | PASS | 1586.956 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 21.1249 | PASS | 2.9937 | PASS | 2893.6796 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 24.8177 | PASS | 6.058 | PASS | 5957.9529 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 24.8177 | PASS | 1.7196 | PASS | 1619.5955 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 40.9058 | PASS | 14.7213 | PASS | 14621.3292 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 23.9792 | PASS | 5.4637 | PASS | 5363.6536 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 23.5588 | PASS | 5.4539 | PASS | 5353.8759 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 9.4738 | PASS | 0.2604 | PASS | 160.4407 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 9.4738 | PASS | 0.2489 | PASS | 148.9321 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 12.3179 | PASS | 11.7171 | PASS | 11617.1301 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 760641 [GEN-2017-226138.00] CKT 1 | 12.3179 | PASS | 11.7171 | PASS | 11617.1301 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 139.0303 | PASS | 13.8601 | PASS | 13760.0557 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 14.1776 | PASS | 9.8588 | PASS | 9758.7999 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 27.2824 | PASS | 11.0772 | PASS | 10977.1911 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 20.5331 | PASS | 11.8815 | PASS | 11781.4618 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 6.0207 | PASS | 23.2124 | PASS | 23112.3569 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 6.0207 | PASS | 23.2124 | PASS | 23112.3569 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 6.0207 | PASS | 46.7831 | PASS | 46683.0623 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 11.0072 | PASS | 36.547 | PASS | 36446.9592 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 11.0072 | PASS | 36.547 | PASS | 36446.9592 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 13.5968 | PASS | 0.3021 | PASS | 202.0916 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 15.5266 | PASS | 5.0441 | PASS | 4944.113 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 26.0291 | PASS | 1.6867 | PASS | 1586.7274 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 26.0291 | PASS | 1.6867 | PASS | 1586.7274 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 21.1152 | PASS | 2.9881 | PASS | 2888.0977 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 24.8212 | PASS | 6.0595 | PASS | 5959.4717 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 24.8212 | PASS | 1.7195 | PASS | 1619.4943 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 40.9026 | PASS | 14.7204 | PASS | 14620.3719 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 23.9776 | PASS | 5.4624 | PASS | 5362.3844 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 23.5578 | PASS | 5.4531 | PASS | 5353.1158 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 9.4836 | PASS | 0.2604 | PASS | 160.4451 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 9.4836 | PASS | 0.2489 | PASS | 148.9382 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 12.324 | PASS | 11.7226 | PASS | 11622.5525 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533040 [EVANS N4 138.00] TO BUS 762922 [GEN-2018-057138.00] CKT 1 | 12.324 | PASS | 11.7226 | PASS | 11622.5525 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 127.4752 | PASS | 13.882 | PASS | 13781.9906 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 14.1776 | PASS | 9.8588 | PASS | 9758.7913 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 27.2806 | PASS | 11.0767 | PASS | 10976.7036 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 20.5341 | PASS | 11.8821 | PASS | 11782.0662 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.0206 | PASS | 23.2122 | PASS | 23112.1886 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.0206 | PASS | 23.2122 | PASS | 23112.1886 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.0206 | PASS | 46.7718 | PASS | 46671.8098 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1981 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1981 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 13.5935 | PASS | 0.3025 | PASS | 202.5372 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 15.5267 | PASS | 5.0443 | PASS | 4944.3407 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6278 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6278 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 21.1114 | PASS | 2.9857 | PASS | 2885.6801 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 24.8224 | PASS | 6.06 | PASS | 5959.9773 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4606 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9467 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8279 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7433 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 9.4872 | PASS | 0.2604 | PASS | 160.4415 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 9.4872 | PASS | 0.2489 | PASS | 148.9342 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 12.0374 | PASS | 11.7323 | PASS | 11632.2697 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533044 [GILL E 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 12.0374 | PASS | 11.7323 | PASS | 11632.2697 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 138.9219 | PASS | 13.8711 | PASS | 13771.1086 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8714 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7309 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2827 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2524 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2524 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.0206 | PASS | 46.772 | PASS | 46671.9772 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1633 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1633 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 13.5932 | PASS | 0.3026 | PASS | 202.5501 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6246 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7676 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 24.8224 | PASS | 6.06 | PASS | 5959.9818 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9402 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8197 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7409 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9305 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533046 [GILL S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9305 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 138.9416 | PASS | 13.871 | PASS | 13770.9821 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8702 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7302 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2807 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2523 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2523 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 6.0206 | PASS | 46.772 | PASS | 46671.9782 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1638 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1638 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 13.5932 | PASS | 0.3026 | PASS | 202.55 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6245 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7671 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 24.8224 | PASS | 6.06 | PASS | 5959.9817 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9403 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8198 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7409 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 12.3225 | PASS | 11.727 | PASS | 11627.0388 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT Z1 | 12.3225 | PASS | 11.727 | PASS | 11627.0388 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 126.9954 | PASS | 13.8192 | PASS | 13719.1662 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 14.1757 | PASS | 9.8582 | PASS | 9758.1682 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 27.2779 | PASS | 11.0762 | PASS | 10976.2326 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 20.5329 | PASS | 11.8812 | PASS | 11781.2315 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 6.0199 | PASS | 23.2113 | PASS | 23111.3102 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 6.0199 | PASS | 23.2113 | PASS | 23111.3102 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 6.0199 | PASS | 46.7808 | PASS | 46680.8196 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.8835 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.8835 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 13.5935 | PASS | 0.3025 | PASS | 202.4582 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 15.5259 | PASS | 5.0429 | PASS | 4942.9439 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6401 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6401 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 21.1102 | PASS | 2.9847 | PASS | 2884.7157 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9598 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4618 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 40.9014 | PASS | 14.72 | PASS | 14620.0037 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 23.977 | PASS | 5.4619 | PASS | 5361.8983 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 23.5574 | PASS | 5.4528 | PASS | 5352.817 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 9.487 | PASS | 0.2604 | PASS | 160.4368 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 9.487 | PASS | 0.2489 | PASS | 148.9281 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 7.7293 | PASS | 11.7738 | PASS | 11673.8269 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533047 [GILL 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 7.7293 | PASS | 11.7738 | PASS | 11673.8269 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 126.5283 | PASS | 13.8495 | PASS | 13749.5278 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 14.1776 | PASS | 9.8588 | PASS | 9758.8483 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 27.2802 | PASS | 11.0767 | PASS | 10976.6844 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 20.534 | PASS | 11.8824 | PASS | 11782.4059 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2028 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2028 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 6.0205 | PASS | 46.7718 | PASS | 46671.7893 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 11.0061 | PASS | 36.5452 | PASS | 36445.1535 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 11.0061 | PASS | 36.5452 | PASS | 36445.1535 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 13.5931 | PASS | 0.3026 | PASS | 202.5598 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 15.5264 | PASS | 5.0448 | PASS | 4944.7769 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6257 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6257 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 21.1108 | PASS | 2.9858 | PASS | 2885.8288 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9817 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9381 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.817 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7403 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 9.4852 | PASS | 0.2604 | PASS | 160.4456 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 9.4852 | PASS | 0.2489 | PASS | 148.9393 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 12.0152 | PASS | 11.7196 | PASS | 11619.5892 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533051 [INTERST4 138.00] TO BUS 533050 [HOOVERS4 138.00] CKT 1 | 12.0152 | PASS | 11.7196 | PASS | 11619.5892 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 126.8532 | PASS | 13.9109 | PASS | 13810.9171 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 14.1778 | PASS | 9.859 | PASS | 9758.9943 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 27.2805 | PASS | 11.0768 | PASS | 10976.8471 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 20.5338 | PASS | 11.8822 | PASS | 11782.1679 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.3974 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.3974 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 6.0206 | PASS | 46.7724 | PASS | 46672.3943 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1479 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1479 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 13.5932 | PASS | 0.3025 | PASS | 202.5399 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 15.5263 | PASS | 5.0443 | PASS | 4944.3214 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6258 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6258 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 21.1108 | PASS | 2.9856 | PASS | 2885.6382 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9821 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9396 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8183 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7422 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 9.484 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 9.484 | PASS | 24.89% | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 12.0337 | PASS | 11.7429 | PASS | 11642.9087 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533071 [WACO S 4 138.00] TO BUS 533045 [GILL W 4 138.00] CKT 1 | 12.0337 | PASS | 1174% | PASS | 11642.9087 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 127.1286 | PASS | 13.8739 | PASS | 13773.9195 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 14.1773 | PASS | 9.8587 | PASS | 9758.7366 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 27.2798 | PASS | 11.0766 | PASS | 10976.5963 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 20.5334 | PASS | 11.8822 | PASS | 11782.2484 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 6.0205 | PASS | 23.2121 | PASS | 23112.1069 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 6.0205 | PASS | 23.2121 | PASS | 23112.1069 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 6.0205 | PASS | 46.7723 | PASS | 46672.2858 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0767 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0767 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 13.5931 | PASS | 0.3026 | PASS | 202.5677 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 15.5259 | PASS | 5.0446 | PASS | 4944.5714 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6244 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6244 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 21.1101 | PASS | 2.9857 | PASS | 2885.6749 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 24.8224 | PASS | 6.06 | PASS | 5959.9836 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4602 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9339 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 23.9768 | PASS | 5.4618 | PASS | 5361.8103 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7414 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 9.4828 | PASS | 0.2604 | PASS | 160.4466 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 9.4828 | PASS | 0.2489 | PASS | 148.9405 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 12.038 | PASS | 11.7286 | PASS | 11628.5536 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533072 [WACO 4 138.00] TO BUS 533073 [WACO N 4 138.00] CKT Z1 | 12.038 | PASS | 11.7286 | PASS | 11628.5536 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 127.3514 | PASS | 13.8651 | PASS | 13765.0691 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 14.1765 | PASS | 9.8586 | PASS | 9758.6376 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 27.278 | PASS | 11.0764 | PASS | 10976.4454 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 20.5351 | PASS | 11.8824 | PASS | 11782.3776 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 6.0202 | PASS | 23.2121 | PASS | 23112.088 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 6.0202 | PASS | 23.2121 | PASS | 23112.088 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 6.0202 | PASS | 46.782 | PASS | 46682.0091 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0854 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0854 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 13.5917 | PASS | 0.3026 | PASS | 202.6429 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 15.5265 | PASS | 5.0444 | PASS | 4944.4254 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6166 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6166 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7512 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.977 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4607 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.8976 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7646 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.6885 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 9.4892 | PASS | 0.2604 | PASS | 160.441 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 9.4892 | PASS | 0.2489 | PASS | 148.9336 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 6.5726 | PASS | 11.7678 | PASS | 11667.8356 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533075 [VIOLA 4 138.00] TO BUS 771260 [G22-214-TAP 138.00] CKT 1 | 6.5726 | PASS | 11.7678 | PASS | 11667.8356 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 139.1134 | PASS | 13.8707 | PASS | 13770.6998 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 14.1772 | PASS | 9.8587 | PASS | 9758.6569 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 27.2794 | PASS | 11.0765 | PASS | 10976.4677 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 20.5324 | PASS | 11.8858 | PASS | 11785.8181 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 6.0204 | PASS | 23.212 | PASS | 23112.0114 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 6.0204 | PASS | 23.212 | PASS | 23112.0114 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 6.0204 | PASS | 46.7714 | PASS | 46671.3837 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.0224 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.0224 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 13.5928 | PASS | 0.3026 | PASS | 202.6095 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 15.5265 | PASS | 5.0444 | PASS | 4944.3582 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6178 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6178 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 21.1108 | PASS | 2.9855 | PASS | 2885.5202 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 24.8226 | PASS | 6.06 | PASS | 5960.0428 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 24.8226 | PASS | 1.7195 | PASS | 1619.4563 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.9038 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7772 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7229 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 9.4869 | PASS | 0.2604 | PASS | 160.4441 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 9.4869 | PASS | 0.2489 | PASS | 148.9374 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 12.3278 | PASS | 11.7266 | PASS | 11626.5602 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533170 [OSAGE 3 115.00] CKT 1 | 12.3278 | PASS | 11.7266 | PASS | 11626.5602 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 139.077 | PASS | 13.8709 | PASS | 13770.8556 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 14.1769 | PASS | 9.8589 | PASS | 9758.8694 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 27.2795 | PASS | 11.0767 | PASS | 10976.7294 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 18.5695 | PASS | 11.9033 | PASS | 11803.2546 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.3163 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.3163 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 6.0205 | PASS | 46.772 | PASS | 46671.9684 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 11.006 | PASS | 36.545 | PASS | 36445.0029 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 11.006 | PASS | 36.545 | PASS | 36445.0029 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 13.593 | PASS | 0.3025 | PASS | 202.5499 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 15.526 | PASS | 5.0444 | PASS | 4944.4154 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 26.0268 | PASS | 1.6865 | PASS | 1586.5446 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 26.0268 | PASS | 1.6865 | PASS | 1586.5446 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 21.1097 | PASS | 2.9853 | PASS | 2885.308 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.9047 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4655 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 40.8997 | PASS | 14.7196 | PASS | 14619.6242 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 23.976 | PASS | 5.4614 | PASS | 5361.3517 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 23.5567 | PASS | 5.4524 | PASS | 5352.3907 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 9.4629 | PASS | 0.2605 | PASS | 160.463 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 9.4629 | PASS | 0.249 | PASS | 148.9607 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 12.3261 | PASS | 11.7267 | PASS | 11626.6707 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533171 [OSAGE J3 115.00] TO BUS 533173 [SCRANTN3 115.00] CKT 1 | 12.3261 | PASS | 11.7267 | PASS | 11626.6707 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 139.103 | PASS | 13.8713 | PASS | 13771.3378 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 14.1759 | PASS | 9.8591 | PASS | 9759.0839 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 27.2791 | PASS | 11.0769 | PASS | 10976.8695 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 19.8475 | PASS | 11.8815 | PASS | 11781.4655 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 6.0204 | PASS | 23.2122 | PASS | 23112.2468 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 6.0204 | PASS | 23.2122 | PASS | 23112.2468 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 6.0204 | PASS | 46.7719 | PASS | 46671.9128 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2148 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2148 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5542 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 15.5263 | PASS | 5.0447 | PASS | 4944.7022 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6202 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6202 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 21.1109 | PASS | 2.9859 | PASS | 2885.8984 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9871 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.46 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9166 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7878 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7241 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 9.4851 | PASS | 0.2604 | PASS | 160.4473 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 9.4851 | PASS | 0.2489 | PASS | 148.9414 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 12.3277 | PASS | 11.7269 | PASS | 11626.9262 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533301 [EAST ST3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 12.3277 | PASS | 11.7269 | PASS | 11626.9262 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 139.0959 | PASS | 13.8731 | PASS | 13773.1359 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 14.1781 | PASS | 9.8594 | PASS | 9759.4331 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 27.2803 | PASS | 11.077 | PASS | 10976.9946 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 2.2457 | FAIL | 12.0046 | PASS | 11904.5868 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 6.0204 | PASS | 23.2122 | PASS | 23112.2405 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 6.0204 | PASS | 23.2122 | PASS | 23112.2405 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 6.0204 | PASS | 46.7714 | PASS | 46671.3524 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 11.0064 | PASS | 36.5456 | PASS | 36445.588 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 11.0064 | PASS | 36.5456 | PASS | 36445.588 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 13.5931 | PASS | 0.3025 | PASS | 202.5218 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 15.5264 | PASS | 5.0452 | PASS | 4945.195 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 26.0267 | PASS | 1.6865 | PASS | 1586.5116 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 26.0267 | PASS | 1.6865 | PASS | 1586.5116 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 21.1121 | PASS | 2.9868 | PASS | 2886.8256 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.955 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4622 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 40.8995 | PASS | 14.7195 | PASS | 14619.5263 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 23.9759 | PASS | 5.4612 | PASS | 5361.2024 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 23.5568 | PASS | 5.4525 | PASS | 5352.463 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 9.4661 | PASS | 0.2605 | PASS | 160.4692 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 9.4661 | PASS | 0.249 | PASS | 148.9687 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 12.3277 | PASS | 11.728 | PASS | 11628.0316 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533304 [LANG 3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 12.3277 | PASS | 11.728 | PASS | 11628.0316 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 139.0726 | PASS | 13.8707 | PASS | 13770.6708 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 14.1769 | PASS | 9.8589 | PASS | 9758.8512 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 27.2794 | PASS | 11.0767 | PASS | 10976.7247 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 18.5582 | PASS | 11.9081 | PASS | 11808.1423 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.3411 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 6.0205 | PASS | 23.2123 | PASS | 23112.3411 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 6.0205 | PASS | 46.7718 | PASS | 46671.8442 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.9354 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.9354 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 13.5929 | PASS | 0.3025 | PASS | 202.5487 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 15.5258 | PASS | 5.0443 | PASS | 4944.3149 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 26.0266 | PASS | 1.6865 | PASS | 1586.5038 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 26.0266 | PASS | 1.6865 | PASS | 1586.5038 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 21.1093 | PASS | 2.9851 | PASS | 2885.1084 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 24.8222 | PASS | 6.0599 | PASS | 5959.8665 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 24.8222 | PASS | 1.7195 | PASS | 1619.468 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 40.8993 | PASS | 14.7195 | PASS | 14619.4669 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 23.9758 | PASS | 5.4611 | PASS | 5361.1198 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 23.5565 | PASS | 5.4522 | PASS | 5352.2206 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 9.4618 | PASS | 0.2605 | PASS | 160.4657 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 9.4618 | PASS | 0.249 | PASS | 148.964 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 12.3258 | PASS | 11.7266 | PASS | 11626.5585 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533306 [READING3 115.00] TO BUS 767120 [G22-007-TAP 115.00] CKT 1 | 12.3258 | PASS | 11.7266 | PASS | 11626.5585 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 139.0993 | PASS | 13.8707 | PASS | 13770.661 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 14.1748 | PASS | 9.8587 | PASS | 9758.7316 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 27.2786 | PASS | 11.0768 | PASS | 10976.7634 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 19.7566 | PASS | 11.8867 | PASS | 11786.694 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 6.0204 | PASS | 23.2121 | PASS | 23112.1294 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 6.0204 | PASS | 23.2121 | PASS | 23112.1294 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 6.0204 | PASS | 46.7724 | PASS | 46672.4083 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2286 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2286 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5609 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 15.5262 | PASS | 5.0445 | PASS | 4944.4602 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6137 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6137 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 21.1109 | PASS | 2.9859 | PASS | 2885.8512 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.984 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4601 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 40.9009 | PASS | 14.7199 | PASS | 14619.8914 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 23.9767 | PASS | 5.4618 | PASS | 5361.752 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7019 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 9.484 | PASS | 0.2604 | PASS | 160.448 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 9.484 | PASS | 0.2489 | PASS | 148.9422 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 12.3274 | PASS | 11.7266 | PASS | 11626.5868 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533307 [PRAIRIE3 115.00] TO BUS 533309 [WEMPORI3 115.00] CKT 1 | 12.3274 | PASS | 11.7266 | PASS | 11626.5868 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 139.1155 | PASS | 13.8708 | PASS | 13770.8147 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 14.176 | PASS | 9.8576 | PASS | 9757.6308 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 27.2763 | PASS | 11.0735 | PASS | 10973.4935 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 20.5345 | PASS | 11.8822 | PASS | 11782.2435 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 6.0201 | PASS | 23.2108 | PASS | 23110.8002 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 6.0201 | PASS | 23.2108 | PASS | 23110.8002 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 6.0201 | PASS | 46.7704 | PASS | 46670.3731 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.118 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.118 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 13.5922 | PASS | 0.3027 | PASS | 202.7178 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.508 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6213 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6213 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 21.1111 | PASS | 2.9857 | PASS | 2885.7161 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9605 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4618 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.9163 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7913 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7127 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 9.4877 | PASS | 0.2604 | PASS | 160.4433 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 9.4877 | PASS | 0.2489 | PASS | 148.9364 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 12.328 | PASS | 11.7267 | PASS | 11626.6708 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533640 [MCKEE 2 69.000] CKT 1 | 12.328 | PASS | 11.7267 | PASS | 11626.6708 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 139.1199 | PASS | 13.8712 | PASS | 13771.204 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 14.16 | PASS | 9.8503 | PASS | 9750.3373 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 27.1938 | PASS | 11.0737 | PASS | 10973.7201 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 20.5343 | PASS | 1188% | PASS | 11782.135 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 6.0181 | PASS | 23.2114 | PASS | 23111.3996 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 6.0181 | PASS | 2321% | PASS | 23111.3996 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 6.0181 | PASS | 46.7625 | PASS | 46662.5033 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.2823 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.2823 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 13.5943 | PASS | 0.3024 | PASS | 202.4223 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6173 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.6452 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 26.0279 | PASS | 1.6866 | PASS | 1586.6452 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 21.1117 | PASS | 2.986 | PASS | 2886.033 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5960.0002 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4591 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 40.901 | PASS | 14.72 | PASS | 14620.0207 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 23.9767 | PASS | 5.4619 | PASS | 5361.9399 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 23.5571 | PASS | 5.4528 | PASS | 5352.8257 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 9.4877 | PASS | 0.2604 | PASS | 160.4432 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 9.4877 | PASS | 0.2489 | PASS | 148.9363 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9273 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533639 [MARMATN2 69.000] TO BUS 533647 [UN1ELSM2 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9273 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 139.0662 | PASS | 13.8677 | PASS | 13767.6629 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 14.1324 | PASS | 9.8497 | PASS | 9749.7089 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 27.254 | PASS | 11.0755 | PASS | 10975.5047 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 20.5343 | PASS | 11.8821 | PASS | 11782.0928 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 6.0193 | PASS | 23.2098 | PASS | 23109.809 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 6.0193 | PASS | 23.2098 | PASS | 23109.809 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 6.0193 | PASS | 46.774 | PASS | 46673.9972 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.9107 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.9107 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 13.5661 | PASS | 0.3036 | PASS | 203.5615 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 15.5262 | PASS | 5.044 | PASS | 4944.0311 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 26.0277 | PASS | 1.6866 | PASS | 1586.5784 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 26.0277 | PASS | 1.6866 | PASS | 1586.5784 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 21.1105 | PASS | 2.9854 | PASS | 2885.3528 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 24.8222 | PASS | 6.0599 | PASS | 5959.8754 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 24.8222 | PASS | 1.7195 | PASS | 1619.4675 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 40.9004 | PASS | 14.7197 | PASS | 14619.7241 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 23.9765 | PASS | 5.4615 | PASS | 5361.5104 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 23.5569 | PASS | 5.4525 | PASS | 5352.4539 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 9.4865 | PASS | 0.2604 | PASS | 160.4428 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 9.4865 | PASS | 0.2489 | PASS | 148.9357 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 12.325 | PASS | 11.725 | PASS | 11624.9847 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533626 [BURLJCT2 69.000] CKT 1 | 12.325 | PASS | 11.725 | PASS | 11624.9847 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 139.1204 | PASS | 13.8712 | PASS | 13771.2446 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8696 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 27.2803 | PASS | 11.0767 | PASS | 10976.7248 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.282 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2481 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2481 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 6.0206 | PASS | 46.7719 | PASS | 46671.9271 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1632 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1632 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5524 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6237 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.626 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.626 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.765 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9825 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9391 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8184 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7396 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9225 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533653 [WOLFCRK2 69.000] TO BUS 533629 [CC2SHAR2 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9225 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 139.1167 | PASS | 13.8713 | PASS | 13771.2737 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 14.1787 | PASS | 9.8649 | PASS | 9764.8558 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 27.2764 | PASS | 11.0777 | PASS | 10977.7116 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 20.5351 | PASS | 11.8825 | PASS | 11782.5076 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 6.0203 | PASS | 23.2127 | PASS | 23112.704 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 6.0203 | PASS | 23.2127 | PASS | 23112.704 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 6.0203 | PASS | 46.7537 | PASS | 46653.6634 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.0346 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.0346 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 13.5926 | PASS | 0.3026 | PASS | 202.579 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.5371 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6087 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6087 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 21.1108 | PASS | 2.9855 | PASS | 2885.5244 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 24.8226 | PASS | 6.0601 | PASS | 5960.0651 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 24.8226 | PASS | 1.7195 | PASS | 1619.4548 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 40.9009 | PASS | 14.7199 | PASS | 14619.8635 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 23.9767 | PASS | 5.4617 | PASS | 5361.7219 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 23.5571 | PASS | 5.4527 | PASS | 5352.6594 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4436 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9368 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 12.3281 | PASS | 11.7269 | PASS | 11626.8843 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533700 [NEODJCT2 69.000] CKT 1 | 12.3281 | PASS | 11.7269 | PASS | 11626.8843 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 139.1192 | PASS | 13.8712 | PASS | 13771.2364 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 14.178 | PASS | 9.8604 | PASS | 9760.4445 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 27.2792 | PASS | 11.0769 | PASS | 10976.9361 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 20.5348 | PASS | 11.8823 | PASS | 11782.3328 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 6.0205 | PASS | 23.2123 | PASS | 23112.3491 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 6.0205 | PASS | 23.2123 | PASS | 23112.3491 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 6.0205 | PASS | 46.7662 | PASS | 46666.2461 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1244 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1244 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 13.593 | PASS | 0.3026 | PASS | 202.5611 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 15.5267 | PASS | 5.0446 | PASS | 4944.5965 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6209 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6209 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 21.1111 | PASS | 2.9857 | PASS | 2885.6937 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 24.8225 | PASS | 6.06 | PASS | 5960.0066 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 24.8225 | PASS | 1.7195 | PASS | 1619.4587 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9171 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7903 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7156 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 9.4879 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 12.3283 | PASS | 11.7269 | PASS | 11626.9037 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533673 [ALTOO E2 69.000] TO BUS 533706 [RA5HIPR2 69.000] CKT Z1 | 12.3283 | PASS | 11.7269 | PASS | 11626.9037 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 139.1178 | PASS | 13.8714 | PASS | 13771.445 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 14.1781 | PASS | 9.8662 | PASS | 9766.1748 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 27.276 | PASS | 11.0783 | PASS | 10978.3287 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 20.5354 | PASS | 11.8826 | PASS | 11782.6281 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 6.0203 | PASS | 23.213 | PASS | 23112.976 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 6.0203 | PASS | 23.213 | PASS | 23112.976 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 6.0203 | PASS | 46.7565 | PASS | 46656.4585 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.0459 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.0459 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 13.5926 | PASS | 0.3026 | PASS | 202.5599 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 15.5266 | PASS | 5.0446 | PASS | 4944.5603 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6105 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6105 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 21.1108 | PASS | 2.9855 | PASS | 2885.547 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 24.8226 | PASS | 6.0601 | PASS | 5960.0623 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 24.8226 | PASS | 1.7195 | PASS | 1619.455 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 40.9009 | PASS | 14.7199 | PASS | 14619.8712 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 23.9767 | PASS | 5.4617 | PASS | 5361.732 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.6685 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4436 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9369 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 12.3282 | PASS | 11.727 | PASS | 11626.9678 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533674 [ALTOO W2 69.000] TO BUS 533705 [STUDBKR2 69.000] CKT 1 | 12.3282 | PASS | 11.727 | PASS | 11626.9678 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 139.1202 | PASS | 13.8712 | PASS | 13771.221 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 14.1773 | PASS | 9.858 | PASS | 9758.0481 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 27.2818 | PASS | 11.0758 | PASS | 10975.8111 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2729 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 6.0206 | PASS | 23.2119 | PASS | 23111.8573 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 6.0206 | PASS | 23.2119 | PASS | 23111.8573 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 6.0206 | PASS | 46.7712 | PASS | 46671.1668 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1663 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1663 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5704 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6253 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7743 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.975 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4607 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9405 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8189 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7393 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9136 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533768 [NEOSHON2 69.000] TO BUS 533696 [LABETTS2 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9136 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 139.1081 | PASS | 13.871 | PASS | 13770.952 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 14.1043 | PASS | 9.8607 | PASS | 9760.7145 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 27.1031 | PASS | 11.0794 | PASS | 10979.399 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 20.5343 | PASS | 11.8822 | PASS | 11782.209 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 6.0114 | PASS | 23.2135 | PASS | 23113.491 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 6.0114 | PASS | 23.2135 | PASS | 23113.491 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 6.0114 | PASS | 46.814 | PASS | 46713.9933 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1063 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1063 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 13.5877 | PASS | 0.3026 | PASS | 202.6011 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 15.5266 | PASS | 5.0446 | PASS | 4944.557 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6168 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6168 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 21.111 | PASS | 2.9857 | PASS | 2885.6695 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9512 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4625 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.8984 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7606 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.6922 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 9.4877 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 9.4877 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 12.3277 | PASS | 11.7267 | PASS | 11626.7491 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 532926 [BAKER 2 69.000] CKT 1 | 12.3277 | PASS | 11.7267 | PASS | 11626.7491 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 139.1205 | PASS | 13.8712 | PASS | 13771.1938 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 14.177 | PASS | 9.8572 | PASS | 9757.1911 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 27.2837 | PASS | 11.0748 | PASS | 10974.8493 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2637 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 6.0206 | PASS | 23.2114 | PASS | 23111.4403 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 6.0206 | PASS | 23.2114 | PASS | 23111.4403 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 6.0206 | PASS | 46.7713 | PASS | 46671.2832 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1717 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1717 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 13.5933 | PASS | 0.3026 | PASS | 202.5906 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6273 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6266 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6266 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7849 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9674 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4612 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9414 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8207 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7398 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.903 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533703 [ORDNJCT2 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.903 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 139.1048 | PASS | 13.8708 | PASS | 13770.7904 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 14.0902 | PASS | 9.8574 | PASS | 9757.358 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 27.071 | PASS | 11.076 | PASS | 10976.0309 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 20.5342 | PASS | 11.8822 | PASS | 11782.1572 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 6.0093 | PASS | 23.212 | PASS | 23111.9904 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 6.0093 | PASS | 23.212 | PASS | 23111.9904 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 6.0093 | PASS | 46.7652 | PASS | 46665.2467 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1065 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1065 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 13.5865 | PASS | 30.27% | PASS | 202.6726 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.5482 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 26.028 | PASS | 168.7% | PASS | 1586.6144 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 26.028 | PASS | 1.6866 | PASS | 1586.6144 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 21.111 | PASS | 2.9857 | PASS | 2885.6611 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9579 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4619 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 40.901 | PASS | 14.7199 | PASS | 14619.8877 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 23.9768 | PASS | 5.4617 | PASS | 5361.7453 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.6774 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 9.4876 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 9.4876 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 12.3276 | PASS | 11.7267 | PASS | 11626.6787 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533778 [NEOSHOS2 69.000] TO BUS 533758 [CRAWFOR2 69.000] CKT 1 | 12.3276 | PASS | 11.7267 | PASS | 11626.6787 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 137.5739 | PASS | 13.8737 | PASS | 13773.6814 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 14.1774 | PASS | 9.8588 | PASS | 9758.7532 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 27.2802 | PASS | 11.0766 | PASS | 10976.6445 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 20.5345 | PASS | 11.8822 | PASS | 11782.1558 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.131 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.131 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 6.0205 | PASS | 46.7725 | PASS | 46672.4925 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 11.0062 | PASS | 36.5451 | PASS | 36445.1457 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 11.0062 | PASS | 36.5451 | PASS | 36445.1457 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.5488 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.4922 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6268 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6268 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 21.1112 | PASS | 2.9857 | PASS | 2885.6959 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9795 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4605 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9427 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8227 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7439 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4428 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9358 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 12.2905 | PASS | 11.728 | PASS | 11627.9516 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533798 [GILLJCT2 69.000] CKT 1 | 12.2905 | PASS | 11.728 | PASS | 11627.9516 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 137.9531 | PASS | 13.873 | PASS | 13773.0488 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 14.1774 | PASS | 9.8588 | PASS | 9758.7563 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 27.2802 | PASS | 11.0766 | PASS | 10976.6445 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 20.5345 | PASS | 11.8822 | PASS | 11782.1695 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.1318 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.1318 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 6.0205 | PASS | 46.7725 | PASS | 46672.4667 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 11.0062 | PASS | 36.5451 | PASS | 36445.1471 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 11.0062 | PASS | 36.5451 | PASS | 36445.1471 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.5497 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.5102 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6267 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6267 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 21.1112 | PASS | 2.9857 | PASS | 2885.7038 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9793 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4605 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9426 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8226 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7436 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.443 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.936 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 12.2998 | PASS | 11.7277 | PASS | 11627.6656 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533795 [GILL E 2 69.000] TO BUS 533813 [MACARTH2 69.000] CKT 1 | 12.2998 | PASS | 11.7277 | PASS | 11627.6656 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 137.4025 | PASS | 13.8707 | PASS | 13770.6572 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 14.1764 | PASS | 9.8584 | PASS | 9758.4451 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 27.2778 | PASS | 11.0763 | PASS | 10976.3175 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 20.5335 | PASS | 11.8822 | PASS | 11782.2356 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 6.0202 | PASS | 23.2119 | PASS | 23111.8976 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 6.0202 | PASS | 23.2119 | PASS | 23111.8976 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 6.0202 | PASS | 46.7716 | PASS | 46671.5862 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.9497 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 11.006 | PASS | 36.5449 | PASS | 36444.9497 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 13.5918 | PASS | 0.3026 | PASS | 202.6317 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 15.5257 | PASS | 5.0443 | PASS | 4944.3052 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6207 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6207 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 21.1096 | PASS | 2.9855 | PASS | 2885.502 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9787 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4605 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9175 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7885 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7216 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 9.4838 | PASS | 0.2604 | PASS | 160.4454 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 9.4838 | PASS | 0.2489 | PASS | 148.939 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 12.2878 | PASS | 11.726 | PASS | 11626.0246 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533802 [HAYSVJS2 69.000] CKT 1 | 12.2878 | PASS | 11.726 | PASS | 11626.0246 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 137.8885 | PASS | 13.8754 | PASS | 13775.4476 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 14.1772 | PASS | 9.8586 | PASS | 9758.6461 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 27.2799 | PASS | 11.0765 | PASS | 10976.5385 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 20.5343 | PASS | 11.8821 | PASS | 11782.1042 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 6.0205 | PASS | 23.212 | PASS | 23111.9925 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 6.0205 | PASS | 23.212 | PASS | 23111.9925 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 6.0205 | PASS | 46.7725 | PASS | 46672.4999 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1318 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1318 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 13.5933 | PASS | 0.3026 | PASS | 202.5551 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 15.5265 | PASS | 5.0444 | PASS | 4944.4449 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6267 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6267 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 21.1111 | PASS | 2.9857 | PASS | 2885.6624 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9777 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4606 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.943 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.822 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7441 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4428 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9358 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 12.298 | PASS | 11.7285 | PASS | 11628.5195 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533804 [HAYSVJN2 69.000] CKT 1 | 12.298 | PASS | 11.7285 | PASS | 11628.5195 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 138.8397 | PASS | 13.8981 | PASS | 13798.1235 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 14.1779 | PASS | 9.8593 | PASS | 9759.2891 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 27.2785 | PASS | 11.0768 | PASS | 10976.8173 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 20.5347 | PASS | 11.8829 | PASS | 11782.9074 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 6.0204 | PASS | 23.2126 | PASS | 23112.6095 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 6.0204 | PASS | 23.2126 | PASS | 23112.6095 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 6.0204 | PASS | 46.7697 | PASS | 46669.7016 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 11.0055 | PASS | 36.5444 | PASS | 36444.4274 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 11.0055 | PASS | 36.5444 | PASS | 36444.4274 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 13.5901 | PASS | 0.3028 | PASS | 202.7797 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 15.5256 | PASS | 5.0451 | PASS | 4945.1342 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 26.0276 | PASS | 1.6866 | PASS | 1586.5701 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 26.0276 | PASS | 1.6866 | PASS | 1586.5701 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 21.1074 | PASS | 2.9848 | PASS | 2884.7648 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 24.823 | PASS | 6.0602 | PASS | 5960.2398 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 24.823 | PASS | 1.7194 | PASS | 1619.4432 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 40.9003 | PASS | 14.7197 | PASS | 14619.6976 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 23.9764 | PASS | 5.4615 | PASS | 5361.5036 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 23.5569 | PASS | 5.4525 | PASS | 5352.5179 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 9.4864 | PASS | 0.2605 | PASS | 160.4511 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 9.4864 | PASS | 0.2489 | PASS | 148.9463 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 12.3198 | PASS | 11.7378 | PASS | 11637.7803 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533850 [VULCAN 2 69.000] CKT 1 | 12.3198 | PASS | 11.7378 | PASS | 11637.7803 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 138.7773 | PASS | 13.8728 | PASS | 13772.8316 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 14.1776 | PASS | 9.8588 | PASS | 9758.8161 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 27.2803 | PASS | 11.0767 | PASS | 10976.6939 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 20.5345 | PASS | 11.8822 | PASS | 11782.1644 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.201 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.201 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 6.0205 | PASS | 46.7716 | PASS | 46671.6131 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1708 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1708 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.5469 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 15.5267 | PASS | 5.0444 | PASS | 4944.4007 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6271 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6271 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 21.1114 | PASS | 2.9857 | PASS | 2885.7009 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9747 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4608 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9444 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8244 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7428 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 9.4881 | PASS | 0.2604 | PASS | 160.4421 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 9.4881 | PASS | 0.2489 | PASS | 148.9349 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 12.3201 | PASS | 11.7275 | PASS | 11627.4813 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 533796 [GILL W 2 69.000] TO BUS 533851 [VULCTP 2 69.000] CKT 1 | 12.3201 | PASS | 11.7275 | PASS | 11627.4813 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 138.8196 | PASS | 13.8714 | PASS | 13771.3671 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8676 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 27.2801 | PASS | 11.0767 | PASS | 10976.7244 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2792 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2483 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2483 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 6.0205 | PASS | 46.7726 | PASS | 46672.5558 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 11.0057 | PASS | 36.5455 | PASS | 36445.4873 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 11.0057 | PASS | 36.5455 | PASS | 36445.4873 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5535 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 15.5221 | PASS | 5.0441 | PASS | 4944.0594 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6244 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6244 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 21.1053 | PASS | 2.9858 | PASS | 2885.7757 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.98 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9332 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8104 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7324 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 9.4877 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 9.4877 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 12.2804 | PASS | 11.7272 | PASS | 11627.2122 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539003 [CLDWELL4 138.00] CKT 1 | 12.2804 | PASS | 11.7272 | PASS | 11627.2122 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 139.1091 | PASS | 13.8721 | PASS | 13772.1161 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8888 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 27.2802 | PASS | 11.0767 | PASS | 10976.7235 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.3138 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2603 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2603 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 6.0206 | PASS | 46.7718 | PASS | 46671.8403 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0895 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0895 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5698 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 15.5266 | PASS | 5.0447 | PASS | 4944.6743 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6213 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6213 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 21.1109 | PASS | 2.9857 | PASS | 2885.6662 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 24.8225 | PASS | 6.06 | PASS | 5960.0061 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 24.8225 | PASS | 1.7195 | PASS | 1619.4587 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9191 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.7915 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7221 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.444 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9374 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 12.3276 | PASS | 11.7278 | PASS | 11627.8035 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539008 [MILAN_GOAB 138.00] TO BUS 539676 [MILAN 4 138.00] CKT 1 | 12.3276 | PASS | 11.7278 | PASS | 11627.8035 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 138.3974 | PASS | 13.872 | PASS | 13772.0102 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 14.1774 | PASS | 9.8589 | PASS | 9758.8897 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 27.2796 | PASS | 11.0767 | PASS | 10976.746 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2976 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 6.0204 | PASS | 23.2123 | PASS | 23112.2751 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 6.0204 | PASS | 23.2123 | PASS | 23112.2751 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 6.0204 | PASS | 46.7728 | PASS | 46672.764 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 11.0048 | PASS | 36.5454 | PASS | 36445.4021 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 11.0048 | PASS | 36.5454 | PASS | 36445.4021 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 13.5927 | PASS | 0.3026 | PASS | 202.5522 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 15.5148 | PASS | 5.0443 | PASS | 4944.3263 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6244 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6244 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 21.0954 | PASS | 2.9857 | PASS | 2885.7072 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9811 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 24.8224 | PASS | 171.9% | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9329 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 23.9768 | PASS | 546.2% | PASS | 5361.8101 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7318 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 9.4873 | PASS | 0.2604 | PASS | 160.4441 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 9.4873 | PASS | 0.2489 | PASS | 148.9374 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 12.2153 | PASS | 11.7284 | PASS | 11628.3556 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539009 [CONWAY 138.00] TO BUS 539675 [MILANTP4 138.00] CKT 1 | 12.2153 | PASS | 11.7284 | PASS | 11628.3556 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 139.1185 | PASS | 13.8712 | PASS | 13771.2302 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8771 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7389 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2757 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2587 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2587 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46672.0442 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 11.0014 | PASS | 36.5432 | PASS | 36443.1835 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 11.0014 | PASS | 36.5432 | PASS | 36443.1835 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 13.5932 | PASS | 0.3025 | PASS | 202.5467 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 15.5193 | PASS | 5.0436 | PASS | 4943.6255 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6309 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6309 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 21.1078 | PASS | 2.9851 | PASS | 2885.0908 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9807 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 40.9012 | PASS | 14.72 | PASS | 14619.959 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8438 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7593 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.9203 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 530601 [HEIZER 3 115.00] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.9203 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 139.1206 | PASS | 13.8707 | PASS | 13770.749 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 14.1779 | PASS | 9.859 | PASS | 9758.9761 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 27.2808 | PASS | 11.0769 | PASS | 10976.853 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 20.534 | PASS | 11.882 | PASS | 11782.05 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.3543 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.3543 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 6.0206 | PASS | 46.7722 | PASS | 46672.2136 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 11.0028 | PASS | 36.5422 | PASS | 36442.1827 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 11.0028 | PASS | 36.5422 | PASS | 36442.1827 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 13.5934 | PASS | 0.3025 | PASS | 202.5243 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 15.3548 | PASS | 5.0488 | PASS | 4948.8324 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6411 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6411 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 21.0559 | PASS | 2.9828 | PASS | 2882.8306 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9633 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4615 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 40.9013 | PASS | 14.72 | PASS | 14620.0002 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 23.9769 | PASS | 5.4619 | PASS | 5361.8954 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7868 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 9.4883 | PASS | 0.2604 | PASS | 160.4429 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 9.4883 | PASS | 0.2489 | PASS | 148.936 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 12.3281 | PASS | 11.7266 | PASS | 11626.6209 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539642 [ELLSWTP3 115.00] CKT 1 | 12.3281 | PASS | 11.7266 | PASS | 11626.6209 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 139.1175 | PASS | 13.8709 | PASS | 13770.8911 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 14.1776 | PASS | 9.8588 | PASS | 9758.8314 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 27.2802 | PASS | 11.0767 | PASS | 10976.6949 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 20.5346 | PASS | 11.8822 | PASS | 11782.2351 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2114 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2114 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 6.0205 | PASS | 46.7719 | PASS | 46671.9254 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 11.0055 | PASS | 36.5442 | PASS | 36444.1558 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 11.0055 | PASS | 36.5442 | PASS | 36444.1558 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5507 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 15.5069 | PASS | 5.0433 | PASS | 4943.2646 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6299 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6299 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 21.102 | PASS | 2.9845 | PASS | 2884.4686 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9805 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 40.9012 | PASS | 14.72 | PASS | 14619.956 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8388 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7591 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4432 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9363 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 12.3281 | PASS | 11.7267 | PASS | 11626.6971 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539666 [GBENDTP3 115.00] CKT 1 | 12.3281 | PASS | 11.7267 | PASS | 11626.6971 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 139.1205 | PASS | 13.8713 | PASS | 13771.2534 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8701 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7307 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2828 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2525 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2525 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46671.9724 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5502 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6259 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6262 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.768 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9818 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9402 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8197 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7408 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9273 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539677 [GRTBEND1 13.800] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9273 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 139.1192 | PASS | 13.8709 | PASS | 13770.8977 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 14.1776 | PASS | 9.8588 | PASS | 9758.8423 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 27.2803 | PASS | 11.0767 | PASS | 10976.7067 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 20.5346 | PASS | 11.8822 | PASS | 11782.2272 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2238 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2238 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 6.0205 | PASS | 46.7719 | PASS | 46671.9398 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 11.0058 | PASS | 36.5444 | PASS | 36444.3782 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 11.0058 | PASS | 36.5444 | PASS | 36444.3782 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 13.5932 | PASS | 0.3025 | PASS | 202.5489 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 15.5185 | PASS | 5.042 | PASS | 4941.9673 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6283 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6283 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 21.1073 | PASS | 2.9844 | PASS | 2884.4298 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9781 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4606 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9495 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8307 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7509 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4431 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9362 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 12.3282 | PASS | 11.7267 | PASS | 11626.6972 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539681 [N-GBEND3 115.00] CKT 1 | 12.3282 | PASS | 11.7267 | PASS | 11626.6972 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 139.1173 | PASS | 13.8711 | PASS | 13771.0731 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 14.1776 | PASS | 9.8588 | PASS | 9758.8267 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 27.2801 | PASS | 11.0767 | PASS | 10976.6689 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2648 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1968 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1968 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 6.0205 | PASS | 46.7718 | PASS | 46671.8432 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 11.0059 | PASS | 36.5445 | PASS | 36444.5237 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 11.0059 | PASS | 36.5445 | PASS | 36444.5237 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 13.5931 | PASS | 0.3026 | PASS | 202.5704 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 15.5254 | PASS | 5.0441 | PASS | 4944.0512 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6243 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6243 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 21.1095 | PASS | 2.985 | PASS | 2884.9579 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 24.8225 | PASS | 6.06 | PASS | 5960.0042 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 24.8225 | PASS | 1.7195 | PASS | 1619.4589 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.932 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.808 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7388 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 12.3281 | PASS | 11.7268 | PASS | 11626.786 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539684 [OTISSUB3 115.00] CKT 1 | 12.3281 | PASS | 11.7268 | PASS | 11626.786 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 139.1143 | PASS | 13.8712 | PASS | 13771.2073 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.7972 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 27.2799 | PASS | 11.0766 | PASS | 10976.618 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.3259 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1539 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1539 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 6.0205 | PASS | 46.7718 | PASS | 46671.7605 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 11.0058 | PASS | 36.5448 | PASS | 36444.7829 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 11.0058 | PASS | 36.5448 | PASS | 36444.7829 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 13.5929 | PASS | 0.3026 | PASS | 202.5917 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 15.5225 | PASS | 5.0532 | PASS | 4953.2204 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6239 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 26.0281 | PASS | 1.6866 | PASS | 1586.6239 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 21.1063 | PASS | 2.987 | PASS | 2887.0233 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 24.8225 | PASS | 6.06 | PASS | 5960.0299 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 24.8225 | PASS | 1.7195 | PASS | 1619.4571 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 40.9011 | PASS | 14.7199 | PASS | 14619.9296 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.804 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 23.5573 | PASS | 5.4527 | PASS | 5352.7415 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 9.4877 | PASS | 0.2604 | PASS | 160.4437 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 9.4877 | PASS | 0.2489 | PASS | 148.9369 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 12.3279 | PASS | 11.7268 | PASS | 11626.8385 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539678 [GRTBEND3 115.00] TO BUS 539719 [GRTBEND1 34.500] TO BUS 539921 [GRTBENDT 7.2000] CKT 1 | 12.3279 | PASS | 11.7268 | PASS | 11626.8385 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 139.1538 | PASS | 13.8736 | PASS | 13773.5665 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 14.1804 | PASS | 9.8601 | PASS | 9760.1408 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 27.2851 | PASS | 11.0781 | PASS | 10978.0725 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 20.5336 | PASS | 11.8826 | PASS | 11782.6351 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 6.0212 | PASS | 23.2135 | PASS | 23113.4798 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 6.0212 | PASS | 23.2135 | PASS | 23113.4798 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 6.0212 | PASS | 46.7749 | PASS | 46674.8858 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 10.9958 | PASS | 36.5329 | PASS | 36432.9426 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 10.9958 | PASS | 36.5329 | PASS | 36432.9426 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 13.5949 | PASS | 0.3023 | PASS | 202.3211 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 9.827 | PASS | 5.0424 | PASS | 4942.3874 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 26.0287 | PASS | 1.6867 | PASS | 1586.6886 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 26.0287 | PASS | 1.6867 | PASS | 1586.6886 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 21.088 | PASS | 2.9607 | PASS | 2860.6867 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 24.8222 | PASS | 6.0599 | PASS | 5959.8866 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 24.8222 | PASS | 1.7195 | PASS | 1619.4667 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 40.9019 | PASS | 14.7202 | PASS | 14620.1795 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 23.9773 | PASS | 5.4621 | PASS | 5362.1396 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 23.5574 | PASS | 5.4529 | PASS | 5352.8677 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 9.4905 | PASS | 0.2604 | PASS | 160.4448 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 9.4905 | PASS | 0.2489 | PASS | 148.9384 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 12.3307 | PASS | 11.7283 | PASS | 11628.2512 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539679 [GRTBEND6 230.00] TO BUS 768280 [G22-065-TAP 230.00] CKT 1 | 12.3307 | PASS | 11.7283 | PASS | 11628.2512 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 139.1493 | PASS | 13.873 | PASS | 13773.0071 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 14.1787 | PASS | 9.8593 | PASS | 9759.3241 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 27.2829 | PASS | 11.0774 | PASS | 10977.4442 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 20.5351 | PASS | 11.8824 | PASS | 11782.3509 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 6.0209 | PASS | 23.2129 | PASS | 23112.8949 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 6.0209 | PASS | 23.2129 | PASS | 23112.8949 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 6.0209 | PASS | 46.7738 | PASS | 46673.8357 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 11.011 | PASS | 36.5596 | PASS | 36459.6332 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 11.011 | PASS | 36.5596 | PASS | 36459.6332 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 13.5953 | PASS | 0.3023 | PASS | 202.2779 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 15.5672 | PASS | 5.0342 | PASS | 4934.1538 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 26.0283 | PASS | 1.6866 | PASS | 1586.639 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 26.0283 | PASS | 1.6866 | PASS | 1586.639 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 21.1498 | PASS | 2.9951 | PASS | 2895.1283 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 24.8216 | PASS | 6.0596 | PASS | 5959.6379 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 24.8216 | PASS | 1.7195 | PASS | 1619.4833 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 40.9014 | PASS | 14.72 | PASS | 14619.9984 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 23.977 | PASS | 5.4619 | PASS | 5361.9063 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7237 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 9.4888 | PASS | 0.2604 | PASS | 160.4443 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 9.4888 | PASS | 0.2489 | PASS | 148.9377 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 12.3312 | PASS | 1173% | PASS | 11628.4857 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539117 [SPRVILL-EHVB230.00] CKT Z1 | 12.3312 | PASS | 11.7285 | PASS | 11628.4857 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 139.1168 | PASS | 1387% | PASS | 13770.7766 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 14.1773 | PASS | 9.8587 | PASS | 9758.7116 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 27.2798 | PASS | 11.0766 | PASS | 10976.5692 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 20.5344 | PASS | 11.8822 | PASS | 11782.2181 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.0989 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.0989 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 6.0205 | PASS | 46.7717 | PASS | 46671.6634 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 11.0051 | PASS | 36.5426 | PASS | 36442.6305 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 11.0051 | PASS | 36.5426 | PASS | 36442.6305 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 13.593 | PASS | 0.3026 | PASS | 202.5737 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 15.3423 | PASS | 5.0474 | PASS | 4947.4491 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6308 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6308 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 21.0793 | PASS | 2.9814 | PASS | 2881.4089 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9877 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4599 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 40.9012 | PASS | 14.72 | PASS | 14619.9605 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 23.9769 | PASS | 5.4618 | PASS | 5361.8436 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7708 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 9.4875 | PASS | 0.2604 | PASS | 160.4432 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 9.4875 | PASS | 0.2489 | PASS | 148.9363 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 12.3282 | PASS | 11.7267 | PASS | 11626.7278 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539695 [SPEARVL6 230.00] TO BUS 539694 [SPEARVL3 115.00] TO BUS 539935 [SPERVLTT 13.800] CKT 1 | 12.3282 | PASS | 11.7267 | PASS | 11626.7278 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 139.1219 | PASS | 13.871 | PASS | 13771.0187 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.7842 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 27.2801 | PASS | 11.0766 | PASS | 10976.6448 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2636 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1706 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1706 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 6.0205 | PASS | 46.7718 | PASS | 46671.7905 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 11.0049 | PASS | 36.5423 | PASS | 36442.2548 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 11.0049 | PASS | 36.5423 | PASS | 36442.2548 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5615 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 15.5324 | PASS | 5.041 | PASS | 4940.9681 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6339 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6339 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 21.0811 | PASS | 2.9822 | PASS | 2882.1706 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9829 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 40.9013 | PASS | 14.72 | PASS | 14619.9721 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 23.9769 | PASS | 5.4619 | PASS | 5361.8594 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 23.5573 | PASS | 5.4528 | PASS | 5352.7773 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 12.3286 | PASS | 11.7269 | PASS | 11626.8575 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539759 [SPRVL 3 115.00] TO BUS 539771 [NFTDODG3 115.00] CKT 1 | 12.3286 | PASS | 11.7269 | PASS | 11626.8575 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 139.1388 | PASS | 13.8725 | PASS | 13772.5263 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 14.1784 | PASS | 9.8592 | PASS | 9759.191 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 27.2822 | PASS | 11.0772 | PASS | 10977.244 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 20.5349 | PASS | 11.8823 | PASS | 11782.3278 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 6.0208 | PASS | 23.2127 | PASS | 23112.7153 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 6.0208 | PASS | 23.2127 | PASS | 23112.7153 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 6.0208 | PASS | 46.7729 | PASS | 46672.8853 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 11.0092 | PASS | 36.5475 | PASS | 36447.4562 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 11.0092 | PASS | 36.5475 | PASS | 36447.4562 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 13.5947 | PASS | 0.3024 | PASS | 202.35 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 15.5359 | PASS | 5.0447 | PASS | 4944.7028 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6351 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6351 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 21.1306 | PASS | 2.9878 | PASS | 2887.8271 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 24.8218 | PASS | 6.0597 | PASS | 5959.7298 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 24.8218 | PASS | 1.7195 | PASS | 1619.4772 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 40.9013 | PASS | 14.72 | PASS | 14619.981 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 23.9769 | PASS | 5.4619 | PASS | 5361.881 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7285 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 9.4884 | PASS | 0.2604 | PASS | 160.4436 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 9.4884 | PASS | 0.2489 | PASS | 148.9368 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 12.3303 | PASS | 11.7281 | PASS | 11628.0711 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 539815 [IRONWOOD WF7345.00] CKT 1 | 12.3303 | PASS | 11.7281 | PASS | 11628.0711 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 139.0083 | PASS | 13.8698 | PASS | 13769.7887 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 14.1769 | PASS | 9.8586 | PASS | 9758.6335 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 27.2788 | PASS | 11.0765 | PASS | 10976.511 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 20.5342 | PASS | 11.8822 | PASS | 11782.1616 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 6.0203 | PASS | 23.212 | PASS | 23112.0173 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 6.0203 | PASS | 23.212 | PASS | 23112.0173 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 6.0203 | PASS | 46.7725 | PASS | 46672.4739 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 10.9733 | PASS | 36.5629 | PASS | 36462.9219 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 10.9733 | PASS | 36.5629 | PASS | 36462.9219 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 13.5926 | PASS | 0.3026 | PASS | 202.5575 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 15.2819 | PASS | 5.0478 | PASS | 4947.8252 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 26.0284 | PASS | 1.6867 | PASS | 1586.6551 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 26.0284 | PASS | 1.6867 | PASS | 1586.6551 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 20.6829 | PASS | 2.9952 | PASS | 2895.1949 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9822 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 40.9016 | PASS | 14.7201 | PASS | 14620.0614 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 23.9771 | PASS | 5.462 | PASS | 5361.9719 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 23.5575 | PASS | 5.4529 | PASS | 5352.8802 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 9.4822 | PASS | 0.2604 | PASS | 160.4455 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 9.4822 | PASS | 0.2489 | PASS | 148.9391 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 12.321 | PASS | 11.7261 | PASS | 11626.0545 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 560080 [G16-046-TAP 345.00] CKT 1 | 12.321 | PASS | 11.7261 | PASS | 11626.0545 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 139.1532 | PASS | 13.874 | PASS | 13773.9791 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 14.179 | PASS | 9.8595 | PASS | 9759.494 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 27.2838 | PASS | 11.0777 | PASS | 10977.7128 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 20.535 | PASS | 11.8824 | PASS | 11782.394 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 6.021 | PASS | 23.2131 | PASS | 23113.1416 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 6.021 | PASS | 23.2131 | PASS | 23113.1416 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 6.021 | PASS | 46.7741 | PASS | 46674.1234 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 11.0117 | PASS | 36.558 | PASS | 36457.9524 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 11.0117 | PASS | 36.558 | PASS | 36457.9524 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 13.596 | PASS | 0.3022 | PASS | 202.1744 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 15.5411 | PASS | 5.0518 | PASS | 4951.7673 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6428 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 26.0283 | PASS | 1.6866 | PASS | 1586.6428 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 21.1419 | PASS | 2.9982 | PASS | 2898.1674 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 24.8213 | PASS | 6.0595 | PASS | 5959.5016 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 24.8213 | PASS | 1.7195 | PASS | 1619.4924 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 40.9014 | PASS | 14.72 | PASS | 14620.0155 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 23.977 | PASS | 5.4619 | PASS | 5361.9343 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7144 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 9.4886 | PASS | 0.2604 | PASS | 160.4445 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 9.4886 | PASS | 0.2489 | PASS | 148.938 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 12.332 | PASS | 11.7293 | PASS | 11629.3017 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 539803 [IRONWOOD7 345.00] TO BUS 579480 [GEN-2008-124345.00] CKT 1 | 12.332 | PASS | 11.7293 | PASS | 11629.3017 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 139.12 | PASS | 13.8712 | PASS | 13771.2039 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8558 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 27.2802 | PASS | 11.0767 | PASS | 10976.7059 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2913 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2253 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2253 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 6.0205 | PASS | 46.7721 | PASS | 46672.1052 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.156 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.156 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 13.5931 | PASS | 0.3026 | PASS | 202.559 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 15.5266 | PASS | 5.0446 | PASS | 4944.5941 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 23.4961 | PASS | 1.6896 | PASS | 1589.6082 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 23.4961 | PASS | 1.6896 | PASS | 1589.6082 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7605 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 24.8106 | PASS | 6.059 | PASS | 5959.0323 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 24.8106 | PASS | 1.7195 | PASS | 1619.5216 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 14.3115 | PASS | 14.7019 | PASS | 14601.8634 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 23.3232 | PASS | 5.4667 | PASS | 5366.7354 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 23.2184 | PASS | 5.4449 | PASS | 5344.9088 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.8915 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 12.3283 | PASS | 11.7269 | PASS | 11626.8915 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 139.1201 | PASS | 13.8712 | PASS | 13771.2062 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8562 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 27.2803 | PASS | 11.0767 | PASS | 10976.7087 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2871 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 6.0206 | PASS | 23.2122 | PASS | 23112.236 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 6.0206 | PASS | 23.2122 | PASS | 23112.236 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 6.0206 | PASS | 46.772 | PASS | 46672.0039 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1607 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1607 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 13.5932 | PASS | 0.3026 | PASS | 202.5566 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6048 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 22.0787 | PASS | 1.6763 | PASS | 1576.3066 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 22.0787 | PASS | 1.6763 | PASS | 1576.3066 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 21.1113 | PASS | 2.9858 | PASS | 2885.7888 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 24.8224 | PASS | 6.0613 | PASS | 5961.3319 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 24.8224 | PASS | 1.7194 | PASS | 1619.3696 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 25.1716 | PASS | 14.8658 | PASS | 14765.7976 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 22.8619 | PASS | 5.4121 | PASS | 5312.0822 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 23.4745 | PASS | 5.465 | PASS | 5364.9609 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 9.4879 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 9.4879 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 12.3283 | PASS | 11.7269 | PASS | 11626.8944 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541203 [NASHUA 5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT Z1 | 12.3283 | PASS | 11.7269 | PASS | 11626.8944 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 139.1208 | PASS | 13.8713 | PASS | 13771.2816 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.863 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 27.2803 | PASS | 11.0767 | PASS | 10976.7234 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.3022 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2461 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2461 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46671.9609 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1805 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1805 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 13.5932 | PASS | 0.3025 | PASS | 202.5492 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 15.5267 | PASS | 5.0447 | PASS | 4944.6623 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 24.4505 | PASS | 1.684 | PASS | 1584.0203 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 24.4505 | PASS | 1.684 | PASS | 1584.0203 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 21.1113 | PASS | 2.9858 | PASS | 2885.8096 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 24.8218 | PASS | 6.0598 | PASS | 5959.8465 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 24.8218 | PASS | 1.7195 | PASS | 1619.4693 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 40.0576 | PASS | 14.7113 | PASS | 14611.3273 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 23.5566 | PASS | 5.4482 | PASS | 5348.2087 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 23.5457 | PASS | 5.4514 | PASS | 5351.3638 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9489 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541221 [PLTCTY 5 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9489 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 139.1143 | PASS | 13.8706 | PASS | 13770.6296 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 14.1769 | PASS | 9.8585 | PASS | 9758.5455 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 27.279 | PASS | 11.0763 | PASS | 10976.3467 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 20.5346 | PASS | 11.8822 | PASS | 11782.248 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 6.0204 | PASS | 23.2119 | PASS | 23111.8895 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 6.0204 | PASS | 23.2119 | PASS | 23111.8895 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 6.0204 | PASS | 46.7712 | PASS | 46671.196 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0855 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.0855 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 13.5926 | PASS | 0.3026 | PASS | 202.6284 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 15.5265 | PASS | 5.0444 | PASS | 4944.3757 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 26.0218 | PASS | 1.6876 | PASS | 1587.6311 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 26.0218 | PASS | 1.6876 | PASS | 1587.6311 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 21.1112 | PASS | 2.9857 | PASS | 2885.7173 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 24.823 | PASS | 6.0603 | PASS | 5960.2534 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 24.823 | PASS | 1.7194 | PASS | 1619.4422 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 40.9032 | PASS | 14.7232 | PASS | 14623.2425 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 23.9766 | PASS | 5.4657 | PASS | 5365.7491 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 23.5579 | PASS | 5.4539 | PASS | 5353.9044 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 9.4875 | PASS | 0.2604 | PASS | 160.4431 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 9.4875 | PASS | 0.2489 | PASS | 148.9361 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 12.3279 | PASS | 11.7265 | PASS | 11626.5262 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541204 [SMTHVL 5 161.00] TO BUS 541349 [POPE 161.00] CKT 1 | 12.3279 | PASS | 11.7265 | PASS | 11626.5262 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 139.1201 | PASS | 13.8712 | PASS | 13771.2287 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 14.1775 | PASS | 9.8589 | PASS | 9758.8546 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 27.2799 | PASS | 11.0767 | PASS | 10976.7125 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2801 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 6.0205 | PASS | 2321% | PASS | 23112.2366 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.2366 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 6.0205 | PASS | 4677% | PASS | 46672.3775 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1513 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1513 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 13.5929 | PASS | 0.3026 | PASS | 202.5531 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6142 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 26.026 | PASS | 1.6866 | PASS | 1586.6378 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 26.026 | PASS | 1.6866 | PASS | 1586.6378 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 21.1112 | PASS | 2.9857 | PASS | 2885.7409 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 24.0796 | PASS | 6.0614 | PASS | 5961.3523 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 24.0796 | PASS | 1.7191 | PASS | 1619.0903 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 40.8973 | PASS | 14.72 | PASS | 14620.0393 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 23.9758 | PASS | 5.4619 | PASS | 5361.887 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 23.5538 | PASS | 5.4528 | PASS | 5352.8417 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9126 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300082 [5GEORGE 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9126 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 139.1204 | PASS | 13.8713 | PASS | 13771.2927 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 14.177 | PASS | 9.8588 | PASS | 9758.7592 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 27.2784 | PASS | 11.0767 | PASS | 10976.6622 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 20.5346 | PASS | 11.8822 | PASS | 11782.2477 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 6.0203 | PASS | 23.2122 | PASS | 23112.2163 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 6.0203 | PASS | 23.2122 | PASS | 23112.2163 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 6.0203 | PASS | 46.7717 | PASS | 46671.7226 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.009 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36445.009 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 13.5922 | PASS | 0.3025 | PASS | 202.5243 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6383 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 26.0246 | PASS | 1.6862 | PASS | 1586.2114 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 26.0246 | PASS | 1.6862 | PASS | 1586.2114 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 21.1103 | PASS | 2.9853 | PASS | 2885.2592 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 23.3483 | PASS | 6.0317 | PASS | 5931.6681 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 23.3483 | PASS | 1.7208 | PASS | 1620.7872 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 40.8897 | PASS | 14.7168 | PASS | 14616.7684 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 23.9737 | PASS | 5.4593 | PASS | 5359.2804 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 23.5484 | PASS | 5.4461 | PASS | 5346.1089 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4436 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9368 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 12.3285 | PASS | 11.727 | PASS | 11626.9884 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 300117 [5SEDALA 161.00] CKT 1 | 12.3285 | PASS | 11.727 | PASS | 11626.9884 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 139.1203 | PASS | 13.8712 | PASS | 13771.213 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 14.1775 | PASS | 9.8588 | PASS | 9758.7711 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 27.2801 | PASS | 11.0766 | PASS | 10976.5756 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 20.5347 | PASS | 11.8823 | PASS | 11782.2536 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 6.0205 | PASS | 23.2121 | PASS | 23112.0556 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 6.0205 | PASS | 23.2121 | PASS | 23112.0556 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 6.0205 | PASS | 46.7714 | PASS | 46671.3723 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 11.0062 | PASS | 36.5452 | PASS | 36445.1542 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 11.0062 | PASS | 36.5452 | PASS | 36445.1542 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 13.593 | PASS | 0.3026 | PASS | 202.601 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 15.5267 | PASS | 5.0446 | PASS | 4944.6094 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 26.0248 | PASS | 1.686 | PASS | 1586.0193 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 26.0248 | PASS | 1.686 | PASS | 1586.0193 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 21.1112 | PASS | 2.9857 | PASS | 2885.7454 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 24.7536 | PASS | 5.9804 | PASS | 5880.4161 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 24.7536 | PASS | 1.7248 | PASS | 1624.8163 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 40.8888 | PASS | 14.7153 | PASS | 14615.2846 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 23.9732 | PASS | 5.4581 | PASS | 5358.1196 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 23.5483 | PASS | 5.4436 | PASS | 5343.6399 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 12.3284 | PASS | 11.7269 | PASS | 11626.9054 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541146 [SEDLIAW_CAP5161.00] CKT R | 12.3284 | PASS | 11.7269 | PASS | 11626.9054 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 139.1211 | PASS | 13.8713 | PASS | 13771.3086 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.9 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 27.2805 | PASS | 11.0768 | PASS | 10976.7617 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2841 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2774 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2774 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 6.0206 | PASS | 46.7721 | PASS | 46672.0545 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1783 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1783 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.5455 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 15.5267 | PASS | 5.0447 | PASS | 4944.6501 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 26.0278 | PASS | 1.6865 | PASS | 1586.5443 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 26.0278 | PASS | 1.6865 | PASS | 1586.5443 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 21.1113 | PASS | 2.9858 | PASS | 2885.8034 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 24.7666 | PASS | 6.071 | PASS | 5970.9787 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 24.7666 | PASS | 1.7187 | PASS | 1618.6907 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 40.8995 | PASS | 14.7193 | PASS | 14619.2667 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 23.9764 | PASS | 5.4613 | PASS | 5361.3163 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 23.5562 | PASS | 5.4516 | PASS | 5351.5845 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 12.3284 | PASS | 11.727 | PASS | 11626.9612 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541271 [SEDN 2 69.000] CKT 1 | 12.3284 | PASS | 11.727 | PASS | 11626.9612 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 139.1207 | PASS | 13.8713 | PASS | 13771.2689 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 14.1777 | PASS | 9.8589 | PASS | 9758.878 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 27.2804 | PASS | 11.0767 | PASS | 10976.7344 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 20.5347 | PASS | 11.8823 | PASS | 11782.283 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 6.0206 | PASS | 23.2123 | PASS | 23112.2523 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 6.0206 | PASS | 23.2123 | PASS | 23112.2523 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 6.0206 | PASS | 46.772 | PASS | 46671.9964 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.1711 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.1711 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 13.5932 | PASS | 0.3026 | PASS | 202.552 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 15.5267 | PASS | 5.0446 | PASS | 4944.6315 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 26.0279 | PASS | 1.6866 | PASS | 1586.5946 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 26.0279 | PASS | 1.6866 | PASS | 1586.5946 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 21.1112 | PASS | 2.9858 | PASS | 2885.7907 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 24.7795 | PASS | 6.0624 | PASS | 5962.406 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 24.7795 | PASS | 1.7193 | PASS | 1619.2731 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 40.9003 | PASS | 14.7197 | PASS | 14619.682 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 23.9766 | PASS | 5.4616 | PASS | 5361.6251 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 23.5567 | PASS | 5.4523 | PASS | 5352.2915 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 12.3284 | PASS | 11.7269 | PASS | 11626.9365 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541272 [SEDS 2 69.000] CKT 2 | 12.3284 | PASS | 11.7269 | PASS | 11626.9365 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 139.1266 | PASS | 13.8719 | PASS | 13771.875 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 14.1784 | PASS | 9.8592 | PASS | 9759.2253 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 27.2821 | PASS | 11.0772 | PASS | 10977.205 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.314 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 6.0208 | PASS | 23.2127 | PASS | 23112.7235 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 6.0208 | PASS | 23.2127 | PASS | 23112.7235 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 6.0208 | PASS | 46.7731 | PASS | 46673.0725 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 11.0062 | PASS | 36.5453 | PASS | 36445.285 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 11.0062 | PASS | 36.5453 | PASS | 36445.285 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 13.5941 | PASS | 0.3024 | PASS | 202.4277 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 15.5268 | PASS | 5.0449 | PASS | 4944.898 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 25.9992 | PASS | 1.6862 | PASS | 1586.1988 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 25.9992 | PASS | 1.6862 | PASS | 1586.1988 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 21.1115 | PASS | 2.986 | PASS | 2885.9586 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 23.7778 | PASS | 6.0667 | PASS | 5966.6765 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 23.7778 | PASS | 1.7186 | PASS | 1618.6478 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 40.8335 | PASS | 14.7164 | PASS | 14616.3719 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 23.9609 | PASS | 5.4591 | PASS | 5359.0615 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 23.4958 | PASS | 5.446 | PASS | 5345.9901 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 9.4884 | PASS | 0.2604 | PASS | 160.4439 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 9.4884 | PASS | 0.2489 | PASS | 148.9372 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 12.3289 | PASS | 11.7273 | PASS | 11627.3242 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541209 [SEDALIA5 161.00] TO BUS 541337 [WAFBE_SW5 161.00] CKT 1 | 12.3289 | PASS | 11.7273 | PASS | 11627.3242 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 139.1187 | PASS | 13.8711 | PASS | 13771.0658 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 14.1776 | PASS | 9.8588 | PASS | 9758.8358 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 27.28 | PASS | 11.0767 | PASS | 10976.6628 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2587 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1775 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 6.0205 | PASS | 23.2122 | PASS | 23112.1775 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 6.0205 | PASS | 46.7719 | PASS | 46671.9291 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1161 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.1161 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 13.5929 | PASS | 0.3026 | PASS | 202.5781 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.4819 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 23.531 | PASS | 1.6863 | PASS | 1586.2536 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 23.531 | PASS | 1.6863 | PASS | 1586.2536 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 21.1111 | PASS | 2.9857 | PASS | 2885.6977 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 24.8094 | PASS | 6.0589 | PASS | 5958.9404 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 24.8094 | PASS | 1.7195 | PASS | 1619.5273 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 28.6132 | PASS | 14.7454 | PASS | 14645.4106 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 23.3279 | PASS | 5.4529 | PASS | 5352.8565 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 23.2065 | PASS | 5.4482 | PASS | 5348.1917 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 9.4877 | PASS | 0.2604 | PASS | 160.4433 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 9.4877 | PASS | 0.2489 | PASS | 148.9364 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 12.3282 | PASS | 11.7268 | PASS | 11626.7905 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541215 [HLLMRK 5 161.00] TO BUS 541247 [LBRTYWT5 161.00] CKT 1 | 12.3282 | PASS | 11.7268 | PASS | 11626.7905 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 139.1204 | PASS | 13.8712 | PASS | 13771.2122 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 14.1776 | PASS | 9.8588 | PASS | 9758.8144 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 27.2802 | PASS | 11.0766 | PASS | 10976.6475 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 20.5346 | PASS | 11.8821 | PASS | 11782.1479 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 6.0205 | PASS | 23.2121 | PASS | 23112.1333 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 6.0205 | PASS | 23.2121 | PASS | 23112.1333 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 6.0205 | PASS | 46.7716 | PASS | 46671.5857 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 11.0061 | PASS | 36.5451 | PASS | 36445.1293 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 11.0061 | PASS | 36.5451 | PASS | 36445.1293 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 13.5932 | PASS | 0.3026 | PASS | 202.5629 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 15.5266 | PASS | 5.0446 | PASS | 4944.5755 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 26.0331 | PASS | 1.6777 | PASS | 1577.734 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 26.0331 | PASS | 1.6777 | PASS | 1577.734 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 21.1111 | PASS | 2.9857 | PASS | 2885.6758 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 24.8194 | PASS | 6.0584 | PASS | 5958.4487 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 24.8194 | PASS | 1.7196 | PASS | 1619.5628 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 40.849 | PASS | 14.6897 | PASS | 14589.6928 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 23.9539 | PASS | 5.4217 | PASS | 5321.7262 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 23.5442 | PASS | 5.4391 | PASS | 5339.1124 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 12.3284 | PASS | 11.7269 | PASS | 11626.905 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541145 [RNRIDGE_CAP5161.00] CKT R | 12.3284 | PASS | 11.7269 | PASS | 11626.905 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 139.1204 | PASS | 13.8712 | PASS | 13771.2499 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8757 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7313 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2833 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.249 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.249 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46671.9594 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1554 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1554 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5524 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6133 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 25.899 | PASS | 1.6873 | PASS | 1587.3213 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 25.899 | PASS | 1.6873 | PASS | 1587.3213 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7508 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 24.8211 | PASS | 6.0594 | PASS | 5959.4365 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 24.8211 | PASS | 1.7195 | PASS | 1619.4968 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 40.8636 | PASS | 14.7207 | PASS | 14620.731 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 23.9467 | PASS | 5.463 | PASS | 5363.0466 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 23.5216 | PASS | 5.4457 | PASS | 5345.6937 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9232 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541260 [RNRDGE 2 69.000] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9232 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 139.1205 | PASS | 13.8713 | PASS | 13771.2543 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8834 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7449 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2803 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2658 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2658 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 6.0206 | PASS | 46.7721 | PASS | 46672.052 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1678 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1678 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 13.5932 | PASS | 0.3025 | PASS | 202.5483 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 15.5267 | PASS | 504.5% | PASS | 4944.6188 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 26.0245 | PASS | 1.6865 | PASS | 1586.5091 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 26.0245 | PASS | 168.7% | PASS | 1586.5091 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7803 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9536 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4622 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 40.8986 | PASS | 14.7195 | PASS | 14619.5257 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 23.9762 | PASS | 5.4614 | PASS | 5361.4371 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 23.5562 | PASS | 5.4527 | PASS | 5352.6623 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9251 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 541318 [NCONGRS5 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9251 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 139.1209 | PASS | 13.8713 | PASS | 13771.3033 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 14.1779 | PASS | 9.859 | PASS | 9758.9669 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 27.2807 | PASS | 11.0768 | PASS | 10976.8404 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2636 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.3422 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.3422 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 6.0206 | PASS | 46.7722 | PASS | 46672.1836 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1931 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1931 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.5351 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 15.5266 | PASS | 5.0446 | PASS | 4944.5997 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 24.4426 | PASS | 1.6857 | PASS | 1585.7344 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 24.4426 | PASS | 1.6857 | PASS | 1585.7344 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 21.1114 | PASS | 2.9859 | PASS | 2885.8719 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 24.8212 | PASS | 6.0595 | PASS | 5959.4748 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 24.8212 | PASS | 1.7195 | PASS | 1619.4942 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 40.1173 | PASS | 14.7161 | PASS | 14616.1199 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 23.7588 | PASS | 5.4518 | PASS | 5351.7819 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 23.5516 | PASS | 5.449 | PASS | 5348.9796 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9407 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543019 [BARRY 5 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9407 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 139.1242 | PASS | 13.8716 | PASS | 13771.6131 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 14.1782 | PASS | 9.8591 | PASS | 9759.1059 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 27.2814 | PASS | 11.077 | PASS | 10977.0187 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 20.5345 | PASS | 11.8822 | PASS | 11782.2188 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 6.0207 | PASS | 23.2125 | PASS | 23112.5006 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 6.0207 | PASS | 23.2125 | PASS | 23112.5006 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 6.0207 | PASS | 46.7729 | PASS | 46672.8813 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 11.0063 | PASS | 36.5454 | PASS | 36445.3749 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 11.0063 | PASS | 36.5454 | PASS | 36445.3749 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 13.5937 | PASS | 0.3025 | PASS | 202.4868 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 15.5268 | PASS | 5.0448 | PASS | 4944.7978 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 24.1403 | PASS | 1.6984 | PASS | 1598.4164 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 24.1403 | PASS | 1.6984 | PASS | 1598.4164 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 21.1122 | PASS | 2.9863 | PASS | 2886.3391 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 24.823 | PASS | 6.0607 | PASS | 5960.6845 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 24.823 | PASS | 1.7194 | PASS | 1619.4131 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 39.9528 | PASS | 14.7569 | PASS | 14656.8768 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 23.4863 | PASS | 5.433 | PASS | 5333.0095 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 23.5313 | PASS | 5.4592 | PASS | 5359.1599 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 9.4882 | PASS | 0.2604 | PASS | 160.4437 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 9.4882 | PASS | 0.2489 | PASS | 148.9369 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 12.3287 | PASS | 11.7271 | PASS | 11627.1343 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541230 [RNRIDGE5 161.00] TO BUS 543026 [TIFFANY5 161.00] CKT 1 | 12.3287 | PASS | 11.7271 | PASS | 11627.1343 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 139.1306 | PASS | 13.8723 | PASS | 13772.2887 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 14.1788 | PASS | 9.8595 | PASS | 9759.4683 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 27.2824 | PASS | 11.0774 | PASS | 10977.4179 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 20.5348 | PASS | 11.8824 | PASS | 11782.3538 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 6.0208 | PASS | 23.2129 | PASS | 23112.8597 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 6.0208 | PASS | 23.2129 | PASS | 23112.8597 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 6.0208 | PASS | 46.7742 | PASS | 46674.2105 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 11.0064 | PASS | 36.5455 | PASS | 36445.4614 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 11.0064 | PASS | 36.5455 | PASS | 36445.4614 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 13.5938 | PASS | 0.3024 | PASS | 202.4346 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 15.5269 | PASS | 5.0451 | PASS | 4945.0702 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 26.0213 | PASS | 1.6861 | PASS | 1586.1202 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 26.0213 | PASS | 1.6861 | PASS | 1586.1202 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 21.1122 | PASS | 2.9864 | PASS | 2886.3824 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 15.3754 | PASS | 6.1313 | PASS | 6031.2651 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 15.3754 | PASS | 1.708 | PASS | 1607.9986 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 40.8792 | PASS | 14.7156 | PASS | 14615.6142 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 23.9715 | PASS | 5.4586 | PASS | 5358.5973 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 23.5327 | PASS | 5.4443 | PASS | 5344.2831 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 9.4886 | PASS | 0.2604 | PASS | 160.4441 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 9.4886 | PASS | 0.2489 | PASS | 148.9375 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 12.3292 | PASS | 11.7276 | PASS | 11627.565 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541241 [SEDEAST5 161.00] TO BUS 768980 [G22-100-TAP 161.00] CKT 1 | 12.3292 | PASS | 11.7276 | PASS | 11627.565 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 139.121 | PASS | 13.8714 | PASS | 13771.4007 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 14.1779 | PASS | 9.859 | PASS | 9759.0069 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 27.2807 | PASS | 11.0769 | PASS | 10976.8982 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.3463 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.4306 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 6.0206 | PASS | 23.2124 | PASS | 23112.4306 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 6.0206 | PASS | 46.7718 | PASS | 46671.7682 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.3438 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.3438 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 13.5931 | PASS | 0.3026 | PASS | 202.5503 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 15.5267 | PASS | 5.0448 | PASS | 4944.761 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 25.8987 | PASS | 1.6842 | PASS | 1584.2229 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 25.8987 | PASS | 1.6842 | PASS | 1584.2229 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 21.1119 | PASS | 2.9863 | PASS | 2886.2572 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 24.8106 | PASS | 6.054 | PASS | 5954.0075 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 24.8106 | PASS | 1.7199 | PASS | 1619.8607 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 39.8199 | PASS | 14.6745 | PASS | 14574.457 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 23.9324 | PASS | 5.4517 | PASS | 5351.7015 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 22.1866 | PASS | 5.4214 | PASS | 5321.427 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4437 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9369 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 12.3284 | PASS | 11.727 | PASS | 11627.0092 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541202 [SIBLEY 5 161.00] CKT 1 | 12.3284 | PASS | 11.727 | PASS | 11627.0092 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 139.1223 | PASS | 13.8714 | PASS | 13771.4388 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 14.1781 | PASS | 9.8591 | PASS | 9759.0731 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 27.2811 | PASS | 11.077 | PASS | 10976.9742 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 20.5348 | PASS | 11.8823 | PASS | 11782.3292 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 6.0207 | PASS | 23.2125 | PASS | 23112.4882 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 6.0207 | PASS | 23.2125 | PASS | 23112.4882 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 6.0207 | PASS | 46.7731 | PASS | 46673.1086 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.2967 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.2967 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 13.5935 | PASS | 0.3025 | PASS | 202.5118 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 15.5267 | PASS | 5.0447 | PASS | 4944.698 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 25.8874 | PASS | 1.6885 | PASS | 1588.531 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 25.8874 | PASS | 1.6885 | PASS | 1588.531 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 21.1118 | PASS | 2.9861 | PASS | 2886.1472 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 24.8083 | PASS | 6.0545 | PASS | 5954.4734 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 24.8083 | PASS | 1.7198 | PASS | 1619.8285 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 40.3844 | PASS | 14.7434 | PASS | 14643.436 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 23.9348 | PASS | 5.4695 | PASS | 5369.536 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 23.0485 | PASS | 5.485 | PASS | 5384.9757 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 9.4881 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 9.4881 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 12.3285 | PASS | 11.727 | PASS | 11627.0192 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541235 [DUNCAN 5 161.00] CKT 1 | 12.3285 | PASS | 11.727 | PASS | 11627.0192 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 139.1187 | PASS | 13.8711 | PASS | 13771.0671 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 14.1775 | PASS | 9.8588 | PASS | 9758.7803 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 27.2799 | PASS | 11.0766 | PASS | 10976.5838 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2803 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.0895 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 6.0205 | PASS | 23.2121 | PASS | 23112.0895 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 6.0205 | PASS | 46.7717 | PASS | 46671.7005 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1592 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1592 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 13.5929 | PASS | 0.3026 | PASS | 202.6041 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 15.5266 | PASS | 5.0445 | PASS | 4944.535 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 25.995 | PASS | 1.6872 | PASS | 1587.1848 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 25.995 | PASS | 1.6872 | PASS | 1587.1848 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 21.1113 | PASS | 2.9858 | PASS | 2885.817 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 24.706 | PASS | 6.0403 | PASS | 5940.3331 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 24.706 | PASS | 1.7208 | PASS | 1620.7597 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 40.8077 | PASS | 14.7267 | PASS | 14626.6893 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 23.9649 | PASS | 5.4643 | PASS | 5364.2919 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 23.4578 | PASS | 5.4626 | PASS | 5362.6295 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 9.4878 | PASS | 0.2604 | PASS | 160.4433 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 9.4878 | PASS | 0.2489 | PASS | 148.9364 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 12.3282 | PASS | 11.7268 | PASS | 11626.7988 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541244 [ORRICK 5 161.00] CKT 1 | 12.3282 | PASS | 11.7268 | PASS | 11626.7988 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 139.1205 | PASS | 13.8713 | PASS | 13771.2543 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 14.1777 | PASS | 9.8589 | PASS | 9758.87 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 27.2804 | PASS | 11.0767 | PASS | 10976.7307 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 20.5347 | PASS | 11.8823 | PASS | 11782.282 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 6.0206 | PASS | 23.2123 | PASS | 23112.2528 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 6.0206 | PASS | 23.2123 | PASS | 23112.2528 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 6.0206 | PASS | 46.772 | PASS | 46671.9649 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.1637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.1637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 13.5932 | PASS | 0.3025 | PASS | 202.5498 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 15.5267 | PASS | 5.0446 | PASS | 4944.627 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 26.028 | PASS | 1.6866 | PASS | 1586.5969 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 26.028 | PASS | 1.6866 | PASS | 1586.5969 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 21.1112 | PASS | 2.9858 | PASS | 2885.771 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 24.8223 | PASS | 6.06 | PASS | 5960.0049 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 24.8223 | PASS | 1.7195 | PASS | 1619.4587 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 40.8993 | PASS | 14.7199 | PASS | 14619.897 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 23.9766 | PASS | 5.4617 | PASS | 5361.6511 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 23.5565 | PASS | 5.4527 | PASS | 5352.6593 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 12.3284 | PASS | 11.7269 | PASS | 11626.9281 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 2 | 12.3284 | PASS | 11.7269 | PASS | 11626.9281 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 139.1205 | PASS | 13.8713 | PASS | 13771.2534 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 14.1777 | PASS | 9.8589 | PASS | 9758.8695 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 27.2804 | PASS | 11.0767 | PASS | 10976.7304 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 20.5347 | PASS | 11.8823 | PASS | 11782.2821 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 6.0206 | PASS | 23.2123 | PASS | 23112.2524 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 6.0206 | PASS | 23.2123 | PASS | 23112.2524 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 6.0206 | PASS | 46.772 | PASS | 46671.9688 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 11.0062 | PASS | 36.5452 | PASS | 36445.1643 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 11.0062 | PASS | 36.5452 | PASS | 36445.1643 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 13.5932 | PASS | 0.3025 | PASS | 202.5498 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 15.5267 | PASS | 5.0446 | PASS | 4944.6271 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 26.0279 | PASS | 1.6866 | PASS | 1586.597 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 26.0279 | PASS | 1.6866 | PASS | 1586.597 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 21.1112 | PASS | 2.9858 | PASS | 2885.7726 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 24.8223 | PASS | 6.06 | PASS | 5960.0461 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 24.8223 | PASS | 1.7195 | PASS | 1619.4559 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 40.8987 | PASS | 14.72 | PASS | 14620.0127 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 23.9766 | PASS | 5.4616 | PASS | 5361.648 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 23.5563 | PASS | 5.4528 | PASS | 5352.8484 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 12.3284 | PASS | 11.7269 | PASS | 11626.9275 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541250 [SIBLEYPL 161.00] TO BUS 541263 [SIBLEY 2 69.000] CKT 3 | 12.3284 | PASS | 11.7269 | PASS | 11626.9275 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 139.1205 | PASS | 13.8712 | PASS | 13771.249 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8576 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 27.2803 | PASS | 11.0767 | PASS | 10976.7111 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2789 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2275 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2275 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 6.0206 | PASS | 46.7719 | PASS | 46671.8909 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5567 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.624 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 26.0277 | PASS | 1.6865 | PASS | 1586.5469 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 26.0277 | PASS | 1.6865 | PASS | 1586.5469 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7654 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 24.8163 | PASS | 6.0422 | PASS | 5942.155 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 24.8163 | PASS | 1.7207 | PASS | 1620.6595 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 40.8996 | PASS | 1472% | PASS | 14619.3444 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 23.9764 | PASS | 5.4613 | PASS | 5361.3353 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 23.5561 | PASS | 545.2% | PASS | 5351.5874 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9251 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541396 [NUCOR_D1 13.800] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9251 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 139.1126 | PASS | 13.8705 | PASS | 13770.4517 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 14.1768 | PASS | 9.8585 | PASS | 9758.4655 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 27.2788 | PASS | 11.0763 | PASS | 10976.2942 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 20.5346 | PASS | 11.8822 | PASS | 11782.2315 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 6.0203 | PASS | 23.2119 | PASS | 23111.8627 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 6.0203 | PASS | 23.2119 | PASS | 23111.8627 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 6.0203 | PASS | 46.7711 | PASS | 46671.1204 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.075 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 11.0061 | PASS | 36.5451 | PASS | 36445.075 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 13.5927 | PASS | 0.3026 | PASS | 202.6178 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 15.5265 | PASS | 5.0443 | PASS | 4944.3249 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 26.0288 | PASS | 1.6868 | PASS | 1586.8061 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 26.0288 | PASS | 1.6868 | PASS | 1586.8061 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 21.1112 | PASS | 2.9857 | PASS | 2885.7484 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 24.8259 | PASS | 6.0958 | PASS | 5995.8055 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 24.8259 | PASS | 1.717 | PASS | 1617.0223 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 40.9044 | PASS | 14.7213 | PASS | 14621.2926 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 23.9778 | PASS | 5.4629 | PASS | 5362.9428 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 23.5593 | PASS | 5.4553 | PASS | 5355.2655 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 9.4875 | PASS | 0.2604 | PASS | 160.443 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 9.4875 | PASS | 0.2489 | PASS | 148.936 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 12.3277 | PASS | 11.7264 | PASS | 11626.4162 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541397 [NUCOR_C1 13.800] CKT 1 | 12.3277 | PASS | 11.7264 | PASS | 11626.4162 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 139.1205 | PASS | 13.8712 | PASS | 13771.249 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8576 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 27.2803 | PASS | 11.0767 | PASS | 10976.7111 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2789 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2275 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2275 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 6.0206 | PASS | 46.7719 | PASS | 46671.8909 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5566 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.624 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 26.0277 | PASS | 1.6865 | PASS | 1586.547 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 26.0277 | PASS | 1.6865 | PASS | 1586.547 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7654 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 24.8163 | PASS | 6.0422 | PASS | 5942.1623 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 24.8163 | PASS | 1.7207 | PASS | 1620.659 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 40.8996 | PASS | 14.7193 | PASS | 14619.3446 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 23.9764 | PASS | 5.4613 | PASS | 5361.3355 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 23.5561 | PASS | 5.4516 | PASS | 5351.5878 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9251 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 541395 [NUCOR5 161.00] TO BUS 541398 [NUCOR_S1 13.800] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9251 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 139.1227 | PASS | 13.8716 | PASS | 13771.622 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 14.177 | PASS | 9.8589 | PASS | 9758.9022 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 27.2771 | PASS | 11.0768 | PASS | 10976.7861 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 20.5348 | PASS | 11.8823 | PASS | 11782.2976 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 6.02 | PASS | 23.2123 | PASS | 23112.2547 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 6.02 | PASS | 23.2123 | PASS | 23112.2547 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 6.02 | PASS | 46.7729 | PASS | 46672.8815 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.2896 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 11.0063 | PASS | 36.5453 | PASS | 36445.2896 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 13.5916 | PASS | 0.3025 | PASS | 202.5198 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 15.5268 | PASS | 5.0449 | PASS | 4944.9122 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 25.6213 | PASS | 1.6866 | PASS | 1586.6399 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 25.6213 | PASS | 1.6866 | PASS | 1586.6399 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 21.1115 | PASS | 2.986 | PASS | 2886.0047 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 24.7612 | PASS | 6.0576 | PASS | 5957.5637 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 24.7612 | PASS | 1.7196 | PASS | 1619.6063 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 40.85 | PASS | 14.718 | PASS | 14617.992 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 23.7272 | PASS | 5.4605 | PASS | 5360.5165 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 23.5496 | PASS | 5.448 | PASS | 5347.9906 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 9.4883 | PASS | 0.2604 | PASS | 160.4439 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 9.4883 | PASS | 0.2489 | PASS | 148.9372 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 12.3287 | PASS | 11.7272 | PASS | 11627.1921 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 541201 [SIBLEY 7 345.00] CKT 1 | 12.3287 | PASS | 11.7272 | PASS | 11627.1921 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 139.1219 | PASS | 13.8715 | PASS | 13771.4674 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 14.1781 | PASS | 9.8591 | PASS | 9759.0729 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 27.2811 | PASS | 11.077 | PASS | 10976.9817 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 20.5345 | PASS | 11.8823 | PASS | 11782.3204 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 6.0207 | PASS | 23.2125 | PASS | 23112.473 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 6.0207 | PASS | 23.2125 | PASS | 23112.473 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 6.0207 | PASS | 46.7723 | PASS | 46672.3168 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 11.0063 | PASS | 36.5454 | PASS | 36445.3638 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 11.0063 | PASS | 36.5454 | PASS | 36445.3638 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 13.5934 | PASS | 0.3025 | PASS | 202.5089 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 15.5267 | PASS | 5.0447 | PASS | 4944.7422 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 26.0012 | PASS | 1.6869 | PASS | 1586.8963 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 26.0012 | PASS | 1.6869 | PASS | 1586.8963 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 21.112 | PASS | 2.9863 | PASS | 2886.3224 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 24.8218 | PASS | 6.0608 | PASS | 5960.8251 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 24.8218 | PASS | 1.7194 | PASS | 1619.4034 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 40.8852 | PASS | 14.7212 | PASS | 14621.1772 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 23.9448 | PASS | 5.4476 | PASS | 5347.6373 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 23.4835 | PASS | 5.4363 | PASS | 5336.2836 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 9.488 | PASS | 0.2604 | PASS | 160.4437 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 9.488 | PASS | 0.2489 | PASS | 148.9369 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 12.3285 | PASS | 11.727 | PASS | 11627.0368 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543644 [HAWT T20 13.800] CKT 20 | 12.3285 | PASS | 11.727 | PASS | 11627.0368 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 139.1217 | PASS | 13.8714 | PASS | 13771.4057 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 14.178 | PASS | 9.859 | PASS | 9759.0123 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 27.2809 | PASS | 11.0769 | PASS | 10976.9065 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 20.5346 | PASS | 11.8823 | PASS | 11782.3098 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 6.0206 | PASS | 23.2124 | PASS | 23112.4073 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 6.0206 | PASS | 23.2124 | PASS | 23112.4073 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 6.0206 | PASS | 46.7722 | PASS | 46672.2224 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 11.0063 | PASS | 36.5453 | PASS | 36445.3046 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 11.0063 | PASS | 36.5453 | PASS | 36445.3046 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 13.5934 | PASS | 0.3025 | PASS | 202.5212 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 15.5267 | PASS | 5.0447 | PASS | 4944.7077 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 26.0092 | PASS | 1.6868 | PASS | 1586.8003 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 26.0092 | PASS | 1.6868 | PASS | 1586.8003 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 21.1118 | PASS | 2.9862 | PASS | 2886.153 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 24.822 | PASS | 6.0606 | PASS | 5960.5727 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 24.822 | PASS | 1.7194 | PASS | 1619.4204 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 40.8899 | PASS | 14.7207 | PASS | 14620.7367 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 23.954 | PASS | 5.4515 | PASS | 5351.5446 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 23.505 | PASS | 5.4408 | PASS | 5340.815 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 9.488 | PASS | 0.2604 | PASS | 160.4436 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 9.488 | PASS | 0.2489 | PASS | 148.9368 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 12.3285 | PASS | 11.727 | PASS | 11627.0061 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542972 [HAWTH 7 345.00] TO BUS 543665 [HAWTHN5 161.00] TO BUS 543645 [HAWT T22 13.800] CKT 22 | 12.3285 | PASS | 11.727 | PASS | 11627.0061 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 139.1205 | PASS | 13.8712 | PASS | 13771.2432 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 14.1778 | PASS | 9.8589 | PASS | 9758.9461 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 27.2807 | PASS | 11.0768 | PASS | 10976.8171 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 20.5345 | PASS | 11.8822 | PASS | 11782.188 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 6.0206 | PASS | 23.2123 | PASS | 23112.3237 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 6.0206 | PASS | 23.2123 | PASS | 23112.3237 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 6.0206 | PASS | 46.7729 | PASS | 46672.8839 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 11.0062 | PASS | 36.5452 | PASS | 36445.1879 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 11.0062 | PASS | 36.5452 | PASS | 36445.1879 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 13.5933 | PASS | 0.3025 | PASS | 202.5393 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 15.5266 | PASS | 5.0446 | PASS | 4944.5535 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 17.2373 | PASS | 1.7095 | PASS | 1609.5035 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 17.2373 | PASS | 1.7095 | PASS | 1609.5035 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 21.1114 | PASS | 2.9859 | PASS | 2885.8987 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 24.822 | PASS | 6.06 | PASS | 5959.9849 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 24.822 | PASS | 1.7195 | PASS | 1619.4602 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 35.4826 | PASS | 14.7892 | PASS | 14689.1752 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 21.1016 | PASS | 5.4531 | PASS | 5353.134 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 23.5004 | PASS | 5.4594 | PASS | 5359.3525 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 9.488 | PASS | 0.2604 | PASS | 160.4434 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 9.488 | PASS | 0.2489 | PASS | 148.9365 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 12.3284 | PASS | 11.7269 | PASS | 11626.9005 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542980 [NASHUA 7 345.00] TO BUS 543028 [NASHUA-5 161.00] TO BUS 543640 [NASH T11 13.800] CKT 11 | 12.3284 | PASS | 11.7269 | PASS | 11626.9005 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 139.2098 | PASS | 13.8971 | PASS | 13797.0643 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 14.1616 | PASS | 9.8709 | PASS | 9770.8802 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 27.1394 | PASS | 11.0888 | PASS | 10988.7739 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 20.5195 | PASS | 11.8839 | PASS | 11783.8906 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 5.9905 | FAIL | 23.222 | PASS | 23122.0388 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 5.9905 | FAIL | 23.222 | PASS | 23122.0388 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 5.9905 | FAIL | 46.995 | PASS | 46894.9732 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 11.0091 | PASS | 36.5498 | PASS | 36449.7572 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 11.0091 | PASS | 36.5498 | PASS | 36449.7572 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 13.5197 | PASS | 0.299 | PASS | 199.0211 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 15.5309 | PASS | 5.0534 | PASS | 4953.3877 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 25.9766 | PASS | 1.6863 | PASS | 1586.3451 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 25.9766 | PASS | 1.6863 | PASS | 1586.3451 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 21.1188 | PASS | 2.9928 | PASS | 2892.7549 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 24.8053 | PASS | 6.0542 | PASS | 5954.1662 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 24.8053 | PASS | 1.7198 | PASS | 1619.8478 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 40.8528 | PASS | 14.7185 | PASS | 14618.5106 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 23.9456 | PASS | 5.4589 | PASS | 5358.9461 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 23.5238 | PASS | 5.4492 | PASS | 5349.1607 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 9.486 | PASS | 0.2605 | PASS | 160.4621 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 9.486 | PASS | 0.249 | PASS | 148.9607 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 12.3417 | PASS | 11.7427 | PASS | 11642.6853 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542955 [LAC G1 1 22.000] CKT 1 | 12.3417 | PASS | 11.7427 | PASS | 11642.6853 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 139.2382 | PASS | 13.8971 | PASS | 13797.0577 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 14.1844 | PASS | 9.8778 | PASS | 9777.807 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 27.2119 | PASS | 11.0999 | PASS | 10999.8851 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 20.5247 | PASS | 11.8848 | PASS | 11784.7602 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 6.006 | PASS | 23.2389 | PASS | 23138.9409 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 6.006 | PASS | 23.2389 | PASS | 23138.9409 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 6.006 | PASS | 47.0015 | PASS | 46901.5231 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 11.0089 | PASS | 36.5495 | PASS | 36449.4979 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 11.0089 | PASS | 36.5495 | PASS | 36449.4979 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 13.5431 | PASS | 0.2982 | PASS | 198.2427 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 15.5309 | PASS | 5.053 | PASS | 4953.0389 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 26.0002 | PASS | 1.6881 | PASS | 1588.0913 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 26.0002 | PASS | 1.6881 | PASS | 1588.0913 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 21.1189 | PASS | 2.9925 | PASS | 2892.5383 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 24.813 | PASS | 6.0574 | PASS | 5957.4161 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 24.813 | PASS | 1.7196 | PASS | 1619.6308 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 40.8865 | PASS | 14.7265 | PASS | 14626.5118 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 23.9653 | PASS | 5.4707 | PASS | 5370.7087 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 23.5447 | PASS | 5.4609 | PASS | 5360.888 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 9.488 | PASS | 0.2605 | PASS | 160.4607 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 9.488 | PASS | 0.249 | PASS | 148.9589 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 12.3426 | PASS | 11.7424 | PASS | 11642.4274 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542956 [LAC G2 1 24.000] CKT 1 | 12.3426 | PASS | 11.7424 | PASS | 11642.4274 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 139.0718 | PASS | 13.8682 | PASS | 13768.2319 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 14.1373 | PASS | 9.8496 | PASS | 9749.6329 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 27.1465 | PASS | 11.0659 | PASS | 10965.9111 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 20.5037 | PASS | 11.8819 | PASS | 11781.8612 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 5.9919 | FAIL | 23.1978 | PASS | 23097.8349 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 5.9919 | FAIL | 23.1978 | PASS | 23097.8349 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 5.9919 | FAIL | 46.8065 | PASS | 46706.4824 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2285 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2285 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 13.5163 | PASS | 0.3052 | PASS | 205.2451 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 15.5286 | PASS | 5.0476 | PASS | 4947.5892 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 25.9715 | PASS | 1.6857 | PASS | 1585.6585 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 25.9715 | PASS | 1.6857 | PASS | 1585.6585 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 21.1089 | PASS | 2.9848 | PASS | 2884.8224 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 24.8161 | PASS | 6.0574 | PASS | 5957.4166 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 24.8161 | PASS | 1.7196 | PASS | 1619.6315 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 40.8508 | PASS | 14.7153 | PASS | 14615.2896 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 23.9422 | PASS | 5.4548 | PASS | 5354.8199 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 23.5302 | PASS | 5.4446 | PASS | 5344.581 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 9.4905 | PASS | 0.2605 | PASS | 160.455 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 9.4905 | PASS | 0.249 | PASS | 148.9515 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 12.3276 | PASS | 11.7266 | PASS | 11626.6121 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 542965 [W.GRDNR7 345.00] CKT 1 | 12.3276 | PASS | 1173% | PASS | 11626.6121 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 139.0974 | PASS | 13.8691 | PASS | 13769.1445 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 14.1747 | PASS | 985.8% | PASS | 9757.6679 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 27.2741 | PASS | 11.0754 | PASS | 10975.4038 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 20.5341 | PASS | 11.8821 | PASS | 11782.125 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 6.0196 | PASS | 23.211 | PASS | 23111.0076 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 6.0196 | PASS | 23.211 | PASS | 23111.0076 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 6.0196 | PASS | 46.7624 | PASS | 46662.386 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 11.0059 | PASS | 36.5448 | PASS | 36444.8002 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 11.0059 | PASS | 36.5448 | PASS | 36444.8002 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 13.5899 | PASS | 0.3029 | PASS | 202.8955 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 15.5262 | PASS | 5.0439 | PASS | 4943.9167 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 26.0273 | PASS | 1.6866 | PASS | 1586.5958 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 26.0273 | PASS | 1.6866 | PASS | 1586.5958 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 21.1104 | PASS | 2.9852 | PASS | 2885.1983 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 24.823 | PASS | 6.0602 | PASS | 5960.2479 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 24.823 | PASS | 1.7194 | PASS | 1619.4426 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 40.9002 | PASS | 14.7198 | PASS | 14619.8051 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 23.9763 | PASS | 5.4617 | PASS | 5361.6903 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 23.5568 | PASS | 5.4526 | PASS | 5352.6456 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 9.4868 | PASS | 0.2604 | PASS | 160.4425 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 9.4868 | PASS | 0.2489 | PASS | 148.9354 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 12.3266 | PASS | 11.7256 | PASS | 11625.6449 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543629 [LACYGNE11_7 345.00] CKT 1 | 12.3266 | PASS | 11.7256 | PASS | 11625.6449 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 139.1204 | PASS | 13.8712 | PASS | 13771.2499 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 14.1776 | PASS | 9.8589 | PASS | 9758.8653 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 27.2803 | PASS | 11.0767 | PASS | 10976.7223 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2818 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2426 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 6.0206 | PASS | 23.2122 | PASS | 23112.2426 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 6.0206 | PASS | 46.7719 | PASS | 46671.9194 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1631 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1631 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 13.5932 | PASS | 0.3026 | PASS | 202.5511 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6249 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6253 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 26.0282 | PASS | 1.6866 | PASS | 1586.6253 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 21.1112 | PASS | 2.9858 | PASS | 2885.7671 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 24.8224 | PASS | 6.06 | PASS | 5959.9808 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4604 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 40.9012 | PASS | 14.7199 | PASS | 14619.9365 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 23.9768 | PASS | 5.4618 | PASS | 5361.8138 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 23.5572 | PASS | 5.4527 | PASS | 5352.7356 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9255 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543632 [LACYGNE22_7 345.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9255 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 139.1205 | PASS | 13.8713 | PASS | 13771.2511 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 14.1777 | PASS | 9.8589 | PASS | 9758.8688 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 27.2804 | PASS | 11.0767 | PASS | 10976.7288 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 20.5347 | PASS | 11.8823 | PASS | 11782.2823 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 6.0206 | PASS | 23.2123 | PASS | 23112.2522 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 6.0206 | PASS | 23.2123 | PASS | 23112.2522 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 6.0206 | PASS | 46.772 | PASS | 46671.9615 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 11.0062 | PASS | 36.5452 | PASS | 36445.1632 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 11.0062 | PASS | 36.5452 | PASS | 36445.1632 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 13.5932 | PASS | 0.3026 | PASS | 202.5506 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 15.5267 | PASS | 5.0446 | PASS | 4944.6251 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 26.0282 | PASS | 1.6866 | PASS | 1586.6263 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 26.0282 | PASS | 1.6866 | PASS | 1586.6263 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 21.1112 | PASS | 2.9858 | PASS | 2885.7672 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 24.8224 | PASS | 6.06 | PASS | 5959.9822 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 40.9012 | PASS | 14.7199 | PASS | 14619.9402 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 23.9769 | PASS | 5.4618 | PASS | 5361.8197 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 23.5573 | PASS | 5.4527 | PASS | 5352.7408 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 12.3284 | PASS | 11.7269 | PASS | 11626.926 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543667 [LAC3_STAR7 345.00] CKT H | 12.3284 | PASS | 11.7269 | PASS | 11626.926 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 139.1205 | PASS | 13.8713 | PASS | 13771.2532 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 14.1777 | PASS | 9.8589 | PASS | 9758.8708 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 27.2804 | PASS | 11.0767 | PASS | 10976.7312 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 20.5347 | PASS | 11.8823 | PASS | 11782.2828 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 6.0206 | PASS | 23.2123 | PASS | 23112.2533 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 6.0206 | PASS | 23.2123 | PASS | 23112.2533 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 6.0206 | PASS | 46.772 | PASS | 46671.9742 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 11.0062 | PASS | 36.5452 | PASS | 36445.1637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 11.0062 | PASS | 36.5452 | PASS | 36445.1637 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 13.5932 | PASS | 0.3026 | PASS | 202.5502 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 15.5267 | PASS | 5.0446 | PASS | 4944.6259 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 26.0282 | PASS | 1.6866 | PASS | 1586.6263 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 26.0282 | PASS | 1.6866 | PASS | 1586.6263 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 21.1112 | PASS | 2.9858 | PASS | 2885.7679 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 24.8224 | PASS | 6.06 | PASS | 5959.9819 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 24.8224 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 40.9012 | PASS | 14.7199 | PASS | 14619.9406 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 23.9769 | PASS | 5.4618 | PASS | 5361.8203 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 23.5573 | PASS | 5.4527 | PASS | 5352.7414 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 12.3284 | PASS | 11.7269 | PASS | 11626.9272 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543669 [LAC8_STAR7 345.00] CKT H | 12.3284 | PASS | 11.7269 | PASS | 11626.9272 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 139.0035 | PASS | 13.8665 | PASS | 13766.4858 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 14.1391 | PASS | 9.8533 | PASS | 9753.2714 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 27.1401 | PASS | 11.0712 | PASS | 10971.1961 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 20.5311 | PASS | 11.8818 | PASS | 11781.8438 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 5.9895 | FAIL | 23.2054 | PASS | 23105.4409 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 5.9895 | FAIL | 23.2054 | PASS | 23105.4409 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 5.9895 | FAIL | 46.827 | PASS | 46727.0469 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 11.0054 | PASS | 36.544 | PASS | 36444.0165 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 11.0054 | PASS | 36.544 | PASS | 36444.0165 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 13.4998 | PASS | 0.3049 | PASS | 204.893 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 15.5272 | PASS | 5.0456 | PASS | 4945.5774 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 25.9113 | PASS | 1.6858 | PASS | 1585.832 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 25.9113 | PASS | 1.6858 | PASS | 1585.832 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 21.1048 | PASS | 2.9822 | PASS | 2882.1557 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 24.8073 | PASS | 6.0578 | PASS | 5957.7986 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 24.8073 | PASS | 1.7196 | PASS | 1619.6046 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 40.7809 | PASS | 14.7164 | PASS | 14616.4189 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 23.9054 | PASS | 5.456 | PASS | 5355.9548 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 23.4679 | PASS | 5.4475 | PASS | 5347.5353 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 9.4921 | PASS | 0.2604 | PASS | 160.4466 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 9.4921 | PASS | 0.2489 | PASS | 148.9407 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 12.3233 | PASS | 11.7251 | PASS | 11625.1298 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 765571 [G21-029-TAP 345.00] CKT 1 | 12.3233 | PASS | 11.7251 | PASS | 11625.1298 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 138.0445 | PASS | 13.8434 | PASS | 13743.4493 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 14.1929 | PASS | 9.8669 | PASS | 9766.9076 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 27.3038 | PASS | 11.0846 | PASS | 10984.5702 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 20.5363 | PASS | 11.8829 | PASS | 11782.9042 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 6.0241 | PASS | 23.2199 | PASS | 23119.9447 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 6.0241 | PASS | 23.2199 | PASS | 23119.9447 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 6.0241 | PASS | 46.7897 | PASS | 46689.7232 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 11.0035 | PASS | 36.5418 | PASS | 36441.7976 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 11.0035 | PASS | 36.5418 | PASS | 36441.7976 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.8305 | PASS | 0.3153 | PASS | 215.2992 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 15.5236 | PASS | 5.0451 | PASS | 4945.0799 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 26.009 | PASS | 1.6878 | PASS | 1587.8198 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 26.009 | PASS | 1.6878 | PASS | 1587.8198 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 21.0914 | PASS | 2.9769 | PASS | 2876.9125 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 24.8201 | PASS | 6.0597 | PASS | 5959.6897 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 24.8201 | PASS | 1.7195 | PASS | 1619.4794 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 40.893 | PASS | 14.7254 | PASS | 14625.4373 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 23.9694 | PASS | 5.4692 | PASS | 5369.217 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 23.5502 | PASS | 5.46 | PASS | 5360.0202 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 9.4841 | PASS | 0.2605 | PASS | 160.4503 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 9.4841 | PASS | 0.2489 | PASS | 148.9456 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.277 | PASS | 11.7138 | PASS | 11613.8356 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 766261 [G20-007-TAP 345.00] CKT 1 | 12.277 | PASS | 11.7138 | PASS | 11613.8356 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 139.112 | PASS | 13.8705 | PASS | 13770.4646 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 14.1765 | PASS | 9.8584 | PASS | 9758.3907 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 27.278 | PASS | 11.0762 | PASS | 10976.1853 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 20.5345 | PASS | 11.8822 | PASS | 11782.2204 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 6.0202 | PASS | 23.2117 | PASS | 23111.7126 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 6.0202 | PASS | 23.2117 | PASS | 23111.7126 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 6.0202 | PASS | 46.7681 | PASS | 46668.1171 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 11.0061 | PASS | 36.545 | PASS | 36445.0272 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 11.0061 | PASS | 36.545 | PASS | 36445.0272 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 13.592 | PASS | 0.3027 | PASS | 202.6824 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 15.5265 | PASS | 5.0444 | PASS | 4944.3619 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 26.0278 | PASS | 1.6866 | PASS | 1586.6073 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 26.0278 | PASS | 1.6866 | PASS | 1586.6073 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 21.1109 | PASS | 2.9856 | PASS | 2885.5555 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 24.8226 | PASS | 6.0601 | PASS | 5960.0701 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 24.8226 | PASS | 1.7195 | PASS | 1619.4544 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 40.9007 | PASS | 14.7199 | PASS | 14619.8555 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 23.9766 | PASS | 5.4617 | PASS | 5361.72 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 23.557 | PASS | 5.4527 | PASS | 5352.6549 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 9.4875 | PASS | 0.2604 | PASS | 160.4431 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 9.4875 | PASS | 0.2489 | PASS | 148.9362 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 12.3277 | PASS | 11.7264 | PASS | 11626.4489 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542981 [LACYGNE7 345.00] TO BUS 543659 [LACYGNE2 69.000] TO BUS 543660 [LACYGN7_TER16.9000] CKT 7 | 12.3277 | PASS | 11.7264 | PASS | 11626.4489 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 139.1045 | PASS | 13.8709 | PASS | 13770.9337 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 14.1769 | PASS | 9.8588 | PASS | 9758.7564 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 27.278 | PASS | 11.0766 | PASS | 10976.581 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 20.5201 | PASS | 11.8819 | PASS | 11781.8773 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 6.0202 | PASS | 23.2121 | PASS | 23112.0816 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 6.0202 | PASS | 23.2121 | PASS | 23112.0816 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 6.0202 | PASS | 46.7737 | PASS | 46673.7289 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 11.006 | PASS | 36.545 | PASS | 36444.9586 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 11.006 | PASS | 36.545 | PASS | 36444.9586 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 13.5921 | PASS | 0.3026 | PASS | 202.5845 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 15.5259 | PASS | 5.0443 | PASS | 4944.298 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 25.9709 | PASS | 1.6868 | PASS | 1586.7987 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 25.9709 | PASS | 1.6868 | PASS | 1586.7987 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 21.1095 | PASS | 2.9852 | PASS | 2885.1702 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 24.8224 | PASS | 6.0599 | PASS | 5959.9335 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 24.8224 | PASS | 1.7195 | PASS | 1619.4635 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 40.8719 | PASS | 14.7205 | PASS | 14620.4581 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 23.9626 | PASS | 5.4621 | PASS | 5362.0818 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 23.5554 | PASS | 5.4525 | PASS | 5352.461 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 9.4824 | PASS | 0.2604 | PASS | 160.4454 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 9.4824 | PASS | 0.2489 | PASS | 148.939 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 12.3275 | PASS | 11.7267 | PASS | 11626.7251 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 1 | 12.3275 | PASS | 11.7267 | PASS | 11626.7251 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 139.1068 | PASS | 13.871 | PASS | 13770.9663 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 14.177 | PASS | 9.8588 | PASS | 9758.766 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 27.2783 | PASS | 11.0766 | PASS | 10976.5934 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 20.522 | PASS | 11.8819 | PASS | 11781.9022 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 6.0202 | PASS | 23.2121 | PASS | 23112.0938 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 6.0202 | PASS | 23.2121 | PASS | 23112.0938 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 6.0202 | PASS | 46.7736 | PASS | 46673.6117 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 11.006 | PASS | 36.545 | PASS | 36444.9731 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 11.006 | PASS | 36.545 | PASS | 36444.9731 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 13.5922 | PASS | 0.3026 | PASS | 202.5811 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 15.526 | PASS | 5.0443 | PASS | 4944.3285 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 25.9768 | PASS | 1.6866 | PASS | 1586.6069 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 25.9768 | PASS | 1.6866 | PASS | 1586.6069 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 21.1097 | PASS | 2.9852 | PASS | 2885.2224 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 24.8222 | PASS | 6.0599 | PASS | 5959.88 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 24.8222 | PASS | 1.7195 | PASS | 1619.4671 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 40.8737 | PASS | 14.7198 | PASS | 14619.7859 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 23.9634 | PASS | 5.4612 | PASS | 5361.2274 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 23.5551 | PASS | 5.4521 | PASS | 5352.07 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 9.4831 | PASS | 0.2604 | PASS | 160.445 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 9.4831 | PASS | 0.2489 | PASS | 148.9384 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 12.3276 | PASS | 11.7267 | PASS | 11626.7461 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 532772 [STRANGR7 345.00] CKT 2 | 12.3276 | PASS | 11.7267 | PASS | 11626.7461 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 139.0564 | PASS | 13.8651 | PASS | 13765.0585 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 14.1713 | PASS | 9.856 | PASS | 9756.0009 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 27.2671 | PASS | 11.0732 | PASS | 10973.1657 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 20.5253 | PASS | 11.8805 | PASS | 11780.4503 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 6.0185 | PASS | 23.2086 | PASS | 23108.5699 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 6.0185 | PASS | 2321% | PASS | 23108.5699 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 6.0185 | PASS | 46.7652 | PASS | 46665.239 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 11.0013 | PASS | 3654% | PASS | 36438.3996 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 11.0013 | PASS | 36.5384 | PASS | 36438.3996 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 13.5873 | PASS | 0.3033 | PASS | 203.33 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 15.5224 | PASS | 5.0384 | PASS | 4938.4058 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 25.9798 | PASS | 1.6811 | PASS | 1581.1443 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 25.9798 | PASS | 1.6811 | PASS | 1581.1443 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 21.0805 | PASS | 2.967 | PASS | 2866.9703 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 24.821 | PASS | 6.0593 | PASS | 5959.2728 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 24.821 | PASS | 1.7195 | PASS | 1619.5078 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 40.8328 | PASS | 14.6991 | PASS | 14599.111 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 23.9423 | PASS | 5.4346 | PASS | 5334.6291 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 23.5338 | PASS | 5.4365 | PASS | 5336.5118 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 9.4796 | PASS | 0.2604 | PASS | 160.4382 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 9.4796 | PASS | 0.2489 | PASS | 148.9296 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 12.3234 | PASS | 11.7233 | PASS | 11623.2583 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541400 [EASTOWN7 345.00] CKT 1 | 12.3234 | PASS | 11.7233 | PASS | 11623.2583 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 139.3405 | PASS | 13.8951 | PASS | 13795.0995 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 14.2012 | PASS | 9.8703 | PASS | 9770.2816 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 27.3236 | PASS | 11.0902 | PASS | 10990.2206 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 20.5265 | PASS | 11.8841 | PASS | 11784.1231 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 6.0268 | PASS | 23.2252 | PASS | 23125.1599 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 6.0268 | PASS | 23.2252 | PASS | 23125.1599 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 6.0268 | PASS | 46.8037 | PASS | 46703.707 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 11.0082 | PASS | 36.5485 | PASS | 36448.5255 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 11.0082 | PASS | 36.5485 | PASS | 36448.5255 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 13.6113 | PASS | 0.2998 | PASS | 199.7736 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 15.5326 | PASS | 5.0547 | PASS | 4954.697 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 25.633 | PASS | 1.6879 | PASS | 1587.927 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 25.633 | PASS | 1.6879 | PASS | 1587.927 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 21.1124 | PASS | 2.9886 | PASS | 2888.5894 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 24.8068 | PASS | 6.0548 | PASS | 5954.7515 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 24.8068 | PASS | 1.7198 | PASS | 1619.8086 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 40.6537 | PASS | 14.7244 | PASS | 14624.4394 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 23.8223 | PASS | 5.4674 | PASS | 5367.4347 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 23.4916 | PASS | 5.453 | PASS | 5352.9955 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 9.4991 | PASS | 0.2605 | PASS | 160.461 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 9.4991 | PASS | 0.249 | PASS | 148.9596 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 12.348 | PASS | 11.7423 | PASS | 11642.3209 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542957 [IAT G1 1 24.000] CKT 1 | 12.348 | PASS | 11.7423 | PASS | 11642.3209 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 139.3905 | PASS | 13.9004 | PASS | 13800.3533 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 14.206 | PASS | 9.8726 | PASS | 9772.5993 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 27.3322 | PASS | 11.0929 | PASS | 10992.8989 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 20.5218 | PASS | 11.8831 | PASS | 11783.1059 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 6.028 | PASS | 23.2276 | PASS | 23127.5774 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 6.028 | PASS | 23.2276 | PASS | 23127.5774 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 6.028 | PASS | 46.8104 | PASS | 46710.4112 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 11.0084 | PASS | 36.5489 | PASS | 36448.9159 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 11.0084 | PASS | 36.5489 | PASS | 36448.9159 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 13.6151 | PASS | 0.2992 | PASS | 199.2046 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 15.5336 | PASS | 5.0564 | PASS | 4956.4053 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 25.4705 | PASS | 1.6798 | PASS | 1579.8432 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 25.4705 | PASS | 1.6798 | PASS | 1579.8432 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 21.1112 | PASS | 2.9883 | PASS | 2888.2614 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 24.7958 | PASS | 6.05 | PASS | 5950.0226 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 24.7958 | PASS | 1.7201 | PASS | 1620.1243 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 40.4992 | PASS | 14.6951 | PASS | 14595.1042 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 23.7353 | PASS | 5.4273 | PASS | 5327.3308 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 23.4477 | PASS | 5.4311 | PASS | 5331.0643 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 9.5017 | PASS | 0.2605 | PASS | 160.4644 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 9.5017 | PASS | 0.249 | PASS | 148.9641 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 12.3524 | PASS | 11.7457 | PASS | 11645.7307 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 542962 [IAT G2 1 24.500] CKT 1 | 12.3524 | PASS | 11.7457 | PASS | 11645.7307 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 139.1182 | PASS | 13.8711 | PASS | 13771.0574 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 14.1778 | PASS | 9.8589 | PASS | 9758.9346 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 27.2806 | PASS | 11.0768 | PASS | 10976.7793 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 20.5345 | PASS | 11.8824 | PASS | 11782.3741 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 6.0206 | PASS | 23.2123 | PASS | 23112.2682 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 6.0206 | PASS | 23.2123 | PASS | 23112.2682 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 6.0206 | PASS | 46.7723 | PASS | 46672.2515 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 11.0061 | PASS | 36.5451 | PASS | 36445.0681 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 11.0061 | PASS | 36.5451 | PASS | 36445.0681 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 13.5931 | PASS | 0.3026 | PASS | 202.563 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 15.5265 | PASS | 5.0444 | PASS | 4944.3973 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 24.4123 | PASS | 1.6771 | PASS | 1577.0528 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 24.4123 | PASS | 1.6771 | PASS | 1577.0528 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 21.1109 | PASS | 2.9856 | PASS | 2885.6067 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 24.8183 | PASS | 6.0585 | PASS | 5958.4521 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 24.8183 | PASS | 1.7196 | PASS | 1619.5624 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 39.9595 | PASS | 14.6878 | PASS | 14587.8264 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 23.4701 | PASS | 5.4192 | PASS | 5319.2457 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 23.5014 | PASS | 5.441 | PASS | 5341.0448 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 9.4875 | PASS | 0.2604 | PASS | 160.4433 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 9.4875 | PASS | 0.2489 | PASS | 148.9364 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 12.3281 | PASS | 11.7268 | PASS | 11626.7617 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 542982 [IATAN 7 345.00] TO BUS 541350 [IATAN5 161.00] TO BUS 541150 [IATAN 11 14.400] CKT 11 | 12.3281 | PASS | 11.7268 | PASS | 11626.7617 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 139.121 | PASS | 13.8713 | PASS | 13771.3015 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.9064 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 27.2805 | PASS | 11.0768 | PASS | 10976.7757 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.28 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2917 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2917 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 6.0206 | PASS | 46.7721 | PASS | 46672.0812 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1925 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1925 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.541 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6471 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 25.6715 | PASS | 1.687 | PASS | 1587.0126 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 25.6715 | PASS | 1.687 | PASS | 1587.0126 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 21.1113 | PASS | 2.9858 | PASS | 2885.847 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 24.8222 | PASS | 6.06 | PASS | 5959.9826 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 24.8222 | PASS | 1.7195 | PASS | 1619.4603 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 40.7119 | PASS | 14.7211 | PASS | 14621.1157 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 22.188 | PASS | 5.4626 | PASS | 5362.5717 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 23.5388 | PASS | 5.4529 | PASS | 5352.894 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 12.3284 | PASS | 11.727 | PASS | 11626.9547 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543018 [NKANCTY5 161.00] CKT 1 | 12.3284 | PASS | 11.727 | PASS | 11626.9547 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 139.1214 | PASS | 13.8713 | PASS | 13771.3304 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.906 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 27.2806 | PASS | 11.0768 | PASS | 10976.7793 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2753 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.3018 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.3018 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 6.0206 | PASS | 46.7721 | PASS | 46672.0988 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1936 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1936 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 13.5933 | PASS | 0.3025 | PASS | 202.5377 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 15.5267 | PASS | 5.0447 | PASS | 4944.6726 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 25.558 | PASS | 1.6841 | PASS | 1584.0728 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 25.558 | PASS | 1.6841 | PASS | 1584.0728 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 21.1113 | PASS | 2.9858 | PASS | 2885.8326 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 24.8234 | PASS | 6.0605 | PASS | 5960.547 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 24.8234 | PASS | 1.7194 | PASS | 1619.4225 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 40.6997 | PASS | 14.7129 | PASS | 14612.9377 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 22.1832 | PASS | 5.3968 | PASS | 5296.7972 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 23.5323 | PASS | 5.4609 | PASS | 5360.9229 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 12.3285 | PASS | 11.727 | PASS | 11626.9774 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543015 [AVONDAL5 161.00] TO BUS 543027 [RANDLPH5 161.00] CKT 1 | 12.3285 | PASS | 11.727 | PASS | 11626.9774 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 139.1217 | PASS | 13.8714 | PASS | 13771.3694 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 14.178 | PASS | 9.8591 | PASS | 9759.0504 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 27.2811 | PASS | 11.0769 | PASS | 10976.9386 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 20.5346 | PASS | 11.8823 | PASS | 11782.2522 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 6.0207 | PASS | 23.2124 | PASS | 23112.4316 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 6.0207 | PASS | 23.2124 | PASS | 23112.4316 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 6.0207 | PASS | 46.7724 | PASS | 46672.379 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2319 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.2319 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 13.5934 | PASS | 0.3025 | PASS | 202.5198 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 15.5266 | PASS | 5.0446 | PASS | 4944.6023 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 22.7717 | PASS | 1.6826 | PASS | 1582.5514 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 22.7717 | PASS | 1.6826 | PASS | 1582.5514 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 21.1116 | PASS | 2.986 | PASS | 2885.9845 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 24.8206 | PASS | 6.0592 | PASS | 5959.1939 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 24.8206 | PASS | 1.7195 | PASS | 1619.5129 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 39.2217 | PASS | 14.7051 | PASS | 14605.0943 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 14.0503 | PASS | 5.315 | PASS | 5214.9786 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 23.5465 | PASS | 5.4478 | PASS | 5347.8458 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 9.4879 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 9.4879 | PASS | 0.2489 | PASS | 148.9367 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 12.3285 | PASS | 11.727 | PASS | 11626.972 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543016 [GLADSTN5 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 12.3285 | PASS | 11.727 | PASS | 11626.972 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 139.0859 | PASS | 13.8677 | PASS | 13767.7446 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 14.1737 | PASS | 9.857 | PASS | 9757.0381 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 27.2727 | PASS | 11.0746 | PASS | 10974.5712 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 20.5341 | PASS | 11.8821 | PASS | 11782.083 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 6.0195 | PASS | 23.2102 | PASS | 23110.212 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 6.0195 | PASS | 23.2102 | PASS | 23110.212 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 6.0195 | PASS | 46.7676 | PASS | 46667.6244 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 11.0059 | PASS | 36.5447 | PASS | 36444.6936 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 11.0059 | PASS | 36.5447 | PASS | 36444.6936 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 13.59 | PASS | 0.303 | PASS | 202.9876 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 15.5257 | PASS | 5.0432 | PASS | 4943.2098 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 26.0011 | PASS | 1.6911 | PASS | 1591.0645 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 26.0011 | PASS | 1.6911 | PASS | 1591.0645 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 21.1109 | PASS | 2.9854 | PASS | 2885.4385 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 24.8256 | PASS | 6.0616 | PASS | 5961.5966 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 24.8256 | PASS | 1.7194 | PASS | 1619.3526 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 40.9106 | PASS | 14.7348 | PASS | 14634.7611 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 23.9165 | PASS | 5.473 | PASS | 5373.0223 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 23.5619 | PASS | 5.4611 | PASS | 5361.0552 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 9.4856 | PASS | 0.2604 | PASS | 160.4412 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 9.4856 | PASS | 0.2489 | PASS | 148.9337 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 12.3254 | PASS | 11.7247 | PASS | 11624.6769 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543022 [CLAYCM15 161.00] TO BUS 543029 [SHOLCRK5 161.00] CKT 1 | 12.3254 | PASS | 11.7247 | PASS | 11624.6769 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 139.1062 | PASS | 13.8698 | PASS | 13769.824 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 14.176 | PASS | 9.8581 | PASS | 9758.1145 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 27.2772 | PASS | 11.0758 | PASS | 10975.8419 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 20.5345 | PASS | 11.8822 | PASS | 11782.2052 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 6.0201 | PASS | 23.2114 | PASS | 23111.4186 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 6.0201 | PASS | 23.2114 | PASS | 23111.4186 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 6.0201 | PASS | 46.7702 | PASS | 46670.1718 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36444.9829 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 11.0061 | PASS | 36.545 | PASS | 36444.9829 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 13.5919 | PASS | 0.3027 | PASS | 202.7291 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 15.5264 | PASS | 5.0441 | PASS | 4944.0619 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 26.0302 | PASS | 1.6874 | PASS | 1587.369 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 26.0302 | PASS | 1.6874 | PASS | 1587.369 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 21.1112 | PASS | 2.9856 | PASS | 2885.645 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 24.8245 | PASS | 6.061 | PASS | 5960.9924 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 24.8245 | PASS | 1.7194 | PASS | 1619.3928 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 40.9085 | PASS | 14.7234 | PASS | 14623.3981 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 23.9812 | PASS | 5.4678 | PASS | 5367.765 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 23.5631 | PASS | 5.4604 | PASS | 5360.41 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 9.487 | PASS | 0.2604 | PASS | 160.4425 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 9.487 | PASS | 0.2489 | PASS | 148.9354 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 12.3272 | PASS | 11.726 | PASS | 11626.0112 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543023 [CLAYCM25 161.00] TO BUS 543020 [BRMGHAM5 161.00] CKT 1 | 12.3272 | PASS | 11.726 | PASS | 11626.0112 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 139.1207 | PASS | 13.8713 | PASS | 13771.27 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 14.1777 | PASS | 9.8589 | PASS | 9758.8822 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 27.2804 | PASS | 11.0767 | PASS | 10976.7452 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 20.5347 | PASS | 11.8823 | PASS | 11782.2802 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2652 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 6.0206 | PASS | 23.2123 | PASS | 23112.2652 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 6.0206 | PASS | 46.772 | PASS | 46672.0047 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1712 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 11.0062 | PASS | 36.5452 | PASS | 36445.1712 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 13.5932 | PASS | 0.3025 | PASS | 202.5473 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 15.5267 | PASS | 5.0446 | PASS | 4944.6311 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 25.8364 | PASS | 168.7% | PASS | 1586.5002 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 25.8364 | PASS | 1.6865 | PASS | 1586.5002 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 21.1113 | PASS | 298.6% | PASS | 2885.7922 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 24.8223 | PASS | 6.0599 | PASS | 5959.93 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 24.8223 | PASS | 1.7195 | PASS | 1619.4638 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 40.8079 | PASS | 14.7194 | PASS | 14619.4405 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 23.9372 | PASS | 5.4605 | PASS | 5360.5473 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 23.5564 | PASS | 5.4523 | PASS | 5352.2592 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9367 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 1 | 12.3284 | PASS | 11.7269 | PASS | 11626.9367 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 139.1207 | PASS | 13.8713 | PASS | 13771.2698 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 14.1777 | PASS | 9.8589 | PASS | 9758.882 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 27.2804 | PASS | 11.0767 | PASS | 10976.745 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 20.5347 | PASS | 11.8823 | PASS | 11782.2799 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 6.0206 | PASS | 23.2123 | PASS | 23112.2646 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 6.0206 | PASS | 23.2123 | PASS | 23112.2646 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 6.0206 | PASS | 46.772 | PASS | 46672.0001 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.171 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 11.0062 | PASS | 36.5452 | PASS | 36445.171 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-054 | Wolf Creek - Blackberry 345 kV Tap | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 13.5932 | PASS | 0.3025 | PASS | 202.5474 | 200 | 230.85
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-065 | tap on Arthur Mullergreen-Spearville 230 kV line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 15.5267 | PASS | 5.0446 | PASS | 4944.6311 | 145 | 162.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 25.8391 | PASS | 1.6865 | PASS | 1586.5022 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-073 | Nashua 161 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 25.8391 | PASS | 1.6865 | PASS | 1586.5022 | 149.98 | 170.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-075 | Tap on the Spearville - Post Rock 345kV line | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 21.1113 | PASS | 2.9858 | PASS | 2885.7918 | 175 | 193.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 24.8223 | PASS | 6.0599 | PASS | 5959.9305 | 50.89 | 93.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-100 | Overton - Sedalia East 161 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 24.8223 | PASS | 1.7195 | PASS | 1619.4637 | 29.11 | 53.55
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-102 | Liberty West 161 kV | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 40.8093 | PASS | 14.7194 | PASS | 14619.4481 | 100 | 112.67
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-142 | Shoal Creek 161 kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 23.9377 | PASS | 5.4606 | PASS | 5360.5646 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-144 | Blue Mills BESS 161kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 23.5564 | PASS | 5.4523 | PASS | 5352.2641 | 210.4 | 240
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 9.488 | PASS | 0.2604 | PASS | 160.4435 | 155.82 | 195.29
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-161 | Burns 345kV Substation | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 9.488 | PASS | 0.2489 | PASS | 148.9366 | 204.18 | 255.89
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 12.3284 | PASS | 11.7269 | PASS | 11626.9366 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-214 | Gill - Viola 138 kV Line Break | OPEN LINE FROM BUS 543039 [FRSTCRK5 161.00] TO BUS 543028 [NASHUA-5 161.00] CKT 2 | 12.3284 | PASS | 11.7269 | PASS | 11626.9366 | 119.5 | 138.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-004 | Murray Gill 138 kV Substation | OPEN LINE FROM BUS 543116 [BLUEMLS2 69.000] TO BUS 543004 [BLUMILS5 161.00] TO BUS 543117 [BLUMILS_TER112.500] CKT 3 | 139.1164 | PASS | 13.8708 | PASS | 13770.8368 | 33 | 40.1
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-005 | Northeast Parsons 138kV Substation | OPEN LINE FROM BUS 543116 [BLUEMLS2 69.000] TO BUS 543004 [BLUMILS5 161.00] TO BUS 543117 [BLUMILS_TER112.500] CKT 3 | 14.1772 | PASS | 9.8586 | PASS | 9758.6494 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-006 | Neosho - N345 161 kV Substation | OPEN LINE FROM BUS 543116 [BLUEMLS2 69.000] TO BUS 543004 [BLUMILS5 161.00] TO BUS 543117 [BLUMILS_TER112.500] CKT 3 | 27.2794 | PASS | 11.0765 | PASS | 10976.4719 | 200 | 224.56
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-007 | Lang - Reading 115 kV Transmission Line | OPEN LINE FROM BUS 543116 [BLUEMLS2 69.000] TO BUS 543004 [BLUMILS5 161.00] TO BUS 543117 [BLUMILS_TER112.500] CKT 3 | 20.5346 | PASS | 11.8823 | PASS | 11782.2585 | 135 | 152.38
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543116 [BLUEMLS2 69.000] TO BUS 543004 [BLUMILS5 161.00] TO BUS 543117 [BLUMILS_TER112.500] CKT 3 | 6.0204 | PASS | 23.212 | PASS | 23112.0106 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-013 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543116 [BLUEMLS2 69.000] TO BUS 543004 [BLUMILS5 161.00] TO BUS 543117 [BLUMILS_TER112.500] CKT 3 | 6.0204 | PASS | 23.212 | PASS | 23112.0106 | 150 | 169.2
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-024 | Tap of Neosho - LaCygne 345 kV Line | OPEN LINE FROM BUS 543116 [BLUEMLS2 69.000] TO BUS 543004 [BLUMILS5 161.00] TO BUS 543117 [BLUMILS_TER112.500] CKT 3 | 6.0204 | PASS | 46.7715 | PASS | 46671.4513 | 200 | 219.6
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543116 [BLUEMLS2 69.000] TO BUS 543004 [BLUMILS5 161.00] TO BUS 543117 [BLUMILS_TER112.500] CKT 3 | 11.0061 | PASS | 36.5451 | PASS | 36445.1128 | 135 | 154.8
DISIS-2022-001 | 03 CENTRAL | 25SP | GEN-2022-015 | Tap of Mingo - Red Willow 345 kV Line | OPEN LINE FROM BUS 543116 [BLUEMLS2 69.000] TO BUS 543004 [BLUMILS5 161.00] TO BUS 543117 [BLUMILS_TER112.500] CKT 3 | 11.0061 | PASS | 36.5451 | PASS | 36445.1128 | 135 | 154.8