## Executive Summary
Executive Summary: GEN-2022-147 Limited Operation System Impact (LOSIS) Study
Interconnection Customer (GEN-2022-147) has requested a Limited Operation System Impact Study (LOSIS) under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions at the time of service to determine the amount of Interconnection Capacity available to the interconnection customers listed under specific system conditions.
Once a GIA amendment to incorporate Limited Operation is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Limited Operation in accordance with the SPP study results.
Limited Operation
In accordance with Section 8.4.3 of the GIP, Availability of Limited Operation, SPP determines in the DISIS whether the full amount of interconnection capacity requested by the Interconnection Customers is available by the requested Commercial Operation Date (COD). SPP quantifies, within the “Requests” tab of the DISIS report, the amount of interconnection capacity available to Interconnection Customers prior to the in-service date of identified Network Upgrades.
In accordance with GIA Article 5.9, Limited Operation, Interconnection Customers may request SPP to perform studies to determine the Limited Operation of each Generating Facility prior to the completion of the identified mitigation for the observed system constraint(s).
Limited Operation conditions and amounts permitted as determined in this study are detailed in the Seasonal LOIS Tab.
Study Limitations
The study has been performed excluding upgrades that are not expected to be in service by the request's COD (12/11/2026). SPP's 2Q 2026 Quarterly Project Tracking Report and DISIS reports has been used to determine the upgrades meeting the criteria for exclusion.
Limited Operation Interconnection Service Available between April 1 - May 31 : 0 MW
Limited Operation Interconnection Service Available between June 1 - Sept 30 : 0 MW
Limited Operation Interconnection Service Available between Oct 1 - Nov 30 : 0 MW
Limited Operation Interconnection Service Available between Dec 1 - March 31 : 0 MW
In the event that an Interconnection Request, with queue priority equal to or higher than an Interconnection Request, which was excluded as a study scenario achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study scenario is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 4.4
https://spp.org/media/2400/gi-manual-business-practice_7250_20251017.pdf
Models Used in Study
Power Flow Analysis: DISIS-2022-001 Phase 2 Restudy 1 (2022 ITP Series)* * modified to exclude network upgrades assigned through DISIS-1701 to DISIS-2021. This model excludes upgrades assigned through DISIS-2022..
Summer: 2024 (24SP), 2027 (27SP)
Winter: 2027 (27WP)
Stability Analysis: DISIS-2022-001 Phase 2 Restudy 1 (2020 Series MDWG Dynamics)* * modified to exclude network upgrades assigned through DISIS-1701 to DISIS-2202.
Summer: 2025 (25SP)
Winter: 2025 (25WP)
Short Circuit Analysis: DISIS-2022-001 Phase 2 Restudy 1 (2020 Series MDWG Dynamics)* * modified to exclude network upgrades assigned through DISIS-1701 to DISIS-2202.
Summer: 2025 (25SP)
Author: SPP Generator Interconnection Department
Published: 8/27/2026

## Revision History
Revision History
Date | Author | Change Description
2026-08-21 | SPP | Draft

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
LOIS Amount
Gen Number | Group | Queue | Queue Order | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirements (MVAR) | Service | Area | POI | Status
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal: CTG | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ER | SPS | Tuco 345kV | DISIS STAGE
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal: CTG | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | DISIS STAGE
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | DISIS STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | DISIS STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | DISIS STAGE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | DISIS STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua 161 kV Substation | DISIS STAGE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | DISIS STAGE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Hybrid: Solar and Storage | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | DISIS STAGE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | DISIS STAGE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | DISIS STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | DISIS STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | DISIS STAGE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | DISIS STAGE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OGE | Woodward 345 kV Substation | DISIS STAGE
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OGE | Woodward 345kV Substation | DISIS STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OGE | Woodward 345kV Substation | DISIS STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEP | Longwood to Scottville 138 kV line | DISIS STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | DISIS STAGE
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEP | Talawanda to Canadian River 138 kV Line Tap | DISIS STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OGE | Bison 345kV Substation | DISIS STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | DISIS STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Hybrid: Solar and Storage | 150 | [9 empty] | ER/NR | AEP | Wilkes 345 kV Substation | DISIS STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OGE | Battlefield BESS 161kV | DISIS STAGE
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | DISIS STAGE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEP | Pirkey 345kV Substation | DISIS STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OGE | Caney Creek 138 kV Substation | DISIS STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEP | Weatherford Jct. to Hinton 138 kV line | DISIS STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | DISIS STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OGE | Horseshoe Lake 138 kV Substation | DISIS STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | DISIS STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEP | Northeastern - Delaware 345 kV transmission line | DISIS STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | DISIS STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OGE | Maud 138 kV substation | DISIS STAGE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
J1846 | 01 NORTH | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 200 | [9 empty] | ER/NR | XEL | Panther 230kV Substation | Active: Study Not Started
J1847 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | SMMPA | Murphy Creek 161kV substation | Active: Study Not Started
J1888 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 175 | [9 empty] | ER/NR | MP | SQUARE BUTTE EAST 230 kV (AC side) | Active: Study Not Started
J1893 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 500 | [9 empty] | ER/NR | MDU | Mandan 230 kV | Active: Study Not Started
J1898 | 01 NORTH | 23.5 | DIS-22-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL | BYRON | Active: Study Not Started
J1952 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 180 | [9 empty] | ER/NR | ALTW | Emery-Floyd 161kV | Active: Study Not Started
J1961 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 190 | [9 empty] | ER/NR | OTP | Buffalo 115kV | Active: Study Not Started
J1978 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 170 | [9 empty] | ER/NR | MEC | Lemars Tap-Little Sioux 161kV | Active: Study Not Started
J1979 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW | Hazleton-Mitchell County 345kV line | Active: Study Not Started
J1989 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [9 empty] | ER/NR | OTP | Twin Brooks-Ellendale 345kV | Active: Study Not Started
J1990 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 215 | [9 empty] | ER/NR | MDU | Ellendale 345kV | Active: Study Not Started
J2021 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 48.43 | [9 empty] | ER/NR | XEL | Tremval 69kV | Active: Study Not Started
J2022 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Pleasant Valley 345 kV Substation | Active: Study Not Started
J2027 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 150 | [9 empty] | ER/NR | GRE | Chub Lake - Hampton Corners 345 kV Line [See Operating Agreement 5 for Correction Discussion] | Active: Study Not Started
J2030 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 56 | [9 empty] | ER/NR | GRE | ISANTTI TAP to ATHNSSW 69kV | Active: Study Not Started
J2040 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 150 | [9 empty] | ER/NR | MEC | Lakefield - Obrien Co 345 kV (43.497803, -95.318336) | Active: Study Not Started
J2053 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 151.47 | [9 empty] | ER/NR | XEL | Lyon County to Cedar Mountain 345kV | Active: Study Not Started
J2065 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Buffalo Ridge to Pipestone 115kV | Active: Study Not Started
J2068 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 75 | [9 empty] | ER/NR | XEL | Herbert 69 kV Substation | Active: Study Not Started
J2080 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 200 | [9 empty] | ER/NR | MP | Square Butte East 230 kV | Active: Study Not Started
J2084 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 45 | [9 empty] | ER/NR | MDU | Linton NW (not in power flow case yet) | Active: Study Not Started
J2085 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 40 | [9 empty] | ER/NR | MDU | Linton NW 115 kV (radial to Wishek 115 kV) | Active: Study Not Started
J2086 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 500 | [9 empty] | ER/NR | OTP | Buffalo 345 kV | Active: Study Not Started
J2087 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 125 | [9 empty] | ER/NR | XEL | Franklin 115kV | Active: Study Not Started
J2088 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 400 | [9 empty] | ER/NR | XEL | WEST MEMPHIS EHV - KEO EHV 500 kV (854.0) | Active: Phase 1
J2097 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 100 | [9 empty] | ER/NR | MP | Tri-County 230 kV Substation | Active: Study Not Started
J2101 | 01 NORTH | 23.5 | DIS-22-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | MDU | Mandan 230 kV | Active: Study Not Started
J2104 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 230.01 | [9 empty] | ER/NR | XEL | Lyon County 345 kV - Cedar Mountain 345 kV | Active: Study Not Started
J2157 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 100 | [9 empty] | ER/NR | MP | Tri-County 230 kV Substation | Active: Study Not Started
J2199 | 01 NORTH | 23.5 | DIS-22-PQ | Battery/Storage | 200 | [9 empty] | ER/NR | XEL | COON CREEK | Active: Study Not Started
J2219 | 01 NORTH | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 180 | [9 empty] | ER/NR | DPC | Rochester - Wabaco 161kV Line (Dairyland Power) | Active: Study Not Started
J2227 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 89 | [9 empty] | ER/NR | DPC | N-3 Bridge Creek to Independence 69kV Line [See Operating Agreement 5 for Correction Discussion] | Active: Study Not Started
J2250 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 200 | [9 empty] | ER/NR | OTP | Ellendale sub 345 kV (46.009357, -98.567742) | Active: Study Not Started
J2276 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 39.5 | [9 empty] | ER/NR | OTP | Alexandria Tap | Active: Study Not Started
J2309 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Chanarambie - Ellsborough 115 kV line | Active: Study Not Started
MPC4500 | 01 NORTH | 23.5 | DIS-22-PQ | WIND | 250 | [9 empty] | ER/NR | OTP
J1889 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Solar | 60 | [9 empty] | ER/NR | ALTW | Mt Vernon Substation | Active: Study Not Started
J2031 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Wind | 100 | [9 empty] | ER/NR | ALTW | 161 kV Toledo Substation | Active: Study Not Started
J2078 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW | Fernald Substation | Active: Study Not Started
J2120 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Battery/Storage | 100 | [9 empty] | ER/NR | ALTW | Fairfax 161 kV | Active: Study Not Started
J2268 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Solar | 370 | [9 empty] | ER/NR | ALTW | Duane Arnold Energy Center | Active: Study Not Started
GIA-118 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | SOLAR | 32 | [9 empty] | ER/NR | AECI
J1849 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | EES | Cypress 230 kV | Active: Phase 1
J1855 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 500 | [9 empty] | ER/NR | EES-EAI | MALLORY 161 | Active: Phase 1
J1856 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 140 | [9 empty] | ER/NR | EES-EAI | SHOFFNER - NEWPORT | Active: Phase 1
J1858 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 440 | [9 empty] | ER/NR | EES-EAI | Sandy Bayou | Active: Phase 1
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW | Quinn | Active: Study Not Started
J1872 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | El Dorado 500kV Substation | Active: Phase 1
J1873 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | El Dorado 500kV Substation | Active: Phase 1
J1890 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 270 | [9 empty] | ER/NR | EES | Hartburg - AEP Layfield 500 kV | Active: Phase 1
J1891 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 200 | [9 empty] | ER/NR | EES-EMI | 230 kV McAdams Substation | Active: Phase 1
J1897 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 500 | [9 empty] | ER/NR | EES-EAI | Dell to San Souci 500kv line | Active: Phase 1
J1899 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 500 | [9 empty] | ER/NR | EES-EAI | Dell to San Souci 500kv line | Active: Phase 1
J1946 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 350 | [9 empty] | ER/NR | SMEPA | 230 kV Missionary Substation | Active: Phase 1
J2010 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 75 | [9 empty] | ER/NR | EES-EAI | Stuttgart Ricuskey to Woodward 230kV | Active: Phase 1
J2047 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 199 | [9 empty] | ER/NR | EES-EMI | Robinsonville 230 kV | Active: Phase 1
J2070 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 100 | [9 empty] | ER/NR | EES | Three Lakes - Pine Lake 115 kV | Active: Study Not Started
J2071 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 198 | [9 empty] | ER/NR | EES | Rye Co - Cypress 138kV | Active: Phase 1
J2075 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | EES | China (Bus# 334204) to Sheco Batiste Creek (Bus# 334240) | Active: Phase 1
J2089 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Line tap DELL to Manilla AECC 161 kV | Active: Phase 1
J2091 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Battery/Storage | 250 | [9 empty] | ER/NR | EES-EMI | TWINKLETOWN 230 KV | Active: Phase 1
J2127 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 172.5 | [9 empty] | ER/NR | SMEPA | Silver Creek 115kV | Active: Phase 1
J2133 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 100 | [9 empty] | ER/NR | EES-EAI | Garner 115 kV Substation | Active: Phase 1
J2134 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 195 | [9 empty] | ER/NR | EES-EAI | White Bluff EHV - Wrightsville 115 kV line | Active: Phase 1
J2143 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | Lake Village Bagby 115 KV | Active: Phase 1
J2149 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 112 | [9 empty] | ER/NR | EES-EAI | White Bluff - Mabelvale 115 kV line | Active: Phase 1
J2153 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 200 | [9 empty] | ER/NR | EES-EAI | Mist 115 kV substation | Active: Phase 1
J2165 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 145 | [9 empty] | ER | EES | JACINTO - SHECO BATISTE CREEK 230kV | Active: Phase 1
J2173 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 396 | [9 empty] | ER/NR | EES-EMI | Bolton 115 kV Substation | Active: Phase 1
J2180 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [9 empty] | ER/NR | CLEC | Fisher | Active: Phase 1
J2181 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | 161 kV line tap of DELL EAST to Blytheville | Active: Phase 1
J2190 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 500 | [9 empty] | ER/NR | EES-EAI | Dell to San Souci 500kv | Active: Phase 1
J2208 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 99 | [9 empty] | ER/NR | CLEC | Mansfield (Bus #500530) to Red River Tap (Bus #500762) 138 kV | Active: Phase 1
J2228 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | EES | Red Gum | Active: Phase 1
J2237 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 185 | [9 empty] | ER/NR | EES-EAI | Brinkley East - Aubrey 230 kV Line | Active: Phase 1
J2252 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 300 | [9 empty] | ER/NR | EES-EAI | Cash - Newport AB | Active: Phase 1
J2261 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 652 | [9 empty] | ER/NR | EES-EAI | Independence(A) (500kV)-Powerline(B) (500kV) | Active: Phase 1
J2262 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 652 | [9 empty] | ER/NR | EES-EAI | Independence(A) (500kV) -Powerline(B) (500kV) | Active: Phase 1
J2287 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 122 | [9 empty] | ER/NR | EES-EMI | DELTA SES SWITCHYARD 115kV | Active: Phase 1
J2289 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER | EES-EMI | Indianola | Active: Phase 1
J2292 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 50 | [9 empty] | ER/NR | LAGN | Goos Ferry | Active: Phase 1
J2294 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | Dell to Nucor 161 kV | Active: Phase 1
J2297 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 100 | [9 empty] | ER | EES-EMI | Indianola | Active: Phase 1
J2298 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | AECC Gainesville | Active: Phase 1
J2314 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 150 | [9 empty] | ER/NR | EES | Petry Woods | Active: Phase 1
J2317 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 202.5 | [9 empty] | ER/NR | EES | Sterlington - Bastrop 115 kV | Active: Phase 1
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | DISIS STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | DISIS STAGE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | DISIS STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | DISIS STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | DISIS STAGE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | DISIS STAGE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | DISIS STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | DISIS STAGE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | DISIS STAGE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | DISIS STAGE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | DISIS STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | DISIS STAGE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | DISIS STAGE
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | DISIS STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | DISIS STAGE
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Hybrid: Solar and Storage | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | DISIS STAGE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | DISIS STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | DISIS STAGE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | DISIS STAGE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | DISIS STAGE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | DISIS STAGE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | DISIS STAGE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | DISIS STAGE
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | DISIS STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | DISIS STAGE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Grand Prairie 161kV Substation | DISIS STAGE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | DISIS STAGE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | DISIS STAGE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | DISIS STAGE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | DISIS STAGE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | DISIS STAGE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | DISIS STAGE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | DISIS STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | DISIS STAGE
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | SOLAR/BATTERY/STORAGE | 50 | [9 empty] | ER/NR | SPS |  | DISIS STAGE
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | SOLAR/BATTERY/STORAGE | 40 | [9 empty] | ER/NR | SPS |  | DISIS STAGE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
J1519 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | St. Francois to Lutesville 345 kV | Active: Phase 2
J1649 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 60 | [9 empty] | ER/NR | BREC | McCracken County to Shell 69kV | Active: Phase 2
J1836 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 300 | [9 empty] | ER/NR | AMMO | Montgomery- Callaway- 7 | Active: Phase 2
GIA-116 | 04 SOUTHEAST | 22.5 | DIS-21-1-PQ | THERMAL | 26 | [9 empty] | ER/NR | AECI
GIA-117 | 04 SOUTHEAST | 22.5 | DIS-21-1-PQ | THERMAL | 46 | [9 empty] | ER/NR | AECI
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal: Gas | 45 | [9 empty] | ER/NR | BEPC | Lonesome Creek 115kV | DISIS STAGE
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Hybrid: Solar and Storage | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | DISIS STAGE
GEN-2020-002 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 81 | [9 empty] | ER | OPPD | 6846 Substation 69 kV | DISIS STAGE
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 320 | [9 empty] | ER/NR | NPPD | Axtell-Sweetwater Substation 345kV | DISIS STAGE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | DISIS STAGE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | DISIS STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | DISIS STAGE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | DISIS STAGE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | DISIS STAGE
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | SOLAR/BATTERY/STORAGE | 35 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | SOLAR/BATTERY/STORAGE | 35 | [9 empty] | ER | KCPL |  | DISIS STAGE
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Diesel and Gas | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | DISIS STAGE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | DISIS STAGE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | DISIS STAGE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Russell 115 kV Substation | DISIS STAGE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | DISIS STAGE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | DISIS STAGE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Gas | 21 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | DISIS STAGE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: CT | 64 | [9 empty] | ER/NR | EDE | 4544 Stateline CC 161kV Substation | DISIS STAGE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | DISIS STAGE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 225 | [9 empty] | ER/NR | EDE | Riverton-Neosho 161kV line | DISIS STAGE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EDE | La Russell 161 kV Substation | DISIS STAGE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | DISIS STAGE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | DISIS STAGE
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 113 | [9 empty] | ER/NR | AEP | Snyder â€“ Altus Jct. 138kV | DISIS STAGE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | DISIS STAGE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | DISIS STAGE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | DISIS STAGE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | DISIS STAGE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | DISIS STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal: Combined Cycle | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | DISIS STAGE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | Wind | 255 | [9 empty] | ER | BEPC-SPP | 115kV Strandahl sub | DISIS STAGE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.15 | [9 empty] | ER/NR | BEPC-SPP | Siouxland 69kV | DISIS STAGE
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC-SPP | Leland Olds 345kV substation | DISIS STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | DISIS STAGE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | DISIS STAGE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | DISIS STAGE
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | DISIS STAGE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | Wind | 200.22 | [9 empty] | ER/NR | WERE | Renfrow-Viola 345 kV | DISIS STAGE
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | DISIS STAGE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | DISIS STAGE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | DISIS STAGE
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | DISIS STAGE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | DISIS STAGE
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | DISIS STAGE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | DISIS STAGE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | DISIS STAGE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | DISIS STAGE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | DISIS STAGE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Hybrid: Solar and Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | DISIS STAGE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | DISIS STAGE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | DISIS STAGE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | DISIS STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
MPC4300 | 01 NORTH | 20.5 | DIS-18-2-PQ | WIND | 400 | [9 empty] | ER/NR | OTP
GIA-100 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 40 | [9 empty] | ER/NR | AECI
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 75 | [9 empty] | ER/NR | AECI
GIA-106 | 03 CENTRAL | 20.5 | DIS-19-1-PQ | SOLAR | 350.08 | [9 empty] | ER/NR | AECI
GIA-107 | 03 CENTRAL | 20.5 | DIS-19-1-PQ | SOLAR | 250 | [9 empty] | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-105 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 20 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 35 | [9 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | SOLAR | 35 | [9 empty] | ER | KCPL |  | DISIS STAGE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | AEPW | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER/NR | MDU | Wishek Junction 230 kV Substation | Done: Phase 3
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Battery/Storage | 20 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | Done: Phase 3
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Adams 345 kV Substation | Done: Phase 3
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Three Lakes 115 kV Substation | Done: Phase 3
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV Substation | Done: Phase 3
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER | ALTW | Magnolia 161 kV Substation | Done: Phase 3
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | XEL | Grant 115 kV Substation | Done: Phase 3
J1181 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW | Hazleton - Mitchell county 345 kV line | Done: Phase 3
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE | Wing River- Riverton 230kV line | Active: Phase 3
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | XEL | Grant 115 kV Substation | Done: Phase 3
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | DPC | Apple River 161 kV Substation | Done: Phase 3
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Benton County 115kV Substation | Done: Phase 3
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Mayhew Lake 115kV Substation | Done: Phase 3
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER | OTP | Astoria 345 kV Substation (J493/J510) | Active: Phase 3
J1503 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | Active: Phase 3
J1504 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | Active: Phase 3
J1534 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV | Active: Phase 3
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Rutland Substation 161kV | Active: Phase 3
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 150 | [9 empty] | ER/NR | XEL | Huntley to Blue Earth 161kV | Active: Phase 3
J1575 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 70 | [9 empty] | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | Active: Phase 3
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Nobles County 345 kV Substation | Active: Phase 3
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Bison 345kV | Active: Phase 3
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Sherburne 345kV | Active: Phase 3
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 120 | [9 empty] | ER/NR | XEL | Langola 115kV Tap | Active: Phase 3
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL | Pipestone to Split Rock 115kV | Active: Phase 3
J1657 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Pine Lake to Apple River 161 kV | Active: Phase 3
J1730 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | XEL | Eau Claire to AS King 345 kV | Active: Phase 3
J1769 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 80 | [9 empty] | ER/NR | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | Active: Phase 3
J1808 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 148 | [9 empty] | ER/NR | DPC | Barron 161 kV | Active: Phase 3
J1826 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hydro | 4 | [9 empty] | ER/NR | XEL | Cannon Falls Transmission 69 kV | Done: Phase 3
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | [9 empty] | ER/NR | XEL | Adams 345kV Substation | Done: Phase 3
MPC3600 | 01 NORTH | 19.5 | DIS-18-1-PQ | SOLAR | 170 | [9 empty] | ER | OTP
MPC3700 | 01 NORTH | 19.5 | DIS-18-1-PQ | SOLAR | 130 | [9 empty] | ER | OTP |  | DISIS STAGE
MPC3800 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 250 | [9 empty] | ER/NR | OTP |  | DISIS STAGE
MPC3900 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 151.2 | [9 empty] | ER/NR | OTP
MPC4000 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 300 | [9 empty] | ER/NR | OTP
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 | [9 empty] | ER/NR | ALTW | Doud Tap 161 kV Substation | Done: Phase 3
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | ALTW | Creston East 69 kV Substation | Done: Phase 3
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | Done: Phase 3
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 | [9 empty] | ER | ALTW | Ledyard - Colby 345kV Line Tap | Done: Phase 3
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | Kossuth - O'Brien 345 kV Line Tap | Done: Phase 3
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | ALTW | 161kV bus at Karma substation | Done: Phase 3
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Gas | 95 | [9 empty] | ER/NR | ALTW | Oakridge 69 kV Substation | Active: Phase 3
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 169.4 | [9 empty] | ER/NR | ALTW | Traer 161-kV Substation | Active: Phase 3
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW | Duane Arnold 345kV Substation | Active: Phase 3
J1520 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV | Active: Phase 3
J1529 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | Active: Phase 3
J1530 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | Active: Phase 3
J1532 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Clarinda-Coburg 69 kV | Active: Phase 3
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | O'Brien - Raun 345 kV | Active: Phase 3
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | Done: Phase 3
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 290 | [9 empty] | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | Done: GIA
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 380 | [9 empty] | ER/NR | AMMO | Spencer Creek 345 kV Substation | Done: GIA
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | Done: GIA
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Zachary Substation 345 kV Bus | Done: GIA
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 68.4 | [9 empty] | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | Done
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138 kV line | Done
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | Done
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hydro | 60 | [9 empty] | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | Done
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 185 | [9 empty] | ER/NR | AMIL | Ashley 138 kV Substation | Active
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | Done
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMMO | Pike - Troy 161kV Line | Done
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 95 | [9 empty] | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | Done
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMIL | Commodore-Jordan 345kV Line | Active
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | Active
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 500 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Active
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 1000 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Active
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Spencer Creek 345kV Substation | Done: GIA
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | Done: GIA
J987 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO | Montgomery 161kV Substation | Done: GIA
J994 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO | Guthrie 161 kV Substation | Done: GIA
GIA-96 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | WIND | 97.5 | [9 empty] | ER | AECI
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 180 | [9 empty] | ER/NR | EES-EAI | Marion - Marked Tree 161kV Line Tap | Done: GIA
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Poco - Menard 138kV Line Tao | Done: GIA
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | [9 empty] | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | Done: GIA
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 450 | [9 empty] | ER/NR | EES-EAI | West Memphis - Keo 500 kV Line Tap | Done: GIA
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | Done: GIA
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | Done: GIA
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV Line Tap | Done: GIA
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EAI | Driver 230 kV Substation | Done: GIA
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER | CLEC | Centennial - West Bay 138kV Line | Done: Phase 3
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 155 | [9 empty] | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | Done: Phase 3
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER | EES | Rilla 115 kV Substation | Done: Phase 3
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done: Phase 3
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 | [9 empty] | ER/NR | EES-EAI | Crossett - Monticello East 115kV Line | Done: Phase 3
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 149 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161kV Line | Done
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 | [9 empty] | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | Done: Phase 3
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 0 | [9 empty] | ER/NR | EES-EAI | Cash - Newport AB161kV Line | Done: Phase 3
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done: Phase 3
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER | CLEC | Cooper - Penton Road 230kV Line | Done: Phase 3
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | Done: Phase 3
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | EES | Oak Ridge 115 kV Substation | Done: Phase 3
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 180 | [9 empty] | ER/NR | EES-EAI | AECC Dry Creek 161kV Switchyard Station | Done: Phase 3
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 105 | [9 empty] | ER | EES | Rich (SHECO) - Livingston 138 kV Line Tap | Done: Phase 3
J1514 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Driver 230kV | Active: Phase 3
J1558 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | Active: Phase 3
J1559 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | Active: Phase 3
J1562 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | Active: Phase 3
J1577 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Hardin West SS (Endpoint A) to Sheridan (Endpoint B) 115 kV | Done: Phase 3
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 325 | [9 empty] | ER/NR | EES | Goos Ferry | Active: Phase 3
J1602 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 25 | [9 empty] | ER/NR | EES | Rilla 115kV substation (Same as J1239) | Active: Phase 3
J1612 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | Active: Phase 3
J1669 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | Active: Phase 3
J1670 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | Active: Phase 3
J1671 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Rocky Creek to Lewis Creek 230kV | Active: Phase 3
J1672 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EMI | Tinnin Road 230kV | Active: Phase 3
J1673 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | Active: Phase 3
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | Active: Phase 3
J1747 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EMI | J830 POI | Active: Phase 3
J1748 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EMI | Twinkletown 230 kV | Active: Phase 3
J1760 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 205 | [9 empty] | ER/NR | EES | Timberland 230kV | Active: Phase 3
J1816 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | Active: Phase 3
J1820 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | Active: Phase 3
J1827 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 90 | [9 empty] | ER/NR | EES | Bastrop tap point | Active: Phase 3
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Gas | 126 | [9 empty] | ER/NR | EES | Sabine 138/230 kV Substation | Active: Phase 3
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 135 | [9 empty] | ER | EES-EAI | Forrest City to Wynne S 161 KV | Active: Phase 3
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | [9 empty] | ER | XEL | Buffalo 115kV Substation | Done: Phase 3
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | OTP | Big Stone South 230kV Substation | Done: Phase 3
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | [9 empty] | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | Done: Phase 3
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line | Done: Phase 3
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | [9 empty] | ER | DPC | Rice - Beaver Creek 161kV line tap | Done: Phase 3
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 101.28 | [9 empty] | ER | XEL | Pine Lake - Apple River 161 kV Line | Done: Phase 3
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 57 | [9 empty] | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW | Murray Junction 69 kV substation | IA PENDING
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | ALTW | Ledyard 345kV Substation | Done: Phase 3
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 | [9 empty] | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | Done: Phase 3
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | [9 empty] | ER/NR | AECI | McCredie 345 kV
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | [9 empty] | ER/NR | AECI | Thomas Hill 69 kV
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | [9 empty] | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | [9 empty] | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | [9 empty] | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 | [9 empty] | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | WIND | 7.5 | [9 empty] | ER | BEPC-SPP
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | [9 empty] | ER | WAPA | NELSON 7
J718 | 01 NORTH | 17.5 | DIS-17-1-PQ | Solar | 49.98 | [9 empty] | ER/NR | DPC | Cherry Grove 69kV Substation | Done: GIA
J748 | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | Highland - Raun 345kV Line Tap | Done: GIA
NPPDSPRINGVIEW | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | WIND | 3 | [9 empty] | ER | NPPD
SPSLEACOUNTY | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | SOLAR | 5.5 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 298 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-124 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 150 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 74 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Thermal: Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
J569 | 01 NORTH | 16.5 | DIS-16-2-PQ | WIND | 100 | [9 empty] | ER/NR | XEL
J476 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | WIND | 246 | [9 empty] | ER/NR | AMMO
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC-SPP | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Thermal: Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Duro 115kV
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | BEPC-SPP | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-064 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 200.1 | [9 empty] | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery/Storage | 20 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 219.96 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 | [9 empty] | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 16 | [9 empty] | ER/NR | BEPC-SPP
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [9 empty] | ER/NR | WAPA | Nelson 115kV
GEN-2009-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 200 | [9 empty] | ER/NR | BEPC-SPP
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 | [9 empty] | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [9 empty] | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 34 | [9 empty] | ER/NR | BEPC-SPP
GEN-2014-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [9 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 3.96 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Hybrid: Solar and Wind | 73.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [9 empty] | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Hybrid: Solar and Wind | 50.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | WIND | 11.5 | [9 empty] | ER | SPS
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Clovis 115kV
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [9 empty] | ER | SPS | FE-Clovis Interchange 115kV
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | [9 empty] | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | Wind | 20 | [9 empty] | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | [9 empty] | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | [9 empty] | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 04 SOUTHEAST | 8 | PQ | Wind | 100 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 04 SOUTHEAST | 8 | PQ | Wind | 20.6 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 30.6 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 SOUTHWEST | 8 | PQ | Wind | 240 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland Â- Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
LLANOESTACADOWHITEDEER | 05 SOUTHWEST | 8 | PQ | WIND | 80 | [9 empty] | ER | SPS
SPSCARSON | 05 SOUTHWEST | 8 | PQ | WIND | 10 | [9 empty] | ER | SPS
SPSDUMAS19THST | 05 SOUTHWEST | 8 | PQ | WIND | 20 | [9 empty] | ER | SPS
SPSETTER | 05 SOUTHWEST | 8 | PQ | WIND | 20 | [9 empty] | ER | SPS
SPSMOOREE | 05 SOUTHWEST | 8 | PQ | WIND | 17.5 | [9 empty] | ER | SPS
SPSSHERMAN | 05 SOUTHWEST | 8 | PQ | WIND | 20 | [9 empty] | ER | SPS
SUNRAY | 05 SOUTHWEST | 8 | PQ | WIND | 34.5 | [9 empty] | ER | SPS
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [9 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | WIND | 19.8 | [9 empty] | ER | SPS
GEN-2011-027 | 02 NEBRASKA | 6 | DIS-11-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | WIND | 20 | [9 empty] | ER | SPS
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | WIND | 10 | [9 empty] | ER | SPS
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 5 | DIS-10-2 | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | WIND | 15 | [9 empty] | ER | SPS
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 48.3 | [9 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 29.7 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [9 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [9 empty] | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 SOUTHEAST | 2 | ICS1 | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 24SP | ERIS 27SP | ERIS 27L | ERIS 27WP | NRIS 24SP | NRIS 27SP | NRIS 27L | NRIS 27WP | Stability SP | Stability WP
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | April 1 - May 31 (Long Term) | 203 | 0 | Rotor Angle Instability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line | N/A | 0 | N/A | 203 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | April 1 - May 31 (Near Term) | 203 | 0 | Rotor Angle Instability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line | 0 | N/A | N/A | 203 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | Dec 1 - March 31 (Long Term) | 203 | 0 | Rotor Angle Instability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line | N/A | N/A | N/A | 203 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | Dec 1 - March 31 (Near Term) | 203 | 0 | Rotor Angle Instability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line | N/A | N/A | N/A | 203 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | June 1 - Sept 30 (Long Term) | 203 | 0 | Rotor Angle Instability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | June 1 - Sept 30 (Near Term) | 203 | 0 | Rotor Angle Instability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | Oct 1 - Nov 30 (Long Term) | 203 | 0 | Rotor Angle Instability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line | N/A | 0 | N/A | 203 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2022-147 | 05 SOUTHWEST | Thermal: CTG | Oct 1 - Nov 30 (Near Term) | 203 | 0 | Rotor Angle Instability | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line | 0 | N/A | N/A | 203 | N/A | N/A | N/A | N/A | 0 | 0

## Upgrade Removal Summary
NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Source Study | Included/Excluded? | Estimated In-Service Date / Lead Time (months)
210483 | 72023 | Multi - Park Community - Sunshine 138 kV | El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | DPA-2017-August-767-774-776 | Excluded | 2026-07-31
210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Excluded | 2026-09-30
210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Excluded | 2027-02-28
210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Excluded | 2027-02-28
210586 | 112443 | Line - Russett - South Brown 138 kV | Russett - South Brown 138 kV Ckt 1 Rebuild | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 2020 ITP | Excluded | 2027-10-31
210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Excluded | 2026-09-30
210708 | 156299 | Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | 36th & Lewis - 52nd & Delaware Tap 138 kV Ckt 1 Rebuild | Rebuild 138 kV line from 36th & Lewis to 52nd & Delaware Tap | 2022 ITP | Excluded | 2027-06-01
220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Excluded | 2026-12-31
220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Excluded | 2026-12-31
220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Excluded | 2026-12-31
220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Excluded | 2026-12-31
220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Excluded | 2026-12-31
220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Excluded | 2026-12-31
220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Excluded | 2027-12-31
220773 | 157396 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 3 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV substation to support a third line from Anadarko to Gracemont. | 2023 ITP | Excluded | 2028-05-31
220737 | 157518 | Line - Pine & Peoria Tap 138 kV - 46th Street Tap 138 kV - Tulsa North 138 kV Rebuild | Tulsa North 138 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Tulsa North 138 kV substation on the 46th Street Tap to Tulsa North 138 kV line to achieve a summer emergency rating of 278 MVA. | 2023 ITP | Excluded | 2027-01-21
220774 | 157530 | Line - Osage - Webb City Tap - Shidler 138 kV Rebuild | Osage 138 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Osage 138 kV substation on the Osage to Webb City Tap 138 kV line to achieve a summer emergency rating of 561 MVA. | 2023 ITP | Excluded | 2026-12-01
220826 | 157696 | Multi - Cunningham - Quahada 115 kV - Buckeye Tap New Line | Buckeye Tap 115 kV Ckt 1 Substation | Build new substation at Buckeye Tap, with four new 115 kV line terminals, connecting the 115 kV lines to Buckeye Substation, Lea County REC, Cunningham Substation to support a new 115 kV line to the new Cunningham - Quahada 115 kV Tap substation with a summer emergency rating of 239 MVA. | 2023 ITP | Excluded | 2029-10-15
220826 | 157794 | Multi - Cunningham - Quahada 115 kV - Buckeye Tap New Line | Buckeye Tap - Cunningham - Quahada 115 kV Ckt 1 New Line. | Build a new 3.2-mile 115 kV Ckt 1 line from the Buckeye Tap 115 kV substation to the Cunningham - Quahada 115 kV New Substation. | 2023 ITP | Excluded | 2029-10-15
220826 | 157796 | Multi - Cunningham - Quahada 115 kV - Buckeye Tap New Line | Cunningham - Quahada 115 kV New Substation | Build a new 115 kV substation 8 miles west of Cunningham, cut-into the Cunningham - Quahada 115 kV line, with three new 115 kV line terminals, connecting the 115 kV lines to Buckeye Tap, Cunningham and Quahada. | 2023 ITP | Excluded | 2029-10-15
220774 | 157880 | Line - Osage - Webb City Tap - Shidler 138 kV Rebuild | Webb City Tap - Osage 138 kV Ckt 1 Rebuild (OGE) | Rebuild 20 miles of 138 kV line from Webb City Tap 138 kV substation to Osage 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 561 MV | 2023 ITP | Excluded | 2026-12-01
220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Excluded | 2027-12-31
220772 | 158573 | Line - Mathewson 345 kV - Redbud 345 kV | Redbud 345 kV Terminal Upgrade | Install any necessary terminal equipment at Redbud 345 kV substation to support a new line from Redbud 345 kV substation to Matthewson 345 kV substation with a summer emergency rating of 1792 MVA. | 2023 ITP | Excluded | 2026-08-28
220772 | 158574 | Line - Mathewson 345 kV - Redbud 345 kV | Matthewson 345 kV Terminal Equipment #2 | Install any necessary terminal equipment at Matthewson 345 kV substation to support a new line from Matthewson 345 kV substation to Redbud 345 kV substation with a summer emergency rating of 1792 MVA. | 2023 ITP | Excluded | 2027-12-01
220773 | 158638 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 2 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV to support a second 138 kV line from Anadarko to Gracemont. | 2023 ITP | Excluded | 2028-05-31
220812 | 170066 | Line - Beckham County - Potter -345 kV New Line | Beckham County 345 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Excluded | 2029-11-12
220817 | 170093 | Line - Beckham County - Potter -345 kV New Line | Potter 345 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Excluded | 2029-11-12
220817 | 170296 | Sub - Conway 115 kV - Kirby 115 kV Terminal Upgrades | Conway 115 kV Terminal Upgrade | Install any necessary terminal equipment at Conway 115 kV substation to support a line from Conway 115 kV substation to Kirby 115 kV substation with a summer emergency rating of 197 MVA. | 2024 ITP | Excluded | 2027-12-31
220817 | 170297 | Sub - Conway 115 kV - Kirby 115 kV Terminal Upgrades | Kirby 115 kV Terminal Upgrade | Install any necessary terminal equipment at Kirby 115 kV substation to support a line from Kirby 115 kV substation to Conway 115 kV substation with a summer emergency rating of 197 MVA. | 2024 ITP | Excluded | 2027-12-31
220817 | 170354 | XFR - Road Runner 345/115 kV #3 | XFR - Roadrunner 345/115 kV #3 | Install new Ckt 3 345/115 kV transformer at Roadrunner 115 kV substation and expand the 115 kV bus. | 2024 ITP | Excluded | 2029-03-15
220817 | 170355 | XFR - Road Runner 345/115 kV #3 | Roadrunner 345/115 kV Transformer Ckt 3 (345 kV) | Install 345 kV terminal equipment to support a Ckt 3 345/115 kV transformer at Roadrunner 345 kV substation with a summer emergency rating of 435 MVA. | 2024 ITP | Excluded | 2029-03-15
220807 | 170381 | Device - Colbert 138 kV Capacitor | Colbert 138 kV Capacitor | Install 6 MVAR Capacitor at Colbert 138 kV substation | 2024 ITP | Excluded | 2029-06-30
220804 | 170389 | Line - Cherokee Data Center East 138 kV - Tulsa North 138 kV Rebuild | Cherokee Data Center East - Tulsa North 138 kV Ckt 1 Rebuild | Rebuild 4.6-mile Ckt 1 line from Tulsa North 138 kV substation to Cherokee Data Center East 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 300 MVA. | 2024 ITP | Excluded | 2027-10-01
220804 | 170390 | Line - Cherokee Data Center East 138 kV - Tulsa North 138 kV Rebuild | Cherokee Data Center East 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Cherokee Data Center East 138 kV substation to support the line from Cherokee Data Center East 138 kV substation to Tulsa North 138 kV substation with a summer emergency rating of 300 MVA. | 2024 ITP | Excluded | 2027-10-01
220804 | 170405 | Line - Cherokee Data Center East 138 kV - Tulsa North 138 kV Rebuild | Tulsa North 138 kV Ckt 1 Terminal Upgrade #3 | Install any necessary terminal equipment at Tulsa North 138 kV substation to support the line from Tulsa North 138 kV substation to Cherokee Data Center East 138 kV substation with a summer emergency rating of 300 MVA. | 2024 ITP | Excluded | 2027-10-01
220804 | 170415 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (AEP) | Install any necessary terminal equipment to support connecting GRDA's third 161/138 kV transformer at Catoosa 138 kV substation with a summer emergency rating of 188 MVA. | 2024 ITP | Excluded | 2027-10-01
220914 | 170417 | Multi - Ft Smith - Muskogee 345 kV New Line Muskogee - Talequah 161 kV Rebuild | Muskogee 345 kV Ckt 1 Terminal Upgrade#1 | Install terminal equipment at Muskogee 345 kV substation to support a new line to Ft Smith 345 kV substation Ckt 1 | 2024 ITP | Excluded | 2028-12-31
220817 | 170433 | Line -Gaines – Riley - Mid America - Mid-Denver Tap 69 kV Rebuild | Riley Tap - Gaines County 69 kV Ckt 1 Rebuild | Rebuild 0.4-mile 69 kV Ckt 1 line from Riley 69 kV Tap to Gaines County 69 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 71 MVA | 2024 ITP | Excluded | 2028-05-31
220817 | 170435 | Line -Gaines – Riley - Mid America - Mid-Denver Tap 69 kV Rebuild | Gaines County 69 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Gaines County 69 kV substation for the line from Gaines County 69 kV substation to Riley 69 kV tap with a summer emergency rating of 71 MVA. | 2024 ITP | Excluded | 2028-05-31
220817 | 170436 | Line -Gaines – Riley - Mid America - Mid-Denver Tap 69 kV Rebuild | Riley - Mid America 69 kV Ckt 1 Rebuild | Rebuild 3.1-mile 69 kV line from Riley 69 kV substation to Mid America 69 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 71 MVA. | 2024 ITP | Excluded | 2028-05-31
220817 | 170438 | Line -Gaines – Riley - Mid America - Mid-Denver Tap 69 kV Rebuild | Mid America 69 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Mid America 69 kV substation for the line from Mid America 69 kV substation to Riley 69 kV substation with a summer emergency rating of 71 MVA. | 2024 ITP | Excluded | 2028-05-31
220817 | 170439 | Line -Gaines – Riley - Mid America - Mid-Denver Tap 69 kV Rebuild | Mid Denver - Mid America 69 kV Ckt 1 Rebuild | Rebuild 2.6-mile 69 kV Ckt 1 line from Mid Denver 69 kV substation to Mid America 69 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 71 MVA. | 2024 ITP | Excluded | 2028-05-31
220817 | 170440 | Line -Gaines – Riley - Mid America - Mid-Denver Tap 69 kV Rebuild | Mid Denver 69 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Mid Denver 69 kV substation for the line from Mid Denver 69 kV substation to Mid American 69 kV substation with a summer emergency rating of 71 MVA. | 2024 ITP | Excluded | 2028-05-31
220817 | 170441 | Line -Gaines – Riley - Mid America - Mid-Denver Tap 69 kV Rebuild | Mid America 69 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Mid America 69 kV substation for the line from Mid America 69 kV substation to Mid Denver 69 kV substation with a summer emergency rating of 71 MVA. | 2024 ITP | Excluded | 2028-05-15
210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Excluded | 2025-12-11
210545 | 112395 | Device - Gypsum 69 kV Capacitor Bank | Gypsum 69 kV Capacitor Bank | Install a new 12 MVAR capacitor bank at Gypsum 69 kV substation. | 2019 ITP | Included | 2026-03-31
210545 | 112435 | Line - East Kingfisher - Kingfisher 138kV | East Kingfisher - Kingfisher 138 kV Rebuild | Rebuild 2.03 miles of 138 kV line from Kingfisher to East Kingfisher and upgrade any necessary terminal equipment at East Kingfisher and/or Kingfisher to increase the summer emergency rating to 187 MVA | 2019 ITP | Included | 2026-05-31
210544 | 112460 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sand Springs - Sheffield Steel 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA | 2019 ITP | Included | 2026-02-26
220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1-345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation. | DISIS-2016-002 | Excluded | 2026-12-31
210574 | 122872 | Line - Carlisle - Murphy 115 kV #2 | Carlisle - Murphy 115 kV Ckt 1 Rebuild | Rebuild 4.0 miles of 115 kV line from Carlisle to Murphy and upgrade any necessary terminal equipment to achieve a summer emergency rating of 240 MVA | 2020 ITP | Included | 2026-04-15
220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Included | 2026-05-15
220726 | 156412 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs - Roadrunner 345 kV ckts 1 & 2 | Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA | 2021 ITP | Included | 2026-05-15
N/A | 143265 | DISIS-2017-001-P2 | Beaver to Eureka 161kV Rebuild (DISIS-2017-001) (AEP) | Rebuild the existing Beaver to Eureka 161kV 1.22 mile line section to achieve a minimum light/emergency rating of 250 MVA | DISIS-2017-001-P2 | Excluded | 36
N/A | TBD | DISIS-2020-001 | Build New Border to Beckham 345 kV Line Ckt 2 | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA *Conceptual cost estimate | DISIS-2020-001 | Excluded | 36
N/A | TBD | DISIS-2020-001 | Build New G17-151-Tap to Border 345 kV Line | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA *Conceptual cost estimate | DISIS-2020-001 | Excluded | 36
N/A | TBD | DISIS-2020-001 | Hobbs to Andrews Voltage Conversion | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | DISIS-2020-001 | Excluded | 36
N/A | TBD | DISIS-2020-001 | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Correct existing Lidar clearance issues on Sidewinder to Andrews 345 kV line to increase the line rating to 1400MVA SN/SE | DISIS-2020-001 | Excluded | 36
N/A | TBD | DISIS-2021-001 | Rebuild LE-LOVINTON2 to LE-TATMGOAB2 69kV line 1 | Rebuild the LE-LOVINTON2 to LE-TATMGOAB2 69kV line CKT1 (5.1 miles) to a minimum rating of 61 MVA | DISIS-2021-001 | Excluded | TBD (36-month lead time)
N/A | TBD | DISIS-2021-001 | Rebuild LE-TATMGOAB2 to LE-MCDONALD2 69kV line 1 | Rebuild the LE-TATMGOAB2 to LE-MCDONALD2 69kV line CKT1 (9 miles) to a minimum rating of 61 MVA | DISIS-2021-001 | Excluded | TBD (36-month lead time)
N/A | TBD | DISIS-2021-001 | Rebuild LE-MCDONALD2 to LE-TATUM_SW2 69kV line 1 | Rebuild the LE-MCDONALD2 to LE-TATUM_SW2 69kV line CKT1 (7 miles) to a minimum rating of 63 MVA | DISIS-2021-001 | Excluded | TBD (36-month lead time)
N/A | TBD | DISIS-2021-001 | Rebuild LE-LEWIS 2 to A21-003-TAP 69kV line NO | Rebuild the LE-LEWIS2 to A21-003-TAP 69kV line CKTNO (0.04 miles) to a minimum rating of 61 MVA | DISIS-2021-001 | Excluded | TBD (36-month lead time)
N/A | TBD | DISIS-2021-001 | Upgrade the existing Elk City 230/138kV Transformer 1 | Upgrade the existing Elk City 230/138 kV Transformer 1 to a minimum MVA of 339 | DISIS-2021-001 | Excluded | TBD (36-month lead time)
N/A | TBD | DISIS-2021-001 | Upgrade the existing Tuco 345/230 kV Transformer 1 | Upgrade the existing Tuco 345/230 kV Transformer 1 to a minimum rating of 583 MVA | DISIS-2021-001 | Excluded | TBD (36-month lead time)
N/A | TBD | DISIS-2021-001 | Build a second Yoakum 345/230 kV Transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Excluded | TBD (36-month lead time)
N/A | 170591 | DISIS-2021-001 | Build New Border to Beckham 345 kV Line Ckt 2 | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA *Conceptual cost estimate | DISIS-2021-001 | Excluded | TBD (36-month lead time)
N/A | 159070 | DISIS-2017-002 | Build Tolk to Potter County 345 kV Circuit 1 | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | DISIS-2017-002 | Excluded | 36

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading (%) | TC Loading (%) | TC Voltage | VMIN | VMAX | Upgrade Name
00ALL | GEN-2022-147 LOSIS | ERIS | Thermal | 525830 TUCO_INT 6 230 997578 UPDATE LATER 230 1 | 27SP | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | 559 | 559 | 109.75 | 121.64 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1
00ALL | GEN-2022-147 LOSIS | ERIS | Thermal | 525830 TUCO_INT 6 230 997579 SIEM 8743066 230 2 | 27SP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 559 | 643 | 92.97 | 103.06 |  |  |  | Build new POTTER_CO 7 to BECKHAM7 345kV Line 1
00ALL | GEN-2022-147 LOSIS | ERIS | Thermal | 525830 TUCO_INT 6 230 997581 UPDATE LATER 230 1 | 24SP | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | 559 | 559 | 109.53 | 121.43 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1
00ALL | GEN-2022-147 LOSIS | ERIS | Thermal | 525830 TUCO_INT 6 230 997582 SIEM 8743066 230 2 | 24SP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 559 | 643 | 92.8 | 102.89 |  |  |  | Build new POTTER_CO 7 to BECKHAM7 345kV Line 1
00ALL | GEN-2022-147 LOSIS | ERIS | Thermal | 525832 TUCO_INT 7 345 997578 UPDATE LATER 230 1 | 27SP | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | 559 | 559 | 108.37 | 120.27 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1
00ALL | GEN-2022-147 LOSIS | ERIS | Thermal | 525832 TUCO_INT 7 345 997579 SIEM 8743066 230 2 | 27SP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 559 | 643 | 91.69 | 101.78 |  |  |  | Build new POTTER_CO 7 to BECKHAM7 345kV Line 1
00ALL | GEN-2022-147 LOSIS | ERIS | Thermal | 525832 TUCO_INT 7 345 997581 UPDATE LATER 230 1 | 24SP | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | 559 | 559 | 108.43 | 120.36 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1
05ALL | GEN-2022-147 LOSIS | ERIS | Stability | Loss of Synchronism in G22-147, ELK, HOBBS, TOLK and other units in Group05 | 25S, 25W | GROUP5_P1_LOCAL_FAULT_003 | [7 empty] | Multi - Border - Woodward 345 kV Tap Phantom to Crossroads to Potter 765 kV New Line
00ALL | GEN-2022-147 LOSIS | ERIS | Thermal | 525832 TUCO_INT 7 345 997582 SIEM 8743066 230 2 | 24SP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 559 | 643 | 91.76 | 101.88 |  |  |  | Build new POTTER_CO 7 to BECKHAM7 345kV Line 1
00ALL | GEN-2022-147 LOSIS | ERIS | Thermal | None | 27WP | None | [7 empty] | None
00ALL | GEN-2022-147 LOSIS | ERIS | Voltage | None | 24SP, 27SP, 27 WP | None | [7 empty] | None
00ALL | GEN-2022-147 LOSIS | ERIS | Non-converged | None | 24SP, 27SP, 27 WP | None | [7 empty] | None

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time (Months) | Total Upgrade Cost
Contingent | GEN-2022-147 LOSIS | Steady State | 05 SOUTHWEST | 2024 ITP | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 170066, 170093 | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | OKGE/SPS | 36 | 428620878
Current Study | GEN-2022-147 LOSIS | Steady State | 05 SOUTHWEST | DISIS-2022-001 | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1 | TBD | Replace the existing TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 with a minimum rating of MVA | SPS | 30 | 19200000
Contingent | GEN-2022-147 LOSIS | Stability | 05 SOUTHWEST | 2020 ITP | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | 143182 | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | AEPW/OKGE | 60 | 12238460
Contingent | GEN-2022-147 LOSIS | Stability | 05 SOUTHWEST | 2024 ITP | ERIS | Phantom to Crossroads to Potter 765 kV New Line | TBD | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | SPS | 36 | 1690874827

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF %
GEN-2022-147 | GEN-2022-147 LOSIS | 05 SOUTHWEST | 170066, 170093 | ERIS | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA. Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Potter 345 kV substation to support the line from Potter 345 kV substation to Beckham County 345 kV substation with a summer emergency rating of 1792 MVA. | - | 0% | 428620878 | 0.01815
GEN-2022-147 | GEN-2022-147 LOSIS | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1 | Current Study | Replace the existing TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 with a minimum rating of 690 MVA | 19200000 | 100% | 19200000 | 0.18336
GEN-2022-147 | GEN-2022-147 LOSIS | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | - | 0% | 12238460 | N/A
GEN-2022-147 | GEN-2022-147 LOSIS | 05 SOUTHWEST | TBD | ERIS | Phantom to Crossroads to Potter 765 kV New Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | - | 0% | 1690874827 | N/A

## All Thermal
SOLUTIONTYPE | STUDY NAME | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | CONSTRAINT VIOLATION CRITERIA | UPGRADE NAME
Thermal | GEN-2022-147 LOSIS | 00ALL | 1 | 24SP | GEN-2022-147 | TO->FROM | 525830 TUCO_INT 6 230 997581 UPDATE LATER 230 1 | 559 | 559 | 0.30405 | 121.43 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1
Thermal | GEN-2022-147 LOSIS | 00ALL | 1 | 24SP | GEN-2022-147 | FROM->TO | 525832 TUCO_INT 7 345 997581 UPDATE LATER 230 1 | 559 | 559 | 0.30405 | 120.36 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1
Thermal | GEN-2022-147 LOSIS | 00ALL | 1 | 24SP | GEN-2022-147 | TO->FROM | 525830 TUCO_INT 6 230 997582 SIEM 8743066 230 2 | 559 | 643 | 0.29604 | 102.89 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
Thermal | GEN-2022-147 LOSIS | 00ALL | 1 | 24SP | GEN-2022-147 | FROM->TO | 525832 TUCO_INT 7 345 997582 SIEM 8743066 230 2 | 559 | 643 | 0.29604 | 101.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
Thermal | GEN-2022-147 LOSIS | 00ALL | 1 | 27SP | GEN-2022-147 | TO->FROM | 525830 TUCO_INT 6 230 997578 UPDATE LATER 230 1 | 559 | 559 | 0.31009 | 121.64 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1
Thermal | GEN-2022-147 LOSIS | 00ALL | 1 | 27SP | GEN-2022-147 | FROM->TO | 525832 TUCO_INT 7 345 997578 UPDATE LATER 230 1 | 559 | 559 | 0.31009 | 120.27 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | TDF Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1
Thermal | GEN-2022-147 LOSIS | 00ALL | 1 | 27SP | GEN-2022-147 | TO->FROM | 525830 TUCO_INT 6 230 997578 UPDATE LATER 230 1 | 559 | 559 | 0.21908 | 102.88 | POI 526936_5 | TDF Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1
Thermal | GEN-2022-147 LOSIS | 00ALL | 1 | 27SP | GEN-2022-147 | FROM->TO | 525832 TUCO_INT 7 345 997578 UPDATE LATER 230 1 | 559 | 559 | 0.21908 | 102.08 | POI 526936_5 | TDF Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1
Thermal | GEN-2022-147 LOSIS | 00ALL | 1 | 27SP | GEN-2022-147 | TO->FROM | 525830 TUCO_INT 6 230 997579 SIEM 8743066 230 2 | 559 | 643 | 0.30192 | 103.06 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
Thermal | GEN-2022-147 LOSIS | 00ALL | 1 | 27SP | GEN-2022-147 | FROM->TO | 525832 TUCO_INT 7 345 997579 SIEM 8743066 230 2 | 559 | 643 | 0.30192 | 101.78 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | TDF Impact | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
Thermal | GEN-2022-147 LOSIS | 00ALL | 1 | 27SP | GEN-2022-147 | TO->FROM | 525830 TUCO_INT 6 230 997578 UPDATE LATER 230 1 | 559 | 559 | 0.21908 | 100.05 | POI 526936_1 | TDF Impact | Replace the TUCO_INT 7 to TUCO_INT 6 345kV Transformer 1
Non-Converged | GEN-2022-147 LOSIS | 00ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2022-147 LOSIS | 00ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2022-147 LOSIS | 00ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2022-147 LOSIS | 00ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | STUDY NAME | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | UPGRADE NAME
Voltage | GEN-2022-147 LOSIS | 00ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2022-147 LOSIS | 00ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2022-147 LOSIS | 00ALL | 2 | 27WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_003 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Unstable rotor angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 32 additional units in Group05. The same rotor angle instability was also present in the base case. Neither reducing the Gen-2022-147 active power output to 75%, 50%, 25%, or 0% nor reducing the fault-clearing time to as low as 0.05 cycles resolved the instability. Gen-2022-147 : PTDF=0.3043 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_004 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.3. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.2. LAMB_TR3 1 (525633) 13.2 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Three Winding #1 b.3. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_006 | 3 Phase fault on LAMTON 3115.00 (525414) 115 kV Bus a. Apply fault at the LAMTON 3115.00 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 (525414) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_007 | 3 Phase fault on LAMB_CNTY 3115.00 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3115.00 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_008 | 3 Phase fault on TULIA_TP 3115.00 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3115.00 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MU-TULIA 3 (522800) 115.0 kV to TULIA_TP 3 (525179) 115.0 kV Transmission Circuit #1 b.2. HAPPY_INT 3 (525154) 115.0 kV to TULIA_TP 3 (525179) 115.0 kV Transmission Circuit #1 b.3. TULIA_TP 3 (525179) 115.0 kV to KRESS_INT 3 (525192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_009 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on CROSBY 3115.00 (525926) 115 kV Bus a. Apply fault at the CROSBY 3115.00 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 (525926) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_011 | 3 Phase fault on SP-WOLF_TP 3115.00 (526481) 115 kV Bus a. Apply fault at the SP-WOLF_TP 3115.00 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to LP-DOUD_TP 3 (526162) 115.0 kV Transmission Circuit #1 b.2. LP-DOUD_TP 3 (526162) 115.0 kV to LP-DOUD 3 (526176) 115.0 kV Transmission Circuit #1 b.3. LP-DOUD_TP 3 (526162) 115.0 kV to SP-WOLF_TP 3 (526481) 115.0 kV Transmission Circuit #1 b.4. SP-UPLAND (526198) 115.0 kV to SP-WOLF_TP 3 (526481) 115.0 kV Transmission Circuit #1 b.5. YUMA_INT 3 (526475) 115.0 kV to SP-WOLF_TP 3 (526481) 115.0 kV Transmission Circuit #1 b.6. SP-WOLF_TP 3 (526481) 115.0 kV to SP-WOLFORTH3 (526483) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_012 | 3 Phase fault on CALLAHAN 3115.00 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3115.00 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 (525326) 115.0 kV to CALLAHAN 3 (525763) 115.0 kV Transmission Circuit #1 b.2. CALLAHAN 3 (525763) 115.0 kV to FLOYD_CNTY 3 (525780) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_013 | 3 Phase fault on COX 3115.00 (525326) 115 kV Bus a. Apply fault at the COX 3115.00 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 (525326) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on STANTON_W 3115.00 (526076) 115 kV Bus a. Apply fault at the STANTON_W 3115.00 (526076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.2. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on LUBBCK_STH 3115.00 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3115.00 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to MURPHY 3 (526192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on SP-ERSKINE 3115.00 (526109) 115 kV Bus a. Apply fault at the SP-ERSKINE 3115.00 (526109) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ERSKINE 3 (526109) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.2. SP-ERSKINE 3 (526109) 115.0 kV to CARLISLE 3 (526160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_021 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to SWISHER 3 (525212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_024 | 3 Phase fault on KRS_RURL_TP3115.00 (525226) 115 kV Bus a. Apply fault at the KRS_RURL_TP3115.00 (525226) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to KRS_RURL_TP3 (525226) 115.0 kV Transmission Circuit #1 b.2. KRESS_RURAL3 (525225) 115.0 kV to KRS_RURL_TP3 (525226) 115.0 kV Transmission Circuit #1 b.3. KRS_RURL_TP3 (525226) 115.0 kV to N_PLAINVEW 3 (525257) 115.0 kV Transmission Circuit #1 b.4. N_PLAINVEW 3 (525257) 115.0 kV to KISER 3 (525272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to BLANCO 3 (525803) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_028 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, and 527003) and Tolk units (525561, 525562). This issue was not observed in base case. The oscillations meet the SPP rotor Angle Damping Requirements (SPPR1= 0.874). CQ request did not meet the 3% criteria. | No mitigations required.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_032 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_034 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_035 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_036 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Unstable rotor angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 32 additional units in Group05. The same rotor angle instability was also present in the base case. Neither reducing the Gen-2022-147 active power output to 75%, 50%, 25%, or 0% nor reducing the fault-clearing time to as low as 0.05 cycles resolved the instability. Gen-2022-147 : PTDF=0.3043 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_043 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_044 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_045 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_046 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_047 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue was observed in base case. | Remove reclosing solves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_048 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue was observed in base case. | Remove reclosing solves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. The issue was observed in base case. | Remove reclosing solves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on PLSNT_HILL 6230.00 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6230.00 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 (524770) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on OASIS 6230.00 (524875) 230 kV Bus a. Apply fault at the OASIS 6230.00 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 (524875) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to PLANT_X 6 (525481) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip LANOGSU1 (523812) and G18-089 (763189) units. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on PLANT_X 3115.00 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3115.00 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_063 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to SUNDOWN 6 (526435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to G17-146-TAP (760498) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-099 (763257) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on NEEDMORE 6230.00 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6230.00 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 (525586) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on SP-ABERNTHY269.000 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY269.000 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 (525731) 69.0 kV to TUCO_INT2 2 (525816) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on HALECENTER 269.000 (525738) 69 kV Bus a. Apply fault at the HALECENTER 269.000 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 (525738) 69.0 kV to TUCO_INT 2 (525826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on TUCO_INT 269.000 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 269.000 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 (525826) 69.0 kV to LH-WIL&ELN+2 (525853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on TUCO_INT 269.000 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 269.000 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 (525826) 69.0 kV to SP-NEWDEAL 2 (525885) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip HALE_WND (525951, 525952) units. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Unstable rotor-angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 36 additional units in Group05. No rotor-angle instability was observed in the base case. Reducing the Gen-2022-147 generator output (Pgen) to 75% and 50% did not resolve the instability. At 25% Pgen, no rotor-angle instability was observed; however, oscillatory behavior persisted in the output power of the Gains units (527001, 527002, 527003) and Tolk units (525561, 525562). Gen-2022-147 : PTDF=0.3043 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 (526161) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_082 | 3 Phase fault on JONES 6230.00 (526337) 230 kV Bus a. Apply fault at the JONES 6230.00 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 (526337) 230.0 kV to GRASSLAND 6 (526677) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_083 | 3 Phase fault on SUNDOWN 6230.00 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6230.00 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 (526435) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_084 | 3 Phase fault on AMOCO_SS 6230.00 (526460) 230 kV Bus a. Apply fault at the AMOCO_SS 6230.00 (526460) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 (526460) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to BRU_SUB 6 (527009) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_086 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to INK_BASIN 6 (527028) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_087 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to MUSTANG 6 (527149) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_089 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_091 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002). Reducing the fault clearing time to 5 cycles, as specified in the TO-submitted stability contingency forms, did not solve the oscillations. This issue was not observed in base case. The oscillations meet the SPP rotor Angle Damping Requirements (SPPR1= 0.852). CQ request did not meet the 3% criteria. | No mitigations required.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP (762216) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Unstable rotor angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 36 additional units in Group05. No such rotor angle instability was observed in the base case. The instability persisted when the Gen-2022-147 output was reduced to 50%, 25%. At 0% Pgen, no rotor-angle instability was observed. Gen-2022-147 : PTDF=0.3043 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to PNM-DC6 (599955) 230.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_094 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_097 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_098 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_099 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_100 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to AMA_SOUTH 3 (524414) 115.0 kV to AMA_SO_TR1 1 (524410) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_101 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to ROOSEVELT 3 (524908) 115.0 kV to ROSEVLT_TR11 (524907) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_102 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to KRESS_INT 2 (525191) 69.0 kV to KRESS_TR1 1 (525190) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_103 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV to SWISHER_TR11 (525211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_104 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR1 1 (525451) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_105 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR2 1 (525452) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_106 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR21 (525458) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-089 (763189) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_107 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR11 (525459) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-089 (763189) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_108 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to PLANT_X 3 (525480) 115.0 kV to PLANTX_TR1 1 (525479) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_109 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 2 1 (525538) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_110 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 2 1 (526938) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_111 | 3 Phase fault on LAMB_CNTY 3115.00 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3115.00 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV to LAMB_TR1 1 (525631) 13.2 kV Three Winding #1 b.2. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV to LAMB_TR2 1 (525632) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_112 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV to FLOYD_TR1 1 (525777) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_113 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV to FLOYD_TR2 1 (525778) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_114 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT2 2 (525816) 69.0 kV to TUCO_TR7 1 (525814) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_115 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV to TUCO_TR5 1 (525822) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_116 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV to TUCO_TR6 1 (525823) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_117 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_118 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_119 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_120 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_121 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to CARLISLE 2 (526159) 69.0 kV to CRLSLE_TR2 1 (526158) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_122 | 3 Phase fault on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 (526161) 230.0 kV to CARLISLE 3 (526160) 115.0 kV to CRLSLE_TR1 1 (526157) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_123 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV to LBB_STH TR11 (526265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_124 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV to LBB_STH TR31 (526264) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_125 | 3 Phase fault on LUBBCK_EST 3115.00 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3115.00 (526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV to LBB_EST TR21 (526295) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_126 | 3 Phase fault on LUBBCK_EST 3115.00 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3115.00 (526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV to LBB_EST TR31 (526296) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_127 | 3 Phase fault on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV to LBB_EST TR11 (526294) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_128 | 3 Phase fault on WOLFFORTH 6230.00 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6230.00 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 (526525) 230.0 kV to WOLFFORTH 3 (526524) 115.0 kV to WOLFRTH_TR11 (526522) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_129 | 3 Phase fault on GRASSLAND 6230.00 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6230.00 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 (526677) 230.0 kV to GRASSLAND 3 (526676) 115.0 kV to GRASLND_TR11 (526674) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_130 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM 3 (526934) 115.0 kV to YOAKUM_TR1 1 (526931) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_131 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM 3 (526934) 115.0 kV to YOAKUM_TR2 1 (526932) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_132 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_133 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV to HOBBS_TR3 1 (527895) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_134 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_135 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_136 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_137 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_138 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_139 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_140 | 3 Phase fault on HALE_WNDCL16230.00 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16230.00 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 (525957) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Remove capacitor reclosing solves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_141 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_142 | 3 Phase fault on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 (526161) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_143 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_LOCAL_FAULT_144 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_001 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_002 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_003 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_004 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_005 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_006 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 5270012) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_007 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_008 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_009 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_010 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_011 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_012 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Unstable rotor-angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 36 additional units in Group05. No rotor-angle instability was observed in the base case. Reducing the Gen-2022-147 generator output (Pgen) to 75% and 50% did not resolve the instability. At 25% Pgen, no rotor-angle instability was observed; however, oscillatory behavior persisted in the output power of the Gains units (527001, 527002, 527003) and Tolk units (525561, 525562). Gen-2022-147 : PTDF=0.3043 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_013 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_014 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_015 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_016 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_017 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_018 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P1_REGIOINAL_FAULT_019 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWHART 6 (525461) 230.0 kV to PLANT_X 6 (525481) 230.0 kV Transmission Circuit #1 b.2. PLANT_X 6 (525481) 230.0 kV to PLANT_X4 1 (525494) 20.0 kV Two Winding #1 b.3. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.4. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 b.5. PLANT_X 6 (525481) 230.0 kV to SUNDOWN 6 (526435) 230.0 kV Transmission Circuit #1 b.6. PLANT_X 6 (525481) 230.0 kV to G17-146-TAP (760498) 230.0 kV Transmission Circuit #1 b.7. PLANTX_TR1 1 (525479) 13.2 kV to PLANT_X 6 (525481) 230.0 kV to PLANT_X 3 (525480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply Fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. LUBBCK_EST 6 (526299) 230.0 kV to GEN-2020-060 (764875) 230.0 kV Transmission Circuit #1 b.3. LBB_EST TR11 (526294) 13.2 kV to LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on GRASSLAND 6230.00 (526677) 230 kV Bus a. Apply Fault at the GRASSLAND 6230.00 (526677) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES 6 (526337) 230.0 kV to GRASSLAND 6 (526677) 230.0 kV Transmission Circuit #1 b.2. GRASSLAND 6 (526677) 230.0 kV to CIRRUS_WND 6 (526679) 230.0 kV Transmission Circuit #1 b.3. GRASLND_TR11 (526674) 13.2 kV to GRASSLAND 6 (526677) 230.0 kV to GRASSLAND 3 (526676) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply Fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.3. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 b.4. LAMB_TR1 1 (525631) 13.2 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Three Winding #1 b.5. LAMB_TR2 1 (525632) 13.2 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Three Winding #2 b.6. LAMB_TR3 1 (525633) 13.2 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Three Winding #1 b.9. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply Fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALLAHAN 3 (525763) 115.0 kV to FLOYD_CNTY 3 (525780) 115.0 kV Transmission Circuit #1 b.2. FLOYD_CNTY 3 (525780) 115.0 kV to BLANCO 3 (525803) 115.0 kV Transmission Circuit #1 b.3. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.4. FLOYD_TR1 1 (525777) 13.2 kV to FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV Three Winding #1 b.5. FLOYD_TR2 1 (525778) 13.2 kV to FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.2. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.3. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.4. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.7. TUCO_TR7 1 (525814) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT2 2 (525816) 69.0 kV Three Winding #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. TUCO_TR5 1 (525822) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #2 b.11. TUCO_TR6 1 (525823) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #1 b.15. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 b.16. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply Fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KRESS_INT 3 (525192) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.2. PLAINVW_TP 2 (525291) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 b.3. S_PLAINVEW 2 (525298) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 b.4. COX 3 (525326) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.5. LAMTON 3 (525414) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.6. SP-HALFWAY+2 (525432) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 b.7. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 b.8. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.9. HALE_TR1 1 (525451) 13.2 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV Three Winding #1 b.10. HALE_TR2 1 (525452) 13.2 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV Three Winding #2 b.11. HALE_CNTY 2 (525453) 69.0 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_TR1 1 (525451) 13.2 kV Three Winding #1 b.12. HALE_CNTY 2 (525453) 69.0 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_TR2 1 (525452) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on STANTON_W 3115.00 (526076) 115 kV Bus a. Apply Fault at the STANTON_W 3115.00 (526076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.2. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.3. SP-ERSKINE 3 (526109) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.4. SP-ERSKINE 3 (526109) 115.0 kV to CARLISLE 3 (526160) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply Fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC-BECK +2 (525045) 69.0 kV to SUDANRURAL 2 (525592) 69.0 kV Transmission Circuit #1 b.2. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 b.3. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.4. SUDANRURAL 2 (525592) 69.0 kV to LC-SANDHLL+2 (525599) 69.0 kV Transmission Circuit #1 b.5. LC-SANDHLL+2 (525599) 69.0 kV to AMHERST 2 (525606) 69.0 kV Transmission Circuit #1 b.6. AMHERST 2 (525606) 69.0 kV to W_LITTLFLD 2 (525613) 69.0 kV Transmission Circuit #1 b.7. W_LITTLFLD 2 (525613) 69.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Transmission Circuit #1 b.8. LTFLD_S&CTY2 (525620) 69.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Transmission Circuit #1 b.9. LTFLD_S&CTY2 (525620) 69.0 kV to W_ANTON_TP 2 (525657) 69.0 kV Transmission Circuit #1 b.10. LAMB_CNTY 2 (525635) 69.0 kV to LC-LTTLFLD+2 (525650) 69.0 kV Transmission Circuit #1 b.11. LAMB_CNTY 2 (525635) 69.0 kV to LC-LUMSCHAP2 (525687) 69.0 kV Transmission Circuit #1 b.12. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 b.13. LC-LTTLFLD+2 (525650) 69.0 kV to W_ANTON_TP 2 (525657) 69.0 kV Transmission Circuit #1 b.14. W_ANTON_TP 2 (525657) 69.0 kV to LC-SPD&HART2 (525664) 69.0 kV Transmission Circuit #1 b.15. W_ANTON_TP 2 (525657) 69.0 kV to BAINER 2 (525671) 69.0 kV Transmission Circuit #1 b.16. LC-SPD&HART2 (525664) 69.0 kV to CNTYLINE_TP2 (525723) 69.0 kV Transmission Circuit #1 b.17. BAINER 2 (525671) 69.0 kV to W_ANTON 2 (525678) 69.0 kV Transmission Circuit #1 b.18. LC-LUMSCHAP2 (525687) 69.0 kV to HOBGOOD 2 (525694) 69.0 kV Transmission Circuit #1 b.19. HOBGOOD 2 (525694) 69.0 kV to PUMP/YH_TP 2 (525697) 69.0 kV Transmission Circuit #1 b.20. PUMP/YH_TP 2 (525697) 69.0 kV to YELLOWHOUSE2 (525703) 69.0 kV Transmission Circuit #1 b.21. PUMP/YH_TP 2 (525697) 69.0 kV to MIDAMERI#2 2 (525708) 69.0 kV Transmission Circuit #1 b.22. PHLLPPMP#2 2 (525701) 69.0 kV to YELLOWHOUSE2 (525703) 69.0 kV Transmission Circuit #1 b.23. MIDAMERI#2 2 (525708) 69.0 kV to WHITHARRAL 2 (525717) 69.0 kV Transmission Circuit #1 b.24. WHITHARRAL 2 (525717) 69.0 kV to LC-HODGE_TP2 (525995) 69.0 kV Transmission Circuit #1 b.25. LAMB_TR1 1 (525631) 13.2 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Three Winding #1 b.26. LAMB_TR3 1 (525633) 13.2 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Three Winding #1 b.27. LAMB_CNTY 2 (525635) 69.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR1 1 (525631) 13.2 kV Three Winding #1 b.28. LAMB_CNTY 2 (525635) 69.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR2 1 (525632) 13.2 kV Three Winding #2 b.31. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply Fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.2. SP-ACUFF +2 (525906) 69.0 kV to CROSBY 2 (525925) 69.0 kV Transmission Circuit #1 b.3. SP-ACUFF +2 (525906) 69.0 kV to VICKERS 2 (526123) 69.0 kV Transmission Circuit #1 b.4. CROSBY 3 (525926) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.5. STANTON_N 2 (526073) 69.0 kV to STANTON_E 2 (526075) 69.0 kV Transmission Circuit #z1 b.6. STANTON_N 2 (526073) 69.0 kV to SW_6786_N 2 (526086) 69.0 kV Transmission Circuit #1 b.7. STANTON_E 2 (526075) 69.0 kV to SW_6786_S 2 (526087) 69.0 kV Transmission Circuit #1 b.8. SW_6786_N 2 (526086) 69.0 kV to SW_6786_S 2 (526087) 69.0 kV Transmission Circuit #z1 b.9. SW_6786_N 2 (526086) 69.0 kV to SP-HETTLER 2 (526102) 69.0 kV Transmission Circuit #1 b.10. SW_6786_S 2 (526087) 69.0 kV to PLANTERS 2 (526284) 69.0 kV Transmission Circuit #1 b.11. SP-HETTLER 2 (526102) 69.0 kV to SP-IDALOU +2 (526116) 69.0 kV Transmission Circuit #1 b.12. SP-IDALOU +2 (526116) 69.0 kV to VICKERS 2 (526123) 69.0 kV Transmission Circuit #1 b.13. ACCO 2 (526249) 69.0 kV to CLUTTER 2 (526310) 69.0 kV Transmission Circuit #1 b.14. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.15. PLANTERS 2 (526284) 69.0 kV to LUBBCK_EST 2 (526297) 69.0 kV Transmission Circuit #1 b.16. LUBBCK_EST 2 (526297) 69.0 kV to CLUTTER 2 (526310) 69.0 kV Transmission Circuit #1 b.17. LUBBCK_EST 2 (526297) 69.0 kV to SLATON 2 (526562) 69.0 kV Transmission Circuit #1 b.18. SLATON 2 (526562) 69.0 kV to SP-SLATON 2 (526569) 69.0 kV Transmission Circuit #1 b.19. SP-SLATON 2 (526569) 69.0 kV to SOUTHLAND 2 (526576) 69.0 kV Transmission Circuit #1 b.20. SOUTHLAND 2 (526576) 69.0 kV to LG-HAKBERRY2 (526583) 69.0 kV Transmission Circuit #1 b.21. LG-HAKBERRY2 (526583) 69.0 kV to DIEKEMPER 2 (526592) 69.0 kV Transmission Circuit #1 b.22. LBB_EST TR11 (526294) 13.2 kV to LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Three Winding #1 b.23. LBB_EST TR21 (526295) 13.2 kV to LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV Three Winding #1 b.24. LBB_EST TR31 (526296) 13.2 kV to LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV Three Winding #2 b.25. LUBBCK_EST 2 (526297) 69.0 kV to LUBBCK_EST 3 (526298) 115.0 kV to LBB_EST TR21 (526295) 13.2 kV Three Winding #1 b.26. LUBBCK_EST 2 (526297) 69.0 kV to LUBBCK_EST 3 (526298) 115.0 kV to LBB_EST TR31 (526296) 13.2 kV Three Winding #2 b.29. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 6 (526299) 230.0 kV to LBB_EST TR11 (526294) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply Fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IVORY 2 (526205) 69.0 kV to BATTON_S 2 (526228) 69.0 kV Transmission Circuit #1 b.2. IVORY 2 (526205) 69.0 kV to IVORY_TP 2 (526256) 69.0 kV Transmission Circuit #z1 b.3. IVORY 2 (526205) 69.0 kV to LUBBCK_STH 2 (526267) 69.0 kV Transmission Circuit #1 b.4. ALLEN 3 (526213) 115.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Transmission Circuit #1 b.5. BATTON_N 2 (526221) 69.0 kV to BATTON_S 2 (526228) 69.0 kV Transmission Circuit #z1 b.6. ACCO 2 (526249) 69.0 kV to IVORY_TP 2 (526256) 69.0 kV Transmission Circuit #1 b.7. ACCO 2 (526249) 69.0 kV to CLUTTER 2 (526310) 69.0 kV Transmission Circuit #1 b.8. IVORY_TP 2 (526256) 69.0 kV to LUBBCK_STH 2 (526267) 69.0 kV Transmission Circuit #1 b.9. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.10. LUBBCK_STH 3 (526268) 115.0 kV to WOODROW 3 (526602) 115.0 kV Transmission Circuit #1 b.11. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.12. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 b.13. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 b.14. WOODROW 3 (526602) 115.0 kV to LYNN_CNTY 3 (526656) 115.0 kV Transmission Circuit #1 b.15. LBB_STH TR31 (526264) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #2 b.16. LBB_STH TR11 (526265) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #1 b.17. LBB_STH TR21 (526266) 13.2 kV to LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_STH 2 (526267) 69.0 kV Three Winding #1 b.18. LUBBCK_STH 2 (526267) 69.0 kV to LUBBCK_STH 3 (526268) 115.0 kV to LBB_STH TR21 (526266) 13.2 kV Three Winding #1 b.20. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_STH 6 (526269) 230.0 kV to LBB_STH TR31 (526264) 13.2 kV Three Winding #2 b.21. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_STH 6 (526269) 230.0 kV to LBB_STH TR11 (526265) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on NEWHART 6230.00 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 b.2. SWISHER_TR11 (525211) 13.2 kV to SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. TUCO_INT 6 (525830) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.2. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.3. TUCO_INT 6 (525830) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on ELK_CT1 345.00 (525850) 345 kV Bus a. Apply Fault at the ELK_CT1 345.00 (525850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.4. ELK_CT1 (525850) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.6. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.7. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_345 (526936) 345.0 kV to GEN-2019-011 (763516) 345.0 kV Transmission Circuit #1 b.6. YOAKUM_345 (526936) 345.0 kV to GEN-2021-090 (766120) 345.0 kV Transmission Circuit #1 b.7. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 5270012) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Unstable rotor angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 36 additional units in Group05. The same rotor angle instability was also present in the base case. Neither reducing the Gen-2022-147 active power output to 75%, 50%, 25%, or 0% nor reducing the fault-clearing time to as low as 0.05 cycles resolved the instability. Gen-2022-147 : PTDF=0.3043 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply Fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.2. ROOSEVELT 6 (524909) 230.0 kV to OASIS 6 (524875) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV to SWISHER_TR11 (525211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply Fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.2. HALE_CNTY 3 (525454) 115.0 kV to KRESS_INT 3 (525192) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLANT_X 6 (525481) 230.0 kV to SUNDOWN 6 (526435) 230.0 kV Transmission Circuit #1 b.2. PLANT_X 6 (525481) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on TOLK 6230.00 (525531) 230 kV Bus a. Apply Fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 6 (525531) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply Fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.2. FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV to FLOYD_TR1 1 (525777) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 b.2. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.2. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLISLE 6 (526161) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.2. CARLISLE 6 (526161) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply Fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 b.2. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply Fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV to LBB_EST TR11 (526294) 13.2 kV Three Winding #1 b.2. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on JONES 6230.00 (526337) 230 kV Bus a. Apply Fault at the JONES 6230.00 (526337) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES 6 (526337) 230.0 kV to LUBBCK_STH 6 (526269) 230.0 kV Transmission Circuit #1 b.2. JONES 6 (526337) 230.0 kV to LUBBCK_STH 6 (526269) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (762216) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (762216) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | The protection relays tripped the G18-015 units (762463 and 762466). After disabling the protection relays, oscillatory behavior was observed in the active power outputs of the TOLK units (525561 and 525562). Voltage oscillations were also observed at Border 7 (515458) and Beckham7 (516059). In addition, reactive power oscillations were observed in the Harrington units (523972, 523973), the G08-047 unit (515905), and the G15-082 unit (585193). These active power and voltage oscillations were not observed in the base case. Reducing the Gen-2022-147 generator output (Pgen) to 75%, 50%, and 25% did not eliminate the active or reactive power oscillations. Gen-2022-147 : PTDF=0.3043 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GEN-2018-015345.00 (762460) 345 kV Bus a. Apply Fault at the GEN-2018-015345.00 (762460) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-015 (762460) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-015 (762460) 345.0 kV to G18-015-XFM1 (762461) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GEN-2020-067345.00 (764935) 345 kV Bus a. Apply Fault at the GEN-2020-067345.00 (764935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-067 (764935) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-067 (764935) 345.0 kV to G20-067-XFM2 (764941) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on G20-067-TAP 345.00 (764945) 345 kV Bus a. Apply Fault at the G20-067-TAP 345.00 (764945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-067-TAP (764945) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. G20-067-TAP (764945) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on G20-068-SS1 345.00 (764948) 345 kV Bus a. Apply Fault at the G20-068-SS1 345.00 (764948) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-068-SS1 (764948) 345.0 kV to GEN-2020-068 (764950) 345.0 kV Transmission Circuit #1 b.2. G20-068-SS1 (764948) 345.0 kV to G20-068-XFM1 (764953) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on G20-068-SS2 345.00 (764949) 345 kV Bus a. Apply Fault at the G20-068-SS2 345.00 (764949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-068-SS2 (764949) 345.0 kV to GEN-2020-068 (764950) 345.0 kV Transmission Circuit #1 b.2. G20-068-SS2 (764949) 345.0 kV to G20-068-XFM2 (764956) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply Fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 6 (525531) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 3 (525828) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES 6 (526337) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BECKHAM7 (516059) 345 kV Bus a. Apply Fault at the BECKHAM7 (516059) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on POTTER_CO 7 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 7 (523961) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply Fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on ELK_CT1 345.00 (525850) 345 kV Bus a. Apply Fault at the ELK_CT1 345.00 (525850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.4. ELK_CT1 (525850) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply Fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.4. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.6. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.8. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.9. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.10. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.11. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.12. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.13. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.14. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.6. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.7. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002, 527003) and TOLK (525561, 525562) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G17-100 (589383) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV to GRAPEVN_TR11 (523769) 13.2 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_001 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345 kV Bus a. Apply Fault at the CROSSROADS (527656) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. RSVLT_CC_E 7 (527655) 345.0 kV to remove bus # b.4. MILO_WIND 1 (527653) 0.7 kV to remove bus # b.5. RSVLT_GEN1 1 (527651) 0.7 kV to remove bus # b.6. RSVLT_GEN2 1 (527652) 0.7 kV to remove bus # b.7. RSVLT_CC_W 7 (527654) 345.0 kV to remove bus # b.8. SAGSFT3_2.21 (527605) 0.7 kV to Generator #1 b.9. SAGSFT4_2.21 (527607) 0.7 kV to Generator #1 b.10. SAGSFT1_2.21 (527614) 0.7 kV to Generator #1 b.11. SAGSFT1_2.01 (527615) 0.7 kV to Generator #1 b.12. SAGSFT2_2.21 (527617) 0.7 kV to Generator #1 b.13. SAGSFT2_2.01 (527618) 0.7 kV to Generator #1 b.14. SAGA_NDCOL 7 (527598) 345.0 kV to remove bus # b.15. SAGA_SDCOL 7 (527599) 345.0 kV to remove bus # b.16. SAGA_SMEAS 7 (527600) 345.0 kV to remove bus # b.17. SAGA_NCOL 7 (527601) 345.0 kV to remove bus # b.18. SAGANCOL1 1 (527602) 34.5 kV to remove bus # b.19. SAGANCOL2 1 (527603) 34.5 kV to remove bus # b.20. GRDXFR3 1 (527604) 0.5 kV to remove bus # b.21. SAGSFT3_2.21 (527605) 0.7 kV to remove bus # b.22. GRDXFR4 1 (527606) 0.5 kV to remove bus # b.23. SAGSFT4_2.21 (527607) 0.7 kV to remove bus # b.24. SUB BUS #3 1 (527608) 34.5 kV to remove bus # b.25. SUB BUS #4 1 (527609) 34.5 kV to remove bus # b.26. SAGA_SCOL 7 (527610) 345.0 kV to remove bus # b.27. SAGASCOL1 1 (527611) 34.5 kV to remove bus # b.28. SAGASCOL2 1 (527612) 34.5 kV to remove bus # b.29. GRDXFR1 1 (527613) 0.5 kV to remove bus # b.30. SAGSFT1_2.21 (527614) 0.7 kV to remove bus # b.31. SAGSFT1_2.01 (527615) 0.7 kV to remove bus # b.32. GRDXFR2 1 (527616) 0.5 kV to remove bus # b.33. SAGSFT2_2.21 (527617) 0.7 kV to remove bus # b.34. SAGSFT2_2.01 (527618) 0.7 kV to remove bus # b.35. SAGA_NCLTR31 (527621) 13.8 kV to remove bus # b.36. SAGA_NCLTR41 (527622) 13.8 kV to remove bus # b.37. SAGA_SCLTR11 (527623) 13.8 kV to remove bus # b.38. SAGA_SCLTR21 (527624) 13.8 kV to remove bus # b.39. SUB BUS #1 (527628) 34.5 kV to remove bus # b.40. SUB BUS #2 (527629) 34.5 kV to remove bus # b.41. CROSSROADS 7 (527656) 345.0 kV to remove bus # b.42. RSVLT_WIND11 (527658) 34.5 kV to remove bus # b.43. RSVLT_WIND21 (527659) 34.5 kV to remove bus # b.44. RSVLT_COL1 1 (527660) 34.5 kV to remove bus # b.45. RSVLT_COL2 1 (527661) 34.5 kV to remove bus # b.46. RSVLT_TR1 1 (527662) 13.2 kV to remove bus # b.47. RSVLT_TR2 1 (527663) 13.2 kV to remove bus # b.48. RSVLT_COL1 7 (527666) 345.0 kV to remove bus # b.49. RSVLT_COL2 7 (527667) 345.0 kV to remove bus # b.50. MILO_CB (577120) 34.5 kV to remove bus # b.51. MILO_WND (577121) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_002 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345 kV Bus a. Apply Fault at the CROSSROADS (527656) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CROSSROADS 7 (527656) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.2. CROSSROADS 7 (527656) 345.0 kV to SAGA_SCOL 7 (527610) 345.0 kV Transmission Circuit #1 b.3. SAGSFT3_2.21 (527605) 0.7 kV to remove bus # b.4. GRDXFR4 1 (527606) 0.5 kV to remove bus # b.5. SAGSFT4_2.21 (527607) 0.7 kV to remove bus # b.6. SUB BUS #3 1 (527608) 34.5 kV to remove bus # b.7. SUB BUS #4 1 (527609) 34.5 kV to remove bus # b.8. GRDXFR1 1 (527613) 0.5 kV to remove bus # b.9. SAGSFT1_2.21 (527614) 0.7 kV to remove bus # b.10. SAGSFT1_2.01 (527615) 0.7 kV to remove bus # b.11. GRDXFR2 1 (527616) 0.5 kV to remove bus # b.12. SAGSFT2_2.21 (527617) 0.7 kV to remove bus # b.13. SAGSFT2_2.01 (527618) 0.7 kV to remove bus # b.14. SAGA_NDCOL 7 (527598) 345.0 kV to remove bus # b.15. SAGA_SDCOL 7 (527599) 345.0 kV to remove bus # b.16. SAGA_SMEAS 7 (527600) 345.0 kV to remove bus # b.17. SAGA_NCOL 7 (527601) 345.0 kV to remove bus # b.18. SAGANCOL1 1 (527602) 34.5 kV to remove bus # b.19. SAGANCOL2 1 (527603) 34.5 kV to remove bus # b.20. GRDXFR3 1 (527604) 0.5 kV to remove bus # b.21. SAGA_SCOL 7 (527610) 345.0 kV to remove bus # b.22. SAGASCOL1 1 (527611) 34.5 kV to remove bus # b.23. SAGASCOL2 1 (527612) 34.5 kV to remove bus # b.24. SAGA_NCLTR31 (527621) 13.8 kV to remove bus # b.25. SAGA_NCLTR41 (527622) 13.8 kV to remove bus # b.26. SAGA_SCLTR11 (527623) 13.8 kV to remove bus # b.27. SAGA_SCLTR21 (527624) 13.8 kV to remove bus # b.28. SUB BUS #1 (527628) 34.5 kV to remove bus # b.29. SUB BUS #2 (527629) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_003 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY (527802) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 b.4. EDDY_TR 1 (527796) 13.2 kV to remove bus # b.5. EDDY_CNTY 7 (527802) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_004 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY (527802) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.4. EDDY_TR 1 (527796) 13.2 kV to remove bus # b.5. EDDY_CNTY 7 (527802) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_005 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY (527802) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. EDDY_NORTH 6 (527799) 230.0 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.5. EDDY_TR 1 (527796) 13.2 kV to remove bus # b.6. EDDY_CNTY 7 (527802) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_006 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #2 b.2. NOVUS1 7 (523112) 345.0 kV to remove bus # b.3. NOVUS1 3 (523111) 115.0 kV to remove bus # b.4. NOVUS1 1 (523109) 34.5 kV to remove bus # b.5. NOVUS_WND 1 (523107) 4.2 kV to remove bus # b.6. NOVUS1_TR1 1 (523110) 13.8 kV to remove bus # b.7. NOVUS_WND 1 (523107) 4.2 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT (527896) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7 (527896) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.3. HOBBS_TR3 1 (527895) 13.2 kV to remove bus # b.4. HOBBS_INT 7 (527896) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_008 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_009 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_010 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.5. YOAKUM_TR1 (526937) 13.2 kV to remove bus # b.6. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_011 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_012 | Single Phase Fault with Stuck Breaker on TUCO (525832) 345 kV Bus a. Apply Fault at the TUCO (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002, 527003) and TOLK (525561, 525562) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_013 | Single Phase Fault with Stuck Breaker on POTTERCO (523959) 230 kV Bus a. Apply Fault at the POTTERCO (523959) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BUSHLAND 6 (524267) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.2. ROLLHILLS 6 (524010) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_014 | Single Phase Fault with Stuck Breaker on YOAKUM (526935) 230 kV Bus a. Apply Fault at the YOAKUM (526935) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM 3 (526934) 115.0 kV to YOAKUM_TR1 1 (526931) 13.2 kV Three Winding #1 b.2. NEEDMORE 6 (525586) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_015 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002, 527003) and TOLK (525561, 525562) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_016 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to DEMPSE34.5_4 (511584) 34.5 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_017 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 b.2. TUCO_INT 7 (525832) 345.0 kV to DEMPSE34.5_4 (511584) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_018 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_019 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_020 | Single Phase Fault with Stuck Breaker on SWISHER (525213) 230 kV Bus a. Apply Fault at the SWISHER (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to Switched Shunt Device # b.2. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_021 | Single Phase Fault with Stuck Breaker on TUCO_INT (525830) 230 kV Bus a. Apply Fault at the TUCO_INT (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to Switched Shunt Device # b.2. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_022 | Single Phase Fault with Stuck Breaker on BUSHLAND (524267) 230 kV Bus a. Apply Fault at the BUSHLAND (524267) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BUSHLAND 6 (524267) 230.0 kV to WILDOR2_JUS6 (524290) 230.0 kV Transmission Circuit #1 b.2. BUSHLAND 6 (524267) 230.0 kV to Switched Shunt Device # b.3. BUSHLAND 6 (524267) 230.0 kV to BUSHLAND 3 (524266) 115.0 kV to BSHLND_TR1 1 (524263) 13.2 kV Three Winding #1 b.4. WILDORA_GEN1 (524285) 0.7 kV to remove bus # b.5. GS-PHWD_GEN1 (524287) 0.7 kV to remove bus # b.6. BUSHLAND 6 (524267) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.7. BUSHLAND 6 (524267) 230.0 kV to DEAFSMITH 6 (524623) 230.0 kV Transmission Circuit #1 b.8. WILDOR_WND 1 (524275) 34.5 kV to remove bus # b.9. WILDOR_WND 6 (524276) 230.0 kV to remove bus # b.10. GS-PHWDRNCH1 (524289) 34.5 kV to remove bus # b.11. WILDOR2_JUS6 (524290) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_023 | Single Phase Fault with Stuck Breaker on HARRINGTON-G3 (523979) 230 kV Bus a. Apply Fault at the HARRINGTON-G3 (523979) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_EST 6 (523979) 230.0 kV to PRINGLE 6 (523267) 230.0 kV Transmission Circuit #1 b.2. HARRNG_EST 6 (523979) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.3. HARRNG_EST 6 (523979) 230.0 kV to remove bus # b.4. HARRNGTON3 1 (523973) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_024 | Single Phase Fault with Stuck Breaker on JONES-G1 (526337) 230 kV Bus a. Apply Fault at the JONES-G1 (526337) 230 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. JONES_1 1 (526331) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_025 | Single Phase Fault with Stuck Breaker on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. PLANT_X 6 (525481) 230.0 kV to remove bus #1 b.2. PLANT_X4 1 (525494) 20.0 kV to Generator #1 b.3. PLANTX_TR1 1 (525479) 13.2 kV to remove bus # b.4. PLANT_X4 1 (525494) 20.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_026 | Single Phase Fault with Stuck Breaker on GRASSLAND 6 (526677) 230 kV Bus a. Apply Fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. GRASSLAND 6 (526677) 230.0 kV to remove bus #1 b.2. CIRRUS_WND 1 (526678) 0.7 kV to Generator #1 b.3. GRASLND_TR11 (526674) 13.2 kV to remove bus # b.4. CIRRUS_WND 1 (526678) 0.7 kV to remove bus # b.5. CIRRUS_WND 6 (526679) 230.0 kV to remove bus # b.6. CIRRUS_WND (599125) 34.5 kV to remove bus # b.7. CIRRUS_CB (599126) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_027 | Single Phase Fault with Stuck Breaker on BUSHLAND (524267) 230 kV Bus a. Apply Fault at the BUSHLAND (524267) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BSHLND_TR1 1 (524263) 13.2 kV to remove bus # b.2. BUSHLAND 6 (524267) 230.0 kV to DEAFSMITH 6 (524623) 230.0 kV Transmission Circuit #1 b.3. BUSHLAND 6 (524267) 230.0 kV to WILDOR2_JUS6 (524290) 230.0 kV Transmission Circuit #1 b.4. WILDORA_GEN1 (524285) 0.7 kV to Generator #1 b.5. GS-PHWD_GEN1 (524287) 0.7 kV to Generator #1 b.6. BUSHLAND 6 (524267) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.7. BUSHLAND 6 (524267) 230.0 kV to remove bus # b.8. WILDOR_WND 1 (524275) 34.5 kV to remove bus # b.9. WILDOR_WND 6 (524276) 230.0 kV to remove bus # b.10. WILDORA_GEN1 (524285) 0.7 kV to remove bus # b.11. GS-PHWD_GEN1 (524287) 0.7 kV to remove bus # b.12. GS-PHWDRNCH1 (524289) 34.5 kV to remove bus # b.13. WILDOR2_JUS6 (524290) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_028 | Single Phase Fault with Stuck Breaker on BUSHLAND (524267) 230 kV Bus a. Apply Fault at the BUSHLAND (524267) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BSHLND_TR1 1 (524263) 13.2 kV to remove bus # b.2. BUSHLAND 6 (524267) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.3. BUSHLAND 6 (524267) 230.0 kV to WILDOR2_JUS6 (524290) 230.0 kV Transmission Circuit #1 b.4. WILDORA_GEN1 (524285) 0.7 kV to Generator #1 b.5. GS-PHWD_GEN1 (524287) 0.7 kV to Generator #1 b.6. BUSHLAND 6 (524267) 230.0 kV to DEAFSMITH 6 (524623) 230.0 kV Transmission Circuit #1 b.7. BUSHLAND 6 (524267) 230.0 kV to remove bus # b.8. WILDOR_WND 1 (524275) 34.5 kV to remove bus # b.9. WILDOR_WND 6 (524276) 230.0 kV to remove bus # b.10. WILDORA_GEN1 (524285) 0.7 kV to remove bus # b.11. GS-PHWD_GEN1 (524287) 0.7 kV to remove bus # b.12. GS-PHWDRNCH1 (524289) 34.5 kV to remove bus # b.13. WILDOR2_JUS6 (524290) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_029 | Single Phase Fault with Stuck Breaker on GRASSLAND (526677) 230 kV Bus a. Apply Fault at the GRASSLAND (526677) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRASSLAND 6 (526677) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. GRASSLAND 3 (526676) 115.0 kV to LYNN_CNTY 3 (526656) 115.0 kV Transmission Circuit #1 b.3. CIRRUS_WND 1 (526678) 0.7 kV to Generator #1 b.4. LG-TWO_DRAW2 (526513) 69.0 kV to remove bus # b.5. SP-SLATON 2 (526569) 69.0 kV to remove bus # b.6. SOUTHLAND 2 (526576) 69.0 kV to remove bus # b.7. LG-HAKBERRY2 (526583) 69.0 kV to remove bus # b.8. DIEKEMPER 2 (526592) 69.0 kV to remove bus # b.9. GARZA 2 (526622) 69.0 kV to remove bus # b.10. GRASLND_TR11 (526674) 13.2 kV to remove bus # b.11. GRASSLAND 3 (526676) 115.0 kV to remove bus # b.12. GRASSLAND 6 (526677) 230.0 kV to remove bus # b.13. CIRRUS_WND 1 (526678) 0.7 kV to remove bus # b.14. CIRRUS_WND 6 (526679) 230.0 kV to remove bus # b.15. GRAHAM_TR2 1 (526691) 13.2 kV to remove bus # b.16. GRAHAM_TR1 1 (526692) 13.2 kV to remove bus # b.17. GRAHAM 2 (526693) 69.0 kV to remove bus # b.18. GRAHAM 3 (526694) 115.0 kV to remove bus # b.19. JST_CORNER 2 (526799) 69.0 kV to remove bus # b.20. BG-FLUVANNA2 (526814) 69.0 kV to remove bus # b.21. BG-JSTBG_TP2 (526821) 69.0 kV to remove bus # b.22. CIRRUS_WND (599125) 34.5 kV to remove bus # b.23. CIRRUS_CB (599126) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_030 | Single Phase Fault with Stuck Breaker on LAMB (525636) 115 kV Bus a. Apply Fault at the LAMB (525636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 b.2. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 b.3. LAMB_CNTY 6 (525637) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.4. SUDANRURAL 2 (525592) 69.0 kV to remove bus # b.5. LC-SANDHLL+2 (525599) 69.0 kV to remove bus # b.6. AMHERST 2 (525606) 69.0 kV to remove bus # b.7. W_LITTLFLD 2 (525613) 69.0 kV to remove bus # b.8. LTFLD_S&CTY2 (525620) 69.0 kV to remove bus # b.9. LAMB_TR1 1 (525631) 13.2 kV to remove bus # b.10. LAMB_TR2 1 (525632) 13.2 kV to remove bus # b.11. LAMB_TR3 1 (525633) 13.2 kV to remove bus # b.12. LAMB_CNTY 2 (525635) 69.0 kV to remove bus # b.13. LAMB_CNTY 3 (525636) 115.0 kV to remove bus # b.14. LAMB_CNTY 6 (525637) 230.0 kV to remove bus # b.15. LC-LTTLFLD+2 (525650) 69.0 kV to remove bus # b.16. W_ANTON_TP 2 (525657) 69.0 kV to remove bus # b.17. LC-SPD&HART2 (525664) 69.0 kV to remove bus # b.18. BAINER 2 (525671) 69.0 kV to remove bus # b.19. W_ANTON 2 (525678) 69.0 kV to remove bus # b.20. LC-LUMSCHAP2 (525687) 69.0 kV to remove bus # b.21. HOBGOOD 2 (525694) 69.0 kV to remove bus # b.22. PUMP/YH_TP 2 (525697) 69.0 kV to remove bus # b.23. PHLLPPMP#2 2 (525701) 69.0 kV to remove bus # b.24. YELLOWHOUSE2 (525703) 69.0 kV to remove bus # b.25. MIDAMERI#2 2 (525708) 69.0 kV to remove bus # b.26. WHITHARRAL 2 (525717) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_031 | Single Phase Fault with Stuck Breaker on LAMB (525636) 115 kV Bus a. Apply Fault at the LAMB (525636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 b.2. LAMB_TR3 1 (525633) 13.2 kV to remove bus # b.3. LAMB_CNTY 3 (525636) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 b.4. SUDANRURAL 2 (525592) 69.0 kV to remove bus # b.5. LC-SANDHLL+2 (525599) 69.0 kV to remove bus # b.6. AMHERST 2 (525606) 69.0 kV to remove bus # b.7. W_LITTLFLD 2 (525613) 69.0 kV to remove bus # b.8. LTFLD_S&CTY2 (525620) 69.0 kV to remove bus # b.9. LAMB_TR1 1 (525631) 13.2 kV to remove bus # b.10. LAMB_TR2 1 (525632) 13.2 kV to remove bus # b.11. LAMB_CNTY 2 (525635) 69.0 kV to remove bus # b.12. LAMB_CNTY 3 (525636) 115.0 kV to remove bus # b.13. LC-LTTLFLD+2 (525650) 69.0 kV to remove bus # b.14. W_ANTON_TP 2 (525657) 69.0 kV to remove bus # b.15. LC-SPD&HART2 (525664) 69.0 kV to remove bus # b.16. BAINER 2 (525671) 69.0 kV to remove bus # b.17. W_ANTON 2 (525678) 69.0 kV to remove bus # b.18. LC-LUMSCHAP2 (525687) 69.0 kV to remove bus # b.19. HOBGOOD 2 (525694) 69.0 kV to remove bus # b.20. PUMP/YH_TP 2 (525697) 69.0 kV to remove bus # b.21. PHLLPPMP#2 2 (525701) 69.0 kV to remove bus # b.22. YELLOWHOUSE2 (525703) 69.0 kV to remove bus # b.23. MIDAMERI#2 2 (525708) 69.0 kV to remove bus # b.24. WHITHARRAL 2 (525717) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_032 | Single Phase Fault with Stuck Breaker on LUBBOCK_STH (526269) 230 kV Bus a. Apply Fault at the LUBBOCK_STH (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 b.2. LUBBCK_STH 3 (526268) 115.0 kV to ALLEN 3 (526213) 115.0 kV Transmission Circuit #1 b.3. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.4. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 b.6. LBB_STH TR31 (526264) 13.2 kV to remove bus # b.7. WOODROW 3 (526602) 115.0 kV to LYNN_CNTY 3 (526656) 115.0 kV Transmission Circuit #1 b.8. IVORY 2 (526205) 69.0 kV to remove bus # b.9. BATTON_S 2 (526228) 69.0 kV to remove bus # b.10. ACCO 2 (526249) 69.0 kV to remove bus # b.11. IVORY_TP 2 (526256) 69.0 kV to remove bus # b.12. LBB_STH TR11 (526265) 13.2 kV to remove bus # b.13. LBB_STH TR21 (526266) 13.2 kV to remove bus # b.14. LUBBCK_STH 2 (526267) 69.0 kV to remove bus # b.15. LUBBCK_STH 3 (526268) 115.0 kV to remove bus # b.16. LUBBCK_STH 6 (526269) 230.0 kV to remove bus # b.17. WOODROW 3 (526602) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_033 | Single Phase Fault with Stuck Breaker on OASIS (524874) 115 kV Bus a. Apply Fault at the OASIS (524874) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OASIS 3 (524874) 115.0 kV to PORTALES 3 (524924) 115.0 kV Transmission Circuit #1 b.2. NORRIS_TP 3 (524764) 115.0 kV to CURRY 3 (524822) 115.0 kV Transmission Circuit #1 b.3. W_CLOVIS 3 (524784) 115.0 kV to FE-CLVS_INT3 (524808) 115.0 kV Transmission Circuit #1 b.4. OASIS 6 (524875) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 b.5. OASIS 6 (524875) 230.0 kV to OASIS 3 (524874) 115.0 kV to OASIS_TR1 1 (524872) 13.2 kV Three Winding #1 b.6. NORRIS_TP 3 (524764) 115.0 kV to remove bus # b.7. W_CLOVIS 3 (524784) 115.0 kV to remove bus # b.8. CANNON_TP 3 (524790) 115.0 kV to remove bus # b.9. CANNONAFB 3 (524794) 115.0 kV to remove bus # b.10. PERIMETER 3 (524797) 115.0 kV to remove bus # b.11. NORRIS 3 (524801) 115.0 kV to remove bus # b.12. FE-CHZPLT 3 (524863) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_034 | Single Phase Fault with Stuck Breaker on CARLISLE (526160) 115 kV Bus a. Apply Fault at the CARLISLE (526160) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SP-ERSKINE 3 (526109) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.2. YUMA_INT 3 (526475) 115.0 kV to SP-WOLF_TP 3 (526481) 115.0 kV Transmission Circuit #1 b.3. CRLSLE_TR1 1 (526157) 13.2 kV to remove bus # b.4. CARLISLE 3 (526160) 115.0 kV to MURPHY 3 (526192) 115.0 kV Transmission Circuit #1 b.5. SP-ERSKINE 3 (526109) 115.0 kV to remove bus # b.6. SP-CARLISLE2 (526130) 69.0 kV to remove bus # b.7. CRLSLE_TR2 1 (526158) 13.2 kV to remove bus # b.8. CARLISLE 2 (526159) 69.0 kV to remove bus # b.9. CARLISLE 3 (526160) 115.0 kV to remove bus # b.10. LP-DOUD_TP 3 (526162) 115.0 kV to remove bus # b.11. LP-DOUD 3 (526176) 115.0 kV to remove bus # b.12. SW_6878 2 (526184) 69.0 kV to remove bus # b.13. BATTON_N 2 (526221) 69.0 kV to remove bus # b.14. SP-WOLF_TP 3 (526481) 115.0 kV to remove bus # b.15. SP-WOLFORTH3 (526483) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_035 | Single Phase Fault with Stuck Breaker on WOLFFORTH (526524) 115 kV Bus a. Apply Fault at the WOLFFORTH (526524) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LP-DOUD_TP 3 (526162) 115.0 kV to CARLISLE 3 (526160) 115.0 kV Transmission Circuit #1 b.2. WOLFRTH_TR11 (526522) 13.2 kV to remove bus # b.3. WOLFFORTH 3 (526524) 115.0 kV to TERRY_CNTY 3 (526736) 115.0 kV Transmission Circuit #1 b.4. LP-DOUD_TP 3 (526162) 115.0 kV to remove bus # b.5. LP-DOUD 3 (526176) 115.0 kV to remove bus # b.6. YUMA_INT 3 (526475) 115.0 kV to remove bus # b.7. SP-WOLF_TP 3 (526481) 115.0 kV to remove bus # b.8. SP-WOLFORTH3 (526483) 115.0 kV to remove bus # b.9. WOLFFORTH 3 (526524) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29S | Transfer | GROUP5_P4_SPS_FAULT_036 | Single Phase Fault with Stuck Breaker on LAMB (525636) 115 kV Bus a. Apply Fault at the LAMB (525636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 b.2. LAMB_CNTY 3 (525636) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 b.3. LAMB_CNTY 6 (525637) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.4. SUDANRURAL 2 (525592) 69.0 kV to remove bus # b.5. LC-SANDHLL+2 (525599) 69.0 kV to remove bus # b.6. AMHERST 2 (525606) 69.0 kV to remove bus # b.7. W_LITTLFLD 2 (525613) 69.0 kV to remove bus # b.8. LTFLD_S&CTY2 (525620) 69.0 kV to remove bus # b.9. LAMB_TR1 1 (525631) 13.2 kV to remove bus # b.10. LAMB_TR2 1 (525632) 13.2 kV to remove bus # b.11. LAMB_TR3 1 (525633) 13.2 kV to remove bus # b.12. LAMB_CNTY 2 (525635) 69.0 kV to remove bus # b.13. LAMB_CNTY 3 (525636) 115.0 kV to remove bus # b.14. LAMB_CNTY 6 (525637) 230.0 kV to remove bus # b.15. LC-LTTLFLD+2 (525650) 69.0 kV to remove bus # b.16. W_ANTON_TP 2 (525657) 69.0 kV to remove bus # b.17. LC-SPD&HART2 (525664) 69.0 kV to remove bus # b.18. BAINER 2 (525671) 69.0 kV to remove bus # b.19. W_ANTON 2 (525678) 69.0 kV to remove bus # b.20. LC-LUMSCHAP2 (525687) 69.0 kV to remove bus # b.21. HOBGOOD 2 (525694) 69.0 kV to remove bus # b.22. PUMP/YH_TP 2 (525697) 69.0 kV to remove bus # b.23. PHLLPPMP#2 2 (525701) 69.0 kV to remove bus # b.24. YELLOWHOUSE2 (525703) 69.0 kV to remove bus # b.25. MIDAMERI#2 2 (525708) 69.0 kV to remove bus # b.26. WHITHARRAL 2 (525717) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_001 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_002 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_003 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Unstable rotor angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 28 additional units in Group05. The same rotor angle instability was also present in the base case. Neither reducing the Gen-2022-147 active power output to 75%, 50%, 25%, or 0% nor reducing the fault-clearing time to as low as 0.05 cycles resolved the instability. Gen-2022-147 : PTDF=0.3033 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_004 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.3. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_005 | 3 Phase fault on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.2. LAMB_TR3 1 (525633) 13.2 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Three Winding #1 b.3. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_006 | 3 Phase fault on LAMTON 3115.00 (525414) 115 kV Bus a. Apply fault at the LAMTON 3115.00 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 (525414) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_007 | 3 Phase fault on LAMB_CNTY 3115.00 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3115.00 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_008 | 3 Phase fault on TULIA_TP 3115.00 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3115.00 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MU-TULIA 3 (522800) 115.0 kV to TULIA_TP 3 (525179) 115.0 kV Transmission Circuit #1 b.2. HAPPY_INT 3 (525154) 115.0 kV to TULIA_TP 3 (525179) 115.0 kV Transmission Circuit #1 b.3. TULIA_TP 3 (525179) 115.0 kV to KRESS_INT 3 (525192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_009 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_010 | 3 Phase fault on CROSBY 3115.00 (525926) 115 kV Bus a. Apply fault at the CROSBY 3115.00 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 (525926) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_011 | 3 Phase fault on SP-WOLF_TP 3115.00 (526481) 115 kV Bus a. Apply fault at the SP-WOLF_TP 3115.00 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to LP-DOUD_TP 3 (526162) 115.0 kV Transmission Circuit #1 b.2. LP-DOUD_TP 3 (526162) 115.0 kV to LP-DOUD 3 (526176) 115.0 kV Transmission Circuit #1 b.3. LP-DOUD_TP 3 (526162) 115.0 kV to SP-WOLF_TP 3 (526481) 115.0 kV Transmission Circuit #1 b.4. SP-UPLAND (526198) 115.0 kV to SP-WOLF_TP 3 (526481) 115.0 kV Transmission Circuit #1 b.5. YUMA_INT 3 (526475) 115.0 kV to SP-WOLF_TP 3 (526481) 115.0 kV Transmission Circuit #1 b.6. SP-WOLF_TP 3 (526481) 115.0 kV to SP-WOLFORTH3 (526483) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_012 | 3 Phase fault on CALLAHAN 3115.00 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3115.00 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 (525326) 115.0 kV to CALLAHAN 3 (525763) 115.0 kV Transmission Circuit #1 b.2. CALLAHAN 3 (525763) 115.0 kV to FLOYD_CNTY 3 (525780) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_013 | 3 Phase fault on COX 3115.00 (525326) 115 kV Bus a. Apply fault at the COX 3115.00 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 (525326) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_014 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_015 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_016 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_017 | 3 Phase fault on STANTON_W 3115.00 (526076) 115 kV Bus a. Apply fault at the STANTON_W 3115.00 (526076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.2. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_018 | 3 Phase fault on LUBBCK_STH 3115.00 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3115.00 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_019 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to MURPHY 3 (526192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_020 | 3 Phase fault on SP-ERSKINE 3115.00 (526109) 115 kV Bus a. Apply fault at the SP-ERSKINE 3115.00 (526109) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ERSKINE 3 (526109) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.2. SP-ERSKINE 3 (526109) 115.0 kV to CARLISLE 3 (526160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_021 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_022 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to SWISHER 3 (525212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_023 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_024 | 3 Phase fault on KRS_RURL_TP3115.00 (525226) 115 kV Bus a. Apply fault at the KRS_RURL_TP3115.00 (525226) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to KRS_RURL_TP3 (525226) 115.0 kV Transmission Circuit #1 b.2. KRESS_RURAL3 (525225) 115.0 kV to KRS_RURL_TP3 (525226) 115.0 kV Transmission Circuit #1 b.3. KRS_RURL_TP3 (525226) 115.0 kV to N_PLAINVEW 3 (525257) 115.0 kV Transmission Circuit #1 b.4. N_PLAINVEW 3 (525257) 115.0 kV to KISER 3 (525272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_025 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to BLANCO 3 (525803) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_026 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_027 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_028 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_029 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_030 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Unstable rotor angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 26 additional units in Group05. No such rotor angle instability was observed in the base case. At 50% Pgen, no rotor-angle instability was observed; however, oscillatory behavior persisted in the output power of the Gains units (527001, 527002, 527003) and Tolk units (525561, 525562). Gen-2022-147 : PTDF=0.2538 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_031 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003) and Tolk units (525561, 525562), along with frequency and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no frequency oscillations were observed in the base case. Reducing the Gen-2022-147 active power output to 75%, 50%, or 25% did not resolve the active power oscillations. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_032 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_033 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003) and Tolk units (525561, 525562), along with frequency and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no frequency oscillations were observed in the base case. Reducing the Gen-2022-147 active power output to 75%, 50%, or 25% did not resolve the active power oscillations. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_034 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_035 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_036 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_038 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Unstable rotor angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 32 additional units in Group05. The same rotor angle instability was also present in the base case. Neither reducing the Gen-2022-147 active power output to 75%, 50%, 25%, or 0% nor reducing the fault-clearing time to as low as 0.05 cycles resolved the instability. Gen-2022-147 : PTDF=0.3033 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_039 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_040 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_041 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_042 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_043 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002), Tolk (525561) and Hobbs (527903)units. The oscillations meet the Rotor Angle Damping Requirements of SPP (SPPR1=0.6655). CQ request did not meet the 3% criteria. | No mitigations required.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_044 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003) and Tolk units (525561, 525562), along with frequency and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no frequency oscillations were observed in the base case. Reducing the Gen-2022-147 active power output to 75%, 50%, or 25% did not resolve the active power oscillations. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_045 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_046 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_047 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_048 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips LANOGSU1 (523812) unit. After disabling protection relays, oscillatory behavior observed in power output of Gains (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_049 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips LANOGSU1 (523812) unit. After disabling protection relays, oscillatory behavior observed in power output of Gains (527001, 527002, 527003) and Tolk (525561) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_050 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips LANOGSU1 (523812) unit. After disabling protection relays, oscillatory behavior observed in power output of Gains (527001, 527002, 527003) and Tolk (525561, 525562) units. The oscillations meet the Rotor Angle Damping Requirements of SPP (SPPR1=0.862). CQ request did not meet the 3% criteria. | No mitigations required.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_051 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips LANOGSU1 (523812) unit. After disabling protection relays, oscillatory behavior observed in power output of Gains (527001, 527002, 527003) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_052 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_053 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips LANOGSU1 (523812) unit. After disabling protection relays, oscillatory behavior observed in power output of Gains (527001, 527002, 527003) and Tolk (525561, 525562) units. | Disabling protection relay and applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_054 | 3 Phase fault on PLSNT_HILL 6230.00 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6230.00 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 (524770) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_055 | 3 Phase fault on OASIS 6230.00 (524875) 230 kV Bus a. Apply fault at the OASIS 6230.00 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 (524875) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_056 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_057 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_058 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_059 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_060 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to PLANT_X 6 (525481) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip LANOGSU1 (523812) and G18-089 (763189) units. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_061 | 3 Phase fault on PLANT_X 3115.00 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3115.00 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_062 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_063 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_064 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to SUNDOWN 6 (526435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_065 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to G17-146-TAP (760498) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Protection relay trips LANOGSU1 (523812) unit. After disabling protection relays, oscillatory behavior observed in power output of Gains (527001, 527002, 527003) and Tolk (525561, 525562) units. | Disabling protection relay and applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_066 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip LANOGSU1 (523812) and G18-089 (763189) units. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_067 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip LANOGSU1 (523812), G18-099 (763254, 763257) and G18-089 (763189) units. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_068 | 3 Phase fault on NEEDMORE 6230.00 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6230.00 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 (525586) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_069 | 3 Phase fault on SP-ABERNTHY269.000 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY269.000 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 (525731) 69.0 kV to TUCO_INT2 2 (525816) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_070 | 3 Phase fault on HALECENTER 269.000 (525738) 69 kV Bus a. Apply fault at the HALECENTER 269.000 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 (525738) 69.0 kV to TUCO_INT 2 (525826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_071 | 3 Phase fault on TUCO_INT 269.000 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 269.000 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 (525826) 69.0 kV to LH-WIL&ELN+2 (525853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_072 | 3 Phase fault on TUCO_INT 269.000 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 269.000 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 (525826) 69.0 kV to SP-NEWDEAL 2 (525885) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_073 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_074 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_075 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Unstable rotor-angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 32 additional units in Group05. The same rotor-angle instability was also present in the base case. The instability persisted when the Gen-2022-147 output was reduced to 50%, 25%, and 0%. Reducing the fault-clearing time to as low as 0.05 cycles did not resolve the instability in the CQ case. However, in the base case, reducing the clearing time to 3 cycles successfully resolved the instability. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_076 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_077 | 3 Phase fault on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 (526161) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_078 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_079 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_080 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_081 | 3 Phase fault on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_082 | 3 Phase fault on JONES 6230.00 (526337) 230 kV Bus a. Apply fault at the JONES 6230.00 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 (526337) 230.0 kV to GRASSLAND 6 (526677) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_083 | 3 Phase fault on SUNDOWN 6230.00 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6230.00 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 (526435) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_084 | 3 Phase fault on AMOCO_SS 6230.00 (526460) 230 kV Bus a. Apply fault at the AMOCO_SS 6230.00 (526460) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 (526460) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_085 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to BRU_SUB 6 (527009) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003) and Tolk units (525561, 525562), along with frequency and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_086 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to INK_BASIN 6 (527028) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003) and Tolk units (525561, 525562), along with frequency and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_087 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to MUSTANG 6 (527149) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003) and Tolk units (525561, 525562), along with frequency and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_088 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_089 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_090 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_091 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the JONES units (526333, 526334) CAPROCK (524779), SPNSPUR (524295) and Tolk units (525561, 525562), along with frequency, voltage and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no voltage and frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_092 | 3 Phase fault on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP (762216) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Unstable rotor angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 32 additional units in Group05. The same rotor angle instability was also present in the base case. Neither reducing the Gen-2022-147 active power output to 75%, 50%, 25%, or 0% nor reducing the fault-clearing time to as low as 0.05 cycles resolved the instability. Gen-2022-147 : PTDF=0.3033 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_093 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to PNM-DC6 (599955) 230.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_094 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_095 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_096 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_097 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_098 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_099 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_100 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to AMA_SOUTH 3 (524414) 115.0 kV to AMA_SO_TR1 1 (524410) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_101 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to ROOSEVELT 3 (524908) 115.0 kV to ROSEVLT_TR11 (524907) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_102 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to KRESS_INT 2 (525191) 69.0 kV to KRESS_TR1 1 (525190) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_103 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV to SWISHER_TR11 (525211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_104 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR1 1 (525451) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_105 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR2 1 (525452) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_106 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR21 (525458) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip LANOGSU1 (523812) and G18-089 (763189) units. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_107 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR11 (525459) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip LANOGSU1 (523812) and G18-089 (763189) units. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_108 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to PLANT_X 3 (525480) 115.0 kV to PLANTX_TR1 1 (525479) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_109 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 2 1 (525538) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_110 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 2 1 (526938) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_111 | 3 Phase fault on LAMB_CNTY 3115.00 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3115.00 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV to LAMB_TR1 1 (525631) 13.2 kV Three Winding #1 b.2. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV to LAMB_TR2 1 (525632) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_112 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV to FLOYD_TR1 1 (525777) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_113 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV to FLOYD_TR2 1 (525778) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_114 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT2 2 (525816) 69.0 kV to TUCO_TR7 1 (525814) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_115 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV to TUCO_TR5 1 (525822) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_116 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV to TUCO_TR6 1 (525823) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_117 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip HALE_WND (525951, 525952, 525953). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_118 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relays trip HALE_WND (525951, 525952, 525953). | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_119 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_120 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_121 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to CARLISLE 2 (526159) 69.0 kV to CRLSLE_TR2 1 (526158) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_122 | 3 Phase fault on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 (526161) 230.0 kV to CARLISLE 3 (526160) 115.0 kV to CRLSLE_TR1 1 (526157) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_123 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV to LBB_STH TR11 (526265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_124 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV to LBB_STH TR31 (526264) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_125 | 3 Phase fault on LUBBCK_EST 3115.00 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3115.00 (526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV to LBB_EST TR21 (526295) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_126 | 3 Phase fault on LUBBCK_EST 3115.00 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3115.00 (526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV to LBB_EST TR31 (526296) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_127 | 3 Phase fault on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV to LBB_EST TR11 (526294) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_128 | 3 Phase fault on WOLFFORTH 6230.00 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6230.00 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 (526525) 230.0 kV to WOLFFORTH 3 (526524) 115.0 kV to WOLFRTH_TR11 (526522) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_129 | 3 Phase fault on GRASSLAND 6230.00 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6230.00 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 (526677) 230.0 kV to GRASSLAND 3 (526676) 115.0 kV to GRASLND_TR11 (526674) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_130 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM 3 (526934) 115.0 kV to YOAKUM_TR1 1 (526931) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002), Tolk (525561) and Hobbs (527903) units. This issue was not observed in base case. CQ request did not meet the 3% criteria. | Reduce clearing time to 3 cycle solves the issue
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_131 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM 3 (526934) 115.0 kV to YOAKUM_TR2 1 (526932) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002), Tolk (525561) and Hobbs (527903) units. This issue was not observed in base case. CQ request did not meet the 3% criteria. | Reduce clearing time to 3 cycle solves the issue
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_132 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_133 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV to HOBBS_TR3 1 (527895) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003) and Hobbs units (525903, 525903), along with Voltage and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no frequency Voltage were observed in the base case. CQ request did not meet the 3% criteria. | Reduce clearing time to 3 cycle solves the issue
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_134 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_135 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_136 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_137 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_138 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_139 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_140 | 3 Phase fault on HALE_WNDCL16230.00 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16230.00 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 (525957) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_141 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_142 | 3 Phase fault on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 (526161) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_143 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_LOCAL_FAULT_144 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_001 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_002 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_003 | 3 Phase fault on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_004 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_005 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_006 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), Tolk (525561) and Hobbs units (525903, 525903), along with frequency and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no frequency oscillations were observed in the base case. CQ request does not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_007 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_008 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), Tolk (525561) and Hobbs units (525903, 525903), along with frequency and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Removal of reclosing solves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_009 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_010 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_011 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_012 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Unstable rotor-angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 32 additional units in Group05. The same rotor-angle instability was also present in the base case. The instability persisted when the Gen-2022-147 output was reduced to 50%, 25%, and 0%. Reducing the fault-clearing time to as low as 0.05 cycles did not resolve the instability in the CQ case. However, in the base case, reducing the clearing time to 3 cycles successfully resolved the instability. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_013 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_014 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_015 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_016 | 3 Phase fault on WHEELER 6230.00 (523777) 230 kV Bus a. Apply fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_017 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_018 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P1_REGIOINAL_FAULT_019 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWHART 6 (525461) 230.0 kV to PLANT_X 6 (525481) 230.0 kV Transmission Circuit #1 b.2. PLANT_X 6 (525481) 230.0 kV to PLANT_X4 1 (525494) 20.0 kV Two Winding #1 b.3. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.4. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 b.5. PLANT_X 6 (525481) 230.0 kV to SUNDOWN 6 (526435) 230.0 kV Transmission Circuit #1 b.6. PLANT_X 6 (525481) 230.0 kV to G17-146-TAP (760498) 230.0 kV Transmission Circuit #1 b.7. PLANTX_TR1 1 (525479) 13.2 kV to PLANT_X 6 (525481) 230.0 kV to PLANT_X 3 (525480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply Fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. LUBBCK_EST 6 (526299) 230.0 kV to GEN-2020-060 (764875) 230.0 kV Transmission Circuit #1 b.3. LBB_EST TR11 (526294) 13.2 kV to LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on GRASSLAND 6230.00 (526677) 230 kV Bus a. Apply Fault at the GRASSLAND 6230.00 (526677) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES 6 (526337) 230.0 kV to GRASSLAND 6 (526677) 230.0 kV Transmission Circuit #1 b.2. GRASSLAND 6 (526677) 230.0 kV to CIRRUS_WND 6 (526679) 230.0 kV Transmission Circuit #1 b.3. GRASLND_TR11 (526674) 13.2 kV to GRASSLAND 6 (526677) 230.0 kV to GRASSLAND 3 (526676) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply Fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.3. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 b.4. LAMB_TR1 1 (525631) 13.2 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Three Winding #1 b.5. LAMB_TR2 1 (525632) 13.2 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Three Winding #2 b.6. LAMB_TR3 1 (525633) 13.2 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Three Winding #1 b.9. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply Fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALLAHAN 3 (525763) 115.0 kV to FLOYD_CNTY 3 (525780) 115.0 kV Transmission Circuit #1 b.2. FLOYD_CNTY 3 (525780) 115.0 kV to BLANCO 3 (525803) 115.0 kV Transmission Circuit #1 b.3. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.4. FLOYD_TR1 1 (525777) 13.2 kV to FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV Three Winding #1 b.5. FLOYD_TR2 1 (525778) 13.2 kV to FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.2. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.3. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.4. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.7. TUCO_TR7 1 (525814) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT2 2 (525816) 69.0 kV Three Winding #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.10. TUCO_TR5 1 (525822) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #2 b.11. TUCO_TR6 1 (525823) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #1 b.15. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 b.16. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply Fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KRESS_INT 3 (525192) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.2. PLAINVW_TP 2 (525291) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 b.3. S_PLAINVEW 2 (525298) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 b.4. COX 3 (525326) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.5. LAMTON 3 (525414) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.6. SP-HALFWAY+2 (525432) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 b.7. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 b.8. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.9. HALE_TR1 1 (525451) 13.2 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV Three Winding #1 b.10. HALE_TR2 1 (525452) 13.2 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV Three Winding #2 b.11. HALE_CNTY 2 (525453) 69.0 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_TR1 1 (525451) 13.2 kV Three Winding #1 b.12. HALE_CNTY 2 (525453) 69.0 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_TR2 1 (525452) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on STANTON_W 3115.00 (526076) 115 kV Bus a. Apply Fault at the STANTON_W 3115.00 (526076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.2. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.3. SP-ERSKINE 3 (526109) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.4. SP-ERSKINE 3 (526109) 115.0 kV to CARLISLE 3 (526160) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply Fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC-BECK +2 (525045) 69.0 kV to SUDANRURAL 2 (525592) 69.0 kV Transmission Circuit #1 b.2. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 b.3. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.4. SUDANRURAL 2 (525592) 69.0 kV to LC-SANDHLL+2 (525599) 69.0 kV Transmission Circuit #1 b.5. LC-SANDHLL+2 (525599) 69.0 kV to AMHERST 2 (525606) 69.0 kV Transmission Circuit #1 b.6. AMHERST 2 (525606) 69.0 kV to W_LITTLFLD 2 (525613) 69.0 kV Transmission Circuit #1 b.7. W_LITTLFLD 2 (525613) 69.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Transmission Circuit #1 b.8. LTFLD_S&CTY2 (525620) 69.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Transmission Circuit #1 b.9. LTFLD_S&CTY2 (525620) 69.0 kV to W_ANTON_TP 2 (525657) 69.0 kV Transmission Circuit #1 b.10. LAMB_CNTY 2 (525635) 69.0 kV to LC-LTTLFLD+2 (525650) 69.0 kV Transmission Circuit #1 b.11. LAMB_CNTY 2 (525635) 69.0 kV to LC-LUMSCHAP2 (525687) 69.0 kV Transmission Circuit #1 b.12. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 b.13. LC-LTTLFLD+2 (525650) 69.0 kV to W_ANTON_TP 2 (525657) 69.0 kV Transmission Circuit #1 b.14. W_ANTON_TP 2 (525657) 69.0 kV to LC-SPD&HART2 (525664) 69.0 kV Transmission Circuit #1 b.15. W_ANTON_TP 2 (525657) 69.0 kV to BAINER 2 (525671) 69.0 kV Transmission Circuit #1 b.16. LC-SPD&HART2 (525664) 69.0 kV to CNTYLINE_TP2 (525723) 69.0 kV Transmission Circuit #1 b.17. BAINER 2 (525671) 69.0 kV to W_ANTON 2 (525678) 69.0 kV Transmission Circuit #1 b.18. LC-LUMSCHAP2 (525687) 69.0 kV to HOBGOOD 2 (525694) 69.0 kV Transmission Circuit #1 b.19. HOBGOOD 2 (525694) 69.0 kV to PUMP/YH_TP 2 (525697) 69.0 kV Transmission Circuit #1 b.20. PUMP/YH_TP 2 (525697) 69.0 kV to YELLOWHOUSE2 (525703) 69.0 kV Transmission Circuit #1 b.21. PUMP/YH_TP 2 (525697) 69.0 kV to MIDAMERI#2 2 (525708) 69.0 kV Transmission Circuit #1 b.22. PHLLPPMP#2 2 (525701) 69.0 kV to YELLOWHOUSE2 (525703) 69.0 kV Transmission Circuit #1 b.23. MIDAMERI#2 2 (525708) 69.0 kV to WHITHARRAL 2 (525717) 69.0 kV Transmission Circuit #1 b.24. WHITHARRAL 2 (525717) 69.0 kV to LC-HODGE_TP2 (525995) 69.0 kV Transmission Circuit #1 b.25. LAMB_TR1 1 (525631) 13.2 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Three Winding #1 b.26. LAMB_TR3 1 (525633) 13.2 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Three Winding #1 b.27. LAMB_CNTY 2 (525635) 69.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR1 1 (525631) 13.2 kV Three Winding #1 b.28. LAMB_CNTY 2 (525635) 69.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR2 1 (525632) 13.2 kV Three Winding #2 b.31. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply Fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.2. SP-ACUFF +2 (525906) 69.0 kV to CROSBY 2 (525925) 69.0 kV Transmission Circuit #1 b.3. SP-ACUFF +2 (525906) 69.0 kV to VICKERS 2 (526123) 69.0 kV Transmission Circuit #1 b.4. CROSBY 3 (525926) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.5. STANTON_N 2 (526073) 69.0 kV to STANTON_E 2 (526075) 69.0 kV Transmission Circuit #z1 b.6. STANTON_N 2 (526073) 69.0 kV to SW_6786_N 2 (526086) 69.0 kV Transmission Circuit #1 b.7. STANTON_E 2 (526075) 69.0 kV to SW_6786_S 2 (526087) 69.0 kV Transmission Circuit #1 b.8. SW_6786_N 2 (526086) 69.0 kV to SW_6786_S 2 (526087) 69.0 kV Transmission Circuit #z1 b.9. SW_6786_N 2 (526086) 69.0 kV to SP-HETTLER 2 (526102) 69.0 kV Transmission Circuit #1 b.10. SW_6786_S 2 (526087) 69.0 kV to PLANTERS 2 (526284) 69.0 kV Transmission Circuit #1 b.11. SP-HETTLER 2 (526102) 69.0 kV to SP-IDALOU +2 (526116) 69.0 kV Transmission Circuit #1 b.12. SP-IDALOU +2 (526116) 69.0 kV to VICKERS 2 (526123) 69.0 kV Transmission Circuit #1 b.13. ACCO 2 (526249) 69.0 kV to CLUTTER 2 (526310) 69.0 kV Transmission Circuit #1 b.14. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.15. PLANTERS 2 (526284) 69.0 kV to LUBBCK_EST 2 (526297) 69.0 kV Transmission Circuit #1 b.16. LUBBCK_EST 2 (526297) 69.0 kV to CLUTTER 2 (526310) 69.0 kV Transmission Circuit #1 b.17. LUBBCK_EST 2 (526297) 69.0 kV to SLATON 2 (526562) 69.0 kV Transmission Circuit #1 b.18. SLATON 2 (526562) 69.0 kV to SP-SLATON 2 (526569) 69.0 kV Transmission Circuit #1 b.19. SP-SLATON 2 (526569) 69.0 kV to SOUTHLAND 2 (526576) 69.0 kV Transmission Circuit #1 b.20. SOUTHLAND 2 (526576) 69.0 kV to LG-HAKBERRY2 (526583) 69.0 kV Transmission Circuit #1 b.21. LG-HAKBERRY2 (526583) 69.0 kV to DIEKEMPER 2 (526592) 69.0 kV Transmission Circuit #1 b.22. LBB_EST TR11 (526294) 13.2 kV to LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Three Winding #1 b.23. LBB_EST TR21 (526295) 13.2 kV to LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV Three Winding #1 b.24. LBB_EST TR31 (526296) 13.2 kV to LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV Three Winding #2 b.25. LUBBCK_EST 2 (526297) 69.0 kV to LUBBCK_EST 3 (526298) 115.0 kV to LBB_EST TR21 (526295) 13.2 kV Three Winding #1 b.26. LUBBCK_EST 2 (526297) 69.0 kV to LUBBCK_EST 3 (526298) 115.0 kV to LBB_EST TR31 (526296) 13.2 kV Three Winding #2 b.29. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 6 (526299) 230.0 kV to LBB_EST TR11 (526294) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply Fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IVORY 2 (526205) 69.0 kV to BATTON_S 2 (526228) 69.0 kV Transmission Circuit #1 b.2. IVORY 2 (526205) 69.0 kV to IVORY_TP 2 (526256) 69.0 kV Transmission Circuit #z1 b.3. IVORY 2 (526205) 69.0 kV to LUBBCK_STH 2 (526267) 69.0 kV Transmission Circuit #1 b.4. ALLEN 3 (526213) 115.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Transmission Circuit #1 b.5. BATTON_N 2 (526221) 69.0 kV to BATTON_S 2 (526228) 69.0 kV Transmission Circuit #z1 b.6. ACCO 2 (526249) 69.0 kV to IVORY_TP 2 (526256) 69.0 kV Transmission Circuit #1 b.7. ACCO 2 (526249) 69.0 kV to CLUTTER 2 (526310) 69.0 kV Transmission Circuit #1 b.8. IVORY_TP 2 (526256) 69.0 kV to LUBBCK_STH 2 (526267) 69.0 kV Transmission Circuit #1 b.9. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.10. LUBBCK_STH 3 (526268) 115.0 kV to WOODROW 3 (526602) 115.0 kV Transmission Circuit #1 b.11. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.12. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 b.13. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 b.14. WOODROW 3 (526602) 115.0 kV to LYNN_CNTY 3 (526656) 115.0 kV Transmission Circuit #1 b.15. LBB_STH TR31 (526264) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #2 b.16. LBB_STH TR11 (526265) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #1 b.17. LBB_STH TR21 (526266) 13.2 kV to LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_STH 2 (526267) 69.0 kV Three Winding #1 b.18. LUBBCK_STH 2 (526267) 69.0 kV to LUBBCK_STH 3 (526268) 115.0 kV to LBB_STH TR21 (526266) 13.2 kV Three Winding #1 b.20. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_STH 6 (526269) 230.0 kV to LBB_STH TR31 (526264) 13.2 kV Three Winding #2 b.21. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_STH 6 (526269) 230.0 kV to LBB_STH TR11 (526265) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on NEWHART 6230.00 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 b.2. SWISHER_TR11 (525211) 13.2 kV to SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. TUCO_INT 6 (525830) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.2. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.3. TUCO_INT 6 (525830) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on ELK_CT1 345.00 (525850) 345 kV Bus a. Apply Fault at the ELK_CT1 345.00 (525850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.4. ELK_CT1 (525850) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002,527003) and Tolk (525561, 525562) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.6. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.7. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_345 (526936) 345.0 kV to GEN-2019-011 (763516) 345.0 kV Transmission Circuit #1 b.6. YOAKUM_345 (526936) 345.0 kV to GEN-2021-090 (766120) 345.0 kV Transmission Circuit #1 b.7. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), Tolk (525561, 525562), ELK (525844, 525845) and Hobbs units (525903, 525903), along with reactive power oscillations in the surrounding area. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), Tolk (525561) and Hobbs units (525903, 525903), along with frequency and reactive power oscillations in the surrounding area. While active oscillations were also present in the base case, no frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Unstable rotor angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 26 additional units in Group05. The same rotor angle instability was also present in the base case. Neither reducing the Gen-2022-147 active power output to 75%, 50%, 25%, or 0% nor reducing the fault-clearing time to as low as 0.05 cycles resolved the instability. Gen-2022-147 : PTDF=0.3033 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line | Limit GEN-2022-147 to 50% generation.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003) and Elk units (525845). These oscillations were also present in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), Tolk (525561, 525562) and Hobbs units (525903, 525903), along with frequency and reactive power oscillations in the surrounding area. While active power oscillations were also present in the base case, no reactive power and frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply Fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.2. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.2. ROOSEVELT 6 (524909) 230.0 kV to OASIS 6 (524875) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV to SWISHER_TR11 (525211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply Fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.2. HALE_CNTY 3 (525454) 115.0 kV to KRESS_INT 3 (525192) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLANT_X 6 (525481) 230.0 kV to SUNDOWN 6 (526435) 230.0 kV Transmission Circuit #1 b.2. PLANT_X 6 (525481) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on TOLK 6230.00 (525531) 230 kV Bus a. Apply Fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 6 (525531) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 b.2. TOLK 6 (525531) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply Fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.2. FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV to FLOYD_TR1 1 (525777) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 b.2. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.2. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLISLE 6 (526161) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.2. CARLISLE 6 (526161) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply Fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 b.2. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply Fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV to LBB_EST TR11 (526294) 13.2 kV Three Winding #1 b.2. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on JONES 6230.00 (526337) 230 kV Bus a. Apply Fault at the JONES 6230.00 (526337) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES 6 (526337) 230.0 kV to LUBBCK_STH 6 (526269) 230.0 kV Transmission Circuit #1 b.2. JONES 6 (526337) 230.0 kV to LUBBCK_STH 6 (526269) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (762216) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (762216) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Unstable rotor angle deviations were observed at Gen-2022-147 (769922), ELK (525844, 525845), Hobbs (527901, 527902, 527903), and 26 additional units in Group05. No such rotor angle instability was observed in the base case. At 50% Pgen, no rotor-angle instability was observed; however, oscillatory behavior persisted in the output power of the Gains units (527001, 527002, 527003) and Tolk units (525561, 525562). Gen-2022-147 : PTDF=0.3033 | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line | Limit GEN-2022-147 to 50% generation.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GEN-2018-015345.00 (762460) 345 kV Bus a. Apply Fault at the GEN-2018-015345.00 (762460) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-015 (762460) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 b.2. GEN-2018-015 (762460) 345.0 kV to G18-015-XFM1 (762461) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GEN-2020-067345.00 (764935) 345 kV Bus a. Apply Fault at the GEN-2020-067345.00 (764935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-067 (764935) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-067 (764935) 345.0 kV to G20-067-XFM2 (764941) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on G20-067-TAP 345.00 (764945) 345 kV Bus a. Apply Fault at the G20-067-TAP 345.00 (764945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-067-TAP (764945) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. G20-067-TAP (764945) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on G20-068-SS1 345.00 (764948) 345 kV Bus a. Apply Fault at the G20-068-SS1 345.00 (764948) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-068-SS1 (764948) 345.0 kV to GEN-2020-068 (764950) 345.0 kV Transmission Circuit #1 b.2. G20-068-SS1 (764948) 345.0 kV to G20-068-XFM1 (764953) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on G20-068-SS2 345.00 (764949) 345 kV Bus a. Apply Fault at the G20-068-SS2 345.00 (764949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-068-SS2 (764949) 345.0 kV to GEN-2020-068 (764950) 345.0 kV Transmission Circuit #1 b.2. G20-068-SS2 (764949) 345.0 kV to G20-068-XFM2 (764956) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply Fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), MUSTANG (527162, 527161) and Hobbs units (527902,527903), along with frequency and reactive power oscillations in the surrounding area. While voltage, active and reactive power oscillations were also present in the base case, no frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 6 (525531) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 3 (525828) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES 6 (526337) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-015 (762463) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), Tolk (525561) and Hobbs units (525903, 525903), along with reactive power oscillations in the surrounding area. While active power oscillations were also present in the base case, no reactive power oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BECKHAM7 (516059) 345 kV Bus a. Apply Fault at the BECKHAM7 (516059) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), Tolk (525561) and Hobbs units (525903, 525903), along with frequency and reactive power oscillations in the surrounding area. While active power oscillations were also present in the base case, no reactive power and frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on POTTER_CO 7 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POTTER_CO 7 (523961) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_OKGE_FAULT_001 | Single Phase Fault with Stuck Breaker on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003) and Hobbs units (525903, 525903), along with frequency and reactive power oscillations in the surrounding area. While active power oscillations were also present in the base case, no reactive power and frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 b.3. GRAPEVN_TR11 (523769) 13.2 kV to GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on STLN-DEMARC6230.00 (523779) 230 kV Bus a. Apply Fault at the STLN-DEMARC6230.00 (523779) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEETWT6 (511541) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 b.3. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on ELK_CT1 345.00 (525850) 345 kV Bus a. Apply Fault at the ELK_CT1 345.00 (525850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.4. ELK_CT1 (525850) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002,527003) and Tolk (525561, 525562) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 b.5. CARPENTER 7 (523823) 345.0 kV to GEN-2021-021 (765490) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply Fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.3. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.4. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.5. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 b.6. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.7. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.8. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.9. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.10. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.11. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.12. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.13. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.14. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BECKHAM7 (516059) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.3. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Two Winding #2 b.4. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 b.6. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.7. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), ELK (525845, 525844) and Tolk (525561, 525562), along with reactive power oscillations in the surrounding area. This issue was observed in base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), Hobbs (527901, 527902, 527903) and Tolk (525561, 525562), along with frequency and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), Hobbs (527901, 527902, 527903) and Tolk (525561, 525562), along with frequency and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to GRAPEVINE 3 (523770) 115.0 kV to GRAPEVN_TR11 (523769) 13.2 kV Three Winding #1 b.2. GRAPEVINE 6 (523771) 230.0 kV to WHEELER 6 (523777) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on WHEELER 6230.00 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6230.00 (523777) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELER 6 (523777) 230.0 kV to STLN-DEMARC6 (523779) 230.0 kV Transmission Circuit #1 b.2. WHEELER 6 (523777) 230.0 kV to WHEELER 3 (523776) 115.0 kV to WHEELER_TR11 (523774) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002,527003) units. The oscillations meet the Rotor Angle Damping Requirements of SPP (SPPR1=0.73). | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_001 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345 kV Bus a. Apply Fault at the CROSSROADS (527656) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.2. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. RSVLT_CC_E 7 (527655) 345.0 kV to remove bus # b.4. MILO_WIND 1 (527653) 0.7 kV to remove bus # b.5. RSVLT_GEN1 1 (527651) 0.7 kV to remove bus # b.6. RSVLT_GEN2 1 (527652) 0.7 kV to remove bus # b.7. RSVLT_CC_W 7 (527654) 345.0 kV to remove bus # b.8. SAGSFT3_2.21 (527605) 0.7 kV to Generator #1 b.9. SAGSFT4_2.21 (527607) 0.7 kV to Generator #1 b.10. SAGSFT1_2.21 (527614) 0.7 kV to Generator #1 b.11. SAGSFT1_2.01 (527615) 0.7 kV to Generator #1 b.12. SAGSFT2_2.21 (527617) 0.7 kV to Generator #1 b.13. SAGSFT2_2.01 (527618) 0.7 kV to Generator #1 b.14. SAGA_NDCOL 7 (527598) 345.0 kV to remove bus # b.15. SAGA_SDCOL 7 (527599) 345.0 kV to remove bus # b.16. SAGA_SMEAS 7 (527600) 345.0 kV to remove bus # b.17. SAGA_NCOL 7 (527601) 345.0 kV to remove bus # b.18. SAGANCOL1 1 (527602) 34.5 kV to remove bus # b.19. SAGANCOL2 1 (527603) 34.5 kV to remove bus # b.20. GRDXFR3 1 (527604) 0.5 kV to remove bus # b.21. SAGSFT3_2.21 (527605) 0.7 kV to remove bus # b.22. GRDXFR4 1 (527606) 0.5 kV to remove bus # b.23. SAGSFT4_2.21 (527607) 0.7 kV to remove bus # b.24. SUB BUS #3 1 (527608) 34.5 kV to remove bus # b.25. SUB BUS #4 1 (527609) 34.5 kV to remove bus # b.26. SAGA_SCOL 7 (527610) 345.0 kV to remove bus # b.27. SAGASCOL1 1 (527611) 34.5 kV to remove bus # b.28. SAGASCOL2 1 (527612) 34.5 kV to remove bus # b.29. GRDXFR1 1 (527613) 0.5 kV to remove bus # b.30. SAGSFT1_2.21 (527614) 0.7 kV to remove bus # b.31. SAGSFT1_2.01 (527615) 0.7 kV to remove bus # b.32. GRDXFR2 1 (527616) 0.5 kV to remove bus # b.33. SAGSFT2_2.21 (527617) 0.7 kV to remove bus # b.34. SAGSFT2_2.01 (527618) 0.7 kV to remove bus # b.35. SAGA_NCLTR31 (527621) 13.8 kV to remove bus # b.36. SAGA_NCLTR41 (527622) 13.8 kV to remove bus # b.37. SAGA_SCLTR11 (527623) 13.8 kV to remove bus # b.38. SAGA_SCLTR21 (527624) 13.8 kV to remove bus # b.39. SUB BUS #1 (527628) 34.5 kV to remove bus # b.40. SUB BUS #2 (527629) 34.5 kV to remove bus # b.41. CROSSROADS 7 (527656) 345.0 kV to remove bus # b.42. RSVLT_WIND11 (527658) 34.5 kV to remove bus # b.43. RSVLT_WIND21 (527659) 34.5 kV to remove bus # b.44. RSVLT_COL1 1 (527660) 34.5 kV to remove bus # b.45. RSVLT_COL2 1 (527661) 34.5 kV to remove bus # b.46. RSVLT_TR1 1 (527662) 13.2 kV to remove bus # b.47. RSVLT_TR2 1 (527663) 13.2 kV to remove bus # b.48. RSVLT_COL1 7 (527666) 345.0 kV to remove bus # b.49. RSVLT_COL2 7 (527667) 345.0 kV to remove bus # b.50. MILO_CB (577120) 34.5 kV to remove bus # b.51. MILO_WND (577121) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips G18-015 (762463) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_002 | Single Phase Fault with Stuck Breaker on CROSSROADS (527656) 345 kV Bus a. Apply Fault at the CROSSROADS (527656) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CROSSROADS 7 (527656) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.2. CROSSROADS 7 (527656) 345.0 kV to SAGA_SCOL 7 (527610) 345.0 kV Transmission Circuit #1 b.3. SAGSFT3_2.21 (527605) 0.7 kV to remove bus # b.4. GRDXFR4 1 (527606) 0.5 kV to remove bus # b.5. SAGSFT4_2.21 (527607) 0.7 kV to remove bus # b.6. SUB BUS #3 1 (527608) 34.5 kV to remove bus # b.7. SUB BUS #4 1 (527609) 34.5 kV to remove bus # b.8. GRDXFR1 1 (527613) 0.5 kV to remove bus # b.9. SAGSFT1_2.21 (527614) 0.7 kV to remove bus # b.10. SAGSFT1_2.01 (527615) 0.7 kV to remove bus # b.11. GRDXFR2 1 (527616) 0.5 kV to remove bus # b.12. SAGSFT2_2.21 (527617) 0.7 kV to remove bus # b.13. SAGSFT2_2.01 (527618) 0.7 kV to remove bus # b.14. SAGA_NDCOL 7 (527598) 345.0 kV to remove bus # b.15. SAGA_SDCOL 7 (527599) 345.0 kV to remove bus # b.16. SAGA_SMEAS 7 (527600) 345.0 kV to remove bus # b.17. SAGA_NCOL 7 (527601) 345.0 kV to remove bus # b.18. SAGANCOL1 1 (527602) 34.5 kV to remove bus # b.19. SAGANCOL2 1 (527603) 34.5 kV to remove bus # b.20. GRDXFR3 1 (527604) 0.5 kV to remove bus # b.21. SAGA_SCOL 7 (527610) 345.0 kV to remove bus # b.22. SAGASCOL1 1 (527611) 34.5 kV to remove bus # b.23. SAGASCOL2 1 (527612) 34.5 kV to remove bus # b.24. SAGA_NCLTR31 (527621) 13.8 kV to remove bus # b.25. SAGA_NCLTR41 (527622) 13.8 kV to remove bus # b.26. SAGA_SCLTR11 (527623) 13.8 kV to remove bus # b.27. SAGA_SCLTR21 (527624) 13.8 kV to remove bus # b.28. SUB BUS #1 (527628) 34.5 kV to remove bus # b.29. SUB BUS #2 (527629) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_003 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY (527802) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 b.4. EDDY_TR 1 (527796) 13.2 kV to remove bus # b.5. EDDY_CNTY 7 (527802) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002, 527003) and Tolk_2 (525562) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_004 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY (527802) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to EDDY_NORTH 6 (527799) 230.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.4. EDDY_TR 1 (527796) 13.2 kV to remove bus # b.5. EDDY_CNTY 7 (527802) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002, 527003) and Tolk_2 (525562) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_005 | Single Phase Fault with Stuck Breaker on EDDY_CNTY (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY (527802) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. EDDY_NORTH 6 (527799) 230.0 kV to EDDY_CNTY 7 (527802) 345.0 kV to EDDY_TR 1 (527796) 13.2 kV Three Winding #1 b.2. EDDY_CNTY 7 (527802) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.5. EDDY_TR 1 (527796) 13.2 kV to remove bus # b.6. EDDY_CNTY 7 (527802) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002, 527003) and Tolk_2 (525562) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_006 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #2 b.2. NOVUS1 7 (523112) 345.0 kV to remove bus # b.3. NOVUS1 3 (523111) 115.0 kV to remove bus # b.4. NOVUS1 1 (523109) 34.5 kV to remove bus # b.5. NOVUS_WND 1 (523107) 4.2 kV to remove bus # b.6. NOVUS1_TR1 1 (523110) 13.8 kV to remove bus # b.7. NOVUS_WND 1 (523107) 4.2 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_007 | Single Phase Fault with Stuck Breaker on HOBBS_INT (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT (527896) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_INT 7 (527896) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.3. HOBBS_TR3 1 (527895) 13.2 kV to remove bus # b.4. HOBBS_INT 7 (527896) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_008 | Single Phase Fault with Stuck Breaker on POTTERCO (523961) 345 kV Bus a. Apply Fault at the POTTERCO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.4. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.5. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.6. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.7. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.8. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.9. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.10. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_009 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_010 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.5. YOAKUM_TR1 (526937) 13.2 kV to remove bus # b.6. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_011 | Single Phase Fault with Stuck Breaker on YOAKUM (526936) 345 kV Bus a. Apply Fault at the YOAKUM (526936) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to G20-067-TAP (764945) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to remove bus # b.5. YOAKUM_345 (526936) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_012 | Single Phase Fault with Stuck Breaker on TUCO (525832) 345 kV Bus a. Apply Fault at the TUCO (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), Tolk (525561, 525562) and Hobbs units (525903, 525903), along with frequency and reactive power oscillations in the surrounding area. While active and reactive power oscillations were also present in the base case, no frequency oscillations were observed in the base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_013 | Single Phase Fault with Stuck Breaker on POTTERCO (523959) 230 kV Bus a. Apply Fault at the POTTERCO (523959) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BUSHLAND 6 (524267) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.2. ROLLHILLS 6 (524010) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_014 | Single Phase Fault with Stuck Breaker on YOAKUM (526935) 230 kV Bus a. Apply Fault at the YOAKUM (526935) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM 3 (526934) 115.0 kV to YOAKUM_TR1 1 (526931) 13.2 kV Three Winding #1 b.2. NEEDMORE 6 (525586) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_015 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory behavior was observed in the active power outputs of the GAINES units (527001, 527002, 527003), Tolk (525561, 525562) and Hobbs units (525903, 525903). The issue was observed in base case. CQ request did not meet the 3% criteria. | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) Phantom to Crossroads to Potter 765 kV New Line
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_016 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to DEMPSE34.5_4 (511584) 34.5 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillatory response observed in the active power outputs of GAINES (527001, 527002) units. | Applying operational steady-state measures (existing capacitors, tap settings, and generator setpoints) resolves the issue.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_017 | Single Phase Fault with Stuck Breaker on TUCO_INT (525832) 345 kV Bus a. Apply Fault at the TUCO_INT (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 b.2. TUCO_INT 7 (525832) 345.0 kV to DEMPSE34.5_4 (511584) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_018 | Single Phase Fault with Stuck Breaker on HITCHLAND (523097) 345 kV Bus a. Apply Fault at the HITCHLAND (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_019 | Single Phase Fault with Stuck Breaker on POTTER_CO (523961) 345 kV Bus a. Apply Fault at the POTTER_CO (523961) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. POTTER_CO 6 (523959) 230.0 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 b.3. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. POTTER_TR 1 (523957) 13.2 kV to remove bus # b.5. POTTER_CO 7 (523961) 345.0 kV to remove bus # b.6. SPNSPUR_WND7 (524296) 345.0 kV to remove bus # b.7. SPNSPUR_COL7 (524299) 345.0 kV to remove bus # b.8. SPNSPUR_COL1 (524298) 34.5 kV to remove bus # b.9. SPNSPUR_WND1 (524294) 34.5 kV to remove bus # b.10. SPNSPUR_GEN1 (524295) 0.7 kV to remove bus # b.11. SPNSPUR_TR11 (524297) 13.2 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_020 | Single Phase Fault with Stuck Breaker on SWISHER (525213) 230 kV Bus a. Apply Fault at the SWISHER (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to Switched Shunt Device # b.2. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_021 | Single Phase Fault with Stuck Breaker on TUCO_INT (525830) 230 kV Bus a. Apply Fault at the TUCO_INT (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to Switched Shunt Device # b.2. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_022 | Single Phase Fault with Stuck Breaker on BUSHLAND (524267) 230 kV Bus a. Apply Fault at the BUSHLAND (524267) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BUSHLAND 6 (524267) 230.0 kV to WILDOR2_JUS6 (524290) 230.0 kV Transmission Circuit #1 b.2. BUSHLAND 6 (524267) 230.0 kV to Switched Shunt Device # b.3. BUSHLAND 6 (524267) 230.0 kV to BUSHLAND 3 (524266) 115.0 kV to BSHLND_TR1 1 (524263) 13.2 kV Three Winding #1 b.4. WILDORA_GEN1 (524285) 0.7 kV to remove bus # b.5. GS-PHWD_GEN1 (524287) 0.7 kV to remove bus # b.6. BUSHLAND 6 (524267) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.7. BUSHLAND 6 (524267) 230.0 kV to DEAFSMITH 6 (524623) 230.0 kV Transmission Circuit #1 b.8. WILDOR_WND 1 (524275) 34.5 kV to remove bus # b.9. WILDOR_WND 6 (524276) 230.0 kV to remove bus # b.10. GS-PHWDRNCH1 (524289) 34.5 kV to remove bus # b.11. WILDOR2_JUS6 (524290) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_023 | Single Phase Fault with Stuck Breaker on HARRINGTON-G3 (523979) 230 kV Bus a. Apply Fault at the HARRINGTON-G3 (523979) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARRNG_EST 6 (523979) 230.0 kV to PRINGLE 6 (523267) 230.0 kV Transmission Circuit #1 b.2. HARRNG_EST 6 (523979) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.3. HARRNG_EST 6 (523979) 230.0 kV to remove bus # b.4. HARRNGTON3 1 (523973) 24.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_024 | Single Phase Fault with Stuck Breaker on JONES-G1 (526337) 230 kV Bus a. Apply Fault at the JONES-G1 (526337) 230 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. JONES_1 1 (526331) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_025 | Single Phase Fault with Stuck Breaker on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. PLANT_X 6 (525481) 230.0 kV to remove bus #1 b.2. PLANT_X4 1 (525494) 20.0 kV to Generator #1 b.3. PLANTX_TR1 1 (525479) 13.2 kV to remove bus # b.4. PLANT_X4 1 (525494) 20.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_026 | Single Phase Fault with Stuck Breaker on GRASSLAND 6 (526677) 230 kV Bus a. Apply Fault at the GRASSLAND 6 (526677) 230 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. GRASSLAND 6 (526677) 230.0 kV to remove bus #1 b.2. CIRRUS_WND 1 (526678) 0.7 kV to Generator #1 b.3. GRASLND_TR11 (526674) 13.2 kV to remove bus # b.4. CIRRUS_WND 1 (526678) 0.7 kV to remove bus # b.5. CIRRUS_WND 6 (526679) 230.0 kV to remove bus # b.6. CIRRUS_WND (599125) 34.5 kV to remove bus # b.7. CIRRUS_CB (599126) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_027 | Single Phase Fault with Stuck Breaker on BUSHLAND (524267) 230 kV Bus a. Apply Fault at the BUSHLAND (524267) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BSHLND_TR1 1 (524263) 13.2 kV to remove bus # b.2. BUSHLAND 6 (524267) 230.0 kV to DEAFSMITH 6 (524623) 230.0 kV Transmission Circuit #1 b.3. BUSHLAND 6 (524267) 230.0 kV to WILDOR2_JUS6 (524290) 230.0 kV Transmission Circuit #1 b.4. WILDORA_GEN1 (524285) 0.7 kV to Generator #1 b.5. GS-PHWD_GEN1 (524287) 0.7 kV to Generator #1 b.6. BUSHLAND 6 (524267) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.7. BUSHLAND 6 (524267) 230.0 kV to remove bus # b.8. WILDOR_WND 1 (524275) 34.5 kV to remove bus # b.9. WILDOR_WND 6 (524276) 230.0 kV to remove bus # b.10. WILDORA_GEN1 (524285) 0.7 kV to remove bus # b.11. GS-PHWD_GEN1 (524287) 0.7 kV to remove bus # b.12. GS-PHWDRNCH1 (524289) 34.5 kV to remove bus # b.13. WILDOR2_JUS6 (524290) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_028 | Single Phase Fault with Stuck Breaker on BUSHLAND (524267) 230 kV Bus a. Apply Fault at the BUSHLAND (524267) 230 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BSHLND_TR1 1 (524263) 13.2 kV to remove bus # b.2. BUSHLAND 6 (524267) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 b.3. BUSHLAND 6 (524267) 230.0 kV to WILDOR2_JUS6 (524290) 230.0 kV Transmission Circuit #1 b.4. WILDORA_GEN1 (524285) 0.7 kV to Generator #1 b.5. GS-PHWD_GEN1 (524287) 0.7 kV to Generator #1 b.6. BUSHLAND 6 (524267) 230.0 kV to DEAFSMITH 6 (524623) 230.0 kV Transmission Circuit #1 b.7. BUSHLAND 6 (524267) 230.0 kV to remove bus # b.8. WILDOR_WND 1 (524275) 34.5 kV to remove bus # b.9. WILDOR_WND 6 (524276) 230.0 kV to remove bus # b.10. WILDORA_GEN1 (524285) 0.7 kV to remove bus # b.11. GS-PHWD_GEN1 (524287) 0.7 kV to remove bus # b.12. GS-PHWDRNCH1 (524289) 34.5 kV to remove bus # b.13. WILDOR2_JUS6 (524290) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Protection relay trips LANOGSU1 (523812) unit. | Protection disabled with no impact to stability.
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_029 | Single Phase Fault with Stuck Breaker on GRASSLAND (526677) 230 kV Bus a. Apply Fault at the GRASSLAND (526677) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRASSLAND 6 (526677) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. GRASSLAND 3 (526676) 115.0 kV to LYNN_CNTY 3 (526656) 115.0 kV Transmission Circuit #1 b.3. CIRRUS_WND 1 (526678) 0.7 kV to Generator #1 b.4. LG-TWO_DRAW2 (526513) 69.0 kV to remove bus # b.5. SP-SLATON 2 (526569) 69.0 kV to remove bus # b.6. SOUTHLAND 2 (526576) 69.0 kV to remove bus # b.7. LG-HAKBERRY2 (526583) 69.0 kV to remove bus # b.8. DIEKEMPER 2 (526592) 69.0 kV to remove bus # b.9. GARZA 2 (526622) 69.0 kV to remove bus # b.10. GRASLND_TR11 (526674) 13.2 kV to remove bus # b.11. GRASSLAND 3 (526676) 115.0 kV to remove bus # b.12. GRASSLAND 6 (526677) 230.0 kV to remove bus # b.13. CIRRUS_WND 1 (526678) 0.7 kV to remove bus # b.14. CIRRUS_WND 6 (526679) 230.0 kV to remove bus # b.15. GRAHAM_TR2 1 (526691) 13.2 kV to remove bus # b.16. GRAHAM_TR1 1 (526692) 13.2 kV to remove bus # b.17. GRAHAM 2 (526693) 69.0 kV to remove bus # b.18. GRAHAM 3 (526694) 115.0 kV to remove bus # b.19. JST_CORNER 2 (526799) 69.0 kV to remove bus # b.20. BG-FLUVANNA2 (526814) 69.0 kV to remove bus # b.21. BG-JSTBG_TP2 (526821) 69.0 kV to remove bus # b.22. CIRRUS_WND (599125) 34.5 kV to remove bus # b.23. CIRRUS_CB (599126) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_030 | Single Phase Fault with Stuck Breaker on LAMB (525636) 115 kV Bus a. Apply Fault at the LAMB (525636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 b.2. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 b.3. LAMB_CNTY 6 (525637) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.4. SUDANRURAL 2 (525592) 69.0 kV to remove bus # b.5. LC-SANDHLL+2 (525599) 69.0 kV to remove bus # b.6. AMHERST 2 (525606) 69.0 kV to remove bus # b.7. W_LITTLFLD 2 (525613) 69.0 kV to remove bus # b.8. LTFLD_S&CTY2 (525620) 69.0 kV to remove bus # b.9. LAMB_TR1 1 (525631) 13.2 kV to remove bus # b.10. LAMB_TR2 1 (525632) 13.2 kV to remove bus # b.11. LAMB_TR3 1 (525633) 13.2 kV to remove bus # b.12. LAMB_CNTY 2 (525635) 69.0 kV to remove bus # b.13. LAMB_CNTY 3 (525636) 115.0 kV to remove bus # b.14. LAMB_CNTY 6 (525637) 230.0 kV to remove bus # b.15. LC-LTTLFLD+2 (525650) 69.0 kV to remove bus # b.16. W_ANTON_TP 2 (525657) 69.0 kV to remove bus # b.17. LC-SPD&HART2 (525664) 69.0 kV to remove bus # b.18. BAINER 2 (525671) 69.0 kV to remove bus # b.19. W_ANTON 2 (525678) 69.0 kV to remove bus # b.20. LC-LUMSCHAP2 (525687) 69.0 kV to remove bus # b.21. HOBGOOD 2 (525694) 69.0 kV to remove bus # b.22. PUMP/YH_TP 2 (525697) 69.0 kV to remove bus # b.23. PHLLPPMP#2 2 (525701) 69.0 kV to remove bus # b.24. YELLOWHOUSE2 (525703) 69.0 kV to remove bus # b.25. MIDAMERI#2 2 (525708) 69.0 kV to remove bus # b.26. WHITHARRAL 2 (525717) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_031 | Single Phase Fault with Stuck Breaker on LAMB (525636) 115 kV Bus a. Apply Fault at the LAMB (525636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 b.2. LAMB_TR3 1 (525633) 13.2 kV to remove bus # b.3. LAMB_CNTY 3 (525636) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 b.4. SUDANRURAL 2 (525592) 69.0 kV to remove bus # b.5. LC-SANDHLL+2 (525599) 69.0 kV to remove bus # b.6. AMHERST 2 (525606) 69.0 kV to remove bus # b.7. W_LITTLFLD 2 (525613) 69.0 kV to remove bus # b.8. LTFLD_S&CTY2 (525620) 69.0 kV to remove bus # b.9. LAMB_TR1 1 (525631) 13.2 kV to remove bus # b.10. LAMB_TR2 1 (525632) 13.2 kV to remove bus # b.11. LAMB_CNTY 2 (525635) 69.0 kV to remove bus # b.12. LAMB_CNTY 3 (525636) 115.0 kV to remove bus # b.13. LC-LTTLFLD+2 (525650) 69.0 kV to remove bus # b.14. W_ANTON_TP 2 (525657) 69.0 kV to remove bus # b.15. LC-SPD&HART2 (525664) 69.0 kV to remove bus # b.16. BAINER 2 (525671) 69.0 kV to remove bus # b.17. W_ANTON 2 (525678) 69.0 kV to remove bus # b.18. LC-LUMSCHAP2 (525687) 69.0 kV to remove bus # b.19. HOBGOOD 2 (525694) 69.0 kV to remove bus # b.20. PUMP/YH_TP 2 (525697) 69.0 kV to remove bus # b.21. PHLLPPMP#2 2 (525701) 69.0 kV to remove bus # b.22. YELLOWHOUSE2 (525703) 69.0 kV to remove bus # b.23. MIDAMERI#2 2 (525708) 69.0 kV to remove bus # b.24. WHITHARRAL 2 (525717) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_032 | Single Phase Fault with Stuck Breaker on LUBBOCK_STH (526269) 230 kV Bus a. Apply Fault at the LUBBOCK_STH (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 b.2. LUBBCK_STH 3 (526268) 115.0 kV to ALLEN 3 (526213) 115.0 kV Transmission Circuit #1 b.3. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.4. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.5. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 b.6. LBB_STH TR31 (526264) 13.2 kV to remove bus # b.7. WOODROW 3 (526602) 115.0 kV to LYNN_CNTY 3 (526656) 115.0 kV Transmission Circuit #1 b.8. IVORY 2 (526205) 69.0 kV to remove bus # b.9. BATTON_S 2 (526228) 69.0 kV to remove bus # b.10. ACCO 2 (526249) 69.0 kV to remove bus # b.11. IVORY_TP 2 (526256) 69.0 kV to remove bus # b.12. LBB_STH TR11 (526265) 13.2 kV to remove bus # b.13. LBB_STH TR21 (526266) 13.2 kV to remove bus # b.14. LUBBCK_STH 2 (526267) 69.0 kV to remove bus # b.15. LUBBCK_STH 3 (526268) 115.0 kV to remove bus # b.16. LUBBCK_STH 6 (526269) 230.0 kV to remove bus # b.17. WOODROW 3 (526602) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_033 | Single Phase Fault with Stuck Breaker on OASIS (524874) 115 kV Bus a. Apply Fault at the OASIS (524874) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OASIS 3 (524874) 115.0 kV to PORTALES 3 (524924) 115.0 kV Transmission Circuit #1 b.2. NORRIS_TP 3 (524764) 115.0 kV to CURRY 3 (524822) 115.0 kV Transmission Circuit #1 b.3. W_CLOVIS 3 (524784) 115.0 kV to FE-CLVS_INT3 (524808) 115.0 kV Transmission Circuit #1 b.4. OASIS 6 (524875) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 b.5. OASIS 6 (524875) 230.0 kV to OASIS 3 (524874) 115.0 kV to OASIS_TR1 1 (524872) 13.2 kV Three Winding #1 b.6. NORRIS_TP 3 (524764) 115.0 kV to remove bus # b.7. W_CLOVIS 3 (524784) 115.0 kV to remove bus # b.8. CANNON_TP 3 (524790) 115.0 kV to remove bus # b.9. CANNONAFB 3 (524794) 115.0 kV to remove bus # b.10. PERIMETER 3 (524797) 115.0 kV to remove bus # b.11. NORRIS 3 (524801) 115.0 kV to remove bus # b.12. FE-CHZPLT 3 (524863) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_034 | Single Phase Fault with Stuck Breaker on CARLISLE (526160) 115 kV Bus a. Apply Fault at the CARLISLE (526160) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SP-ERSKINE 3 (526109) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.2. YUMA_INT 3 (526475) 115.0 kV to SP-WOLF_TP 3 (526481) 115.0 kV Transmission Circuit #1 b.3. CRLSLE_TR1 1 (526157) 13.2 kV to remove bus # b.4. CARLISLE 3 (526160) 115.0 kV to MURPHY 3 (526192) 115.0 kV Transmission Circuit #1 b.5. SP-ERSKINE 3 (526109) 115.0 kV to remove bus # b.6. SP-CARLISLE2 (526130) 69.0 kV to remove bus # b.7. CRLSLE_TR2 1 (526158) 13.2 kV to remove bus # b.8. CARLISLE 2 (526159) 69.0 kV to remove bus # b.9. CARLISLE 3 (526160) 115.0 kV to remove bus # b.10. LP-DOUD_TP 3 (526162) 115.0 kV to remove bus # b.11. LP-DOUD 3 (526176) 115.0 kV to remove bus # b.12. SW_6878 2 (526184) 69.0 kV to remove bus # b.13. BATTON_N 2 (526221) 69.0 kV to remove bus # b.14. SP-WOLF_TP 3 (526481) 115.0 kV to remove bus # b.15. SP-WOLFORTH3 (526483) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_035 | Single Phase Fault with Stuck Breaker on WOLFFORTH (526524) 115 kV Bus a. Apply Fault at the WOLFFORTH (526524) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LP-DOUD_TP 3 (526162) 115.0 kV to CARLISLE 3 (526160) 115.0 kV Transmission Circuit #1 b.2. WOLFRTH_TR11 (526522) 13.2 kV to remove bus # b.3. WOLFFORTH 3 (526524) 115.0 kV to TERRY_CNTY 3 (526736) 115.0 kV Transmission Circuit #1 b.4. LP-DOUD_TP 3 (526162) 115.0 kV to remove bus # b.5. LP-DOUD 3 (526176) 115.0 kV to remove bus # b.6. YUMA_INT 3 (526475) 115.0 kV to remove bus # b.7. SP-WOLF_TP 3 (526481) 115.0 kV to remove bus # b.8. SP-WOLFORTH3 (526483) 115.0 kV to remove bus # b.9. WOLFFORTH 3 (526524) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 SOUTHWEST | GEN-2022-147 LOSIS | 29W | Transfer | GROUP5_P4_SPS_FAULT_036 | Single Phase Fault with Stuck Breaker on LAMB (525636) 115 kV Bus a. Apply Fault at the LAMB (525636) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 b.2. LAMB_CNTY 3 (525636) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 b.3. LAMB_CNTY 6 (525637) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.4. SUDANRURAL 2 (525592) 69.0 kV to remove bus # b.5. LC-SANDHLL+2 (525599) 69.0 kV to remove bus # b.6. AMHERST 2 (525606) 69.0 kV to remove bus # b.7. W_LITTLFLD 2 (525613) 69.0 kV to remove bus # b.8. LTFLD_S&CTY2 (525620) 69.0 kV to remove bus # b.9. LAMB_TR1 1 (525631) 13.2 kV to remove bus # b.10. LAMB_TR2 1 (525632) 13.2 kV to remove bus # b.11. LAMB_TR3 1 (525633) 13.2 kV to remove bus # b.12. LAMB_CNTY 2 (525635) 69.0 kV to remove bus # b.13. LAMB_CNTY 3 (525636) 115.0 kV to remove bus # b.14. LAMB_CNTY 6 (525637) 230.0 kV to remove bus # b.15. LC-LTTLFLD+2 (525650) 69.0 kV to remove bus # b.16. W_ANTON_TP 2 (525657) 69.0 kV to remove bus # b.17. LC-SPD&HART2 (525664) 69.0 kV to remove bus # b.18. BAINER 2 (525671) 69.0 kV to remove bus # b.19. W_ANTON 2 (525678) 69.0 kV to remove bus # b.20. LC-LUMSCHAP2 (525687) 69.0 kV to remove bus # b.21. HOBGOOD 2 (525694) 69.0 kV to remove bus # b.22. PUMP/YH_TP 2 (525697) 69.0 kV to remove bus # b.23. PHLLPPMP#2 2 (525701) 69.0 kV to remove bus # b.24. YELLOWHOUSE2 (525703) 69.0 kV to remove bus # b.25. MIDAMERI#2 2 (525708) 69.0 kV to remove bus # b.26. WHITHARRAL 2 (525717) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2022-147 | 05 SOUTHWEST | 769921 | GEN-2022-147 | 345 | 13.4267 | 14.5968 | 1.1701
GEN-2022-147 | 05 SOUTHWEST | 525832 | TUCO_INT 7 | 345 | 13.5705 | 14.7396 | 1.1691
GEN-2022-147 | 05 SOUTHWEST | 525850 | ELK_CT1 | 345 | 13.4563 | 14.6022 | 1.1459
GEN-2022-147 | 05 SOUTHWEST | 525830 | TUCO_INT 6 | 230 | 23.4398 | 24.3653 | 0.9255
GEN-2022-147 | 05 SOUTHWEST | 525840 | ANTELOPE_1 6 | 230 | 23.236 | 24.1442 | 0.9082
GEN-2022-147 | 05 SOUTHWEST | 762216 | G17-151TAP | 345 | 8.5315 | 8.8619 | 0.3304
GEN-2022-147 | 05 SOUTHWEST | 525828 | TUCO_INT 3 | 115 | 20.7077 | 20.9348 | 0.2271
GEN-2022-147 | 05 SOUTHWEST | 525957 | HALE_WNDCL16 | 230 | 12.4313 | 12.6232 | 0.1919
GEN-2022-147 | 05 SOUTHWEST | 762217 | GEN-2017-151 | 345 | 6.2772 | 6.4457 | 0.1685
GEN-2022-147 | 05 SOUTHWEST | 526337 | JONES 6 | 230 | 18.8095 | 18.9357 | 0.1262
GEN-2022-147 | 05 SOUTHWEST | 764945 | G20-067-TAP | 345 | 8.045 | 8.1589 | 0.1139
GEN-2022-147 | 05 SOUTHWEST | 764950 | GEN-2020-068 | 345 | 8.0038 | 8.1165 | 0.1127
GEN-2022-147 | 05 SOUTHWEST | 526269 | LUBBCK_STH 6 | 230 | 16.6865 | 16.7927 | 0.1062
GEN-2022-147 | 05 SOUTHWEST | 526161 | CARLISLE 6 | 230 | 10.9566 | 11.0469 | 0.0903
GEN-2022-147 | 05 SOUTHWEST | 526525 | WOLFFORTH 6 | 230 | 13.3813 | 13.4664 | 0.0851
GEN-2022-147 | 05 SOUTHWEST | 526268 | LUBBCK_STH 3 | 115 | 19.1625 | 19.2417 | 0.0792
GEN-2022-147 | 05 SOUTHWEST | 764935 | GEN-2020-067 | 345 | 6.7462 | 6.8231 | 0.0769
GEN-2022-147 | 05 SOUTHWEST | 764948 | G20-068-SS1 | 345 | 6.4838 | 6.5576 | 0.0738
GEN-2022-147 | 05 SOUTHWEST | 764949 | G20-068-SS2 | 345 | 6.4838 | 6.5576 | 0.0738
GEN-2022-147 | 05 SOUTHWEST | 525531 | TOLK 6 | 230 | 29.129 | 29.1975 | 0.0685
GEN-2022-147 | 05 SOUTHWEST | 526936 | YOAKUM_345 | 345 | 10.4016 | 10.4614 | 0.0598
GEN-2022-147 | 05 SOUTHWEST | 526298 | LUBBCK_EST 3 | 115 | 15.7228 | 15.7822 | 0.0594
GEN-2022-147 | 05 SOUTHWEST | 766120 | GEN-2021-090 | 345 | 10.3538 | 10.413 | 0.0592
GEN-2022-147 | 05 SOUTHWEST | 526299 | LUBBCK_EST 6 | 230 | 12.5364 | 12.5931 | 0.0567
GEN-2022-147 | 05 SOUTHWEST | 526160 | CARLISLE 3 | 115 | 13.5146 | 13.5697 | 0.0551
GEN-2022-147 | 05 SOUTHWEST | 764875 | GEN-2020-060 | 230 | 12.3404 | 12.3952 | 0.0548
GEN-2022-147 | 05 SOUTHWEST | 526935 | YOAKUM 6 | 230 | 19.7658 | 19.8189 | 0.0531
GEN-2022-147 | 05 SOUTHWEST | 763516 | GEN-2019-011 | 345 | 9.7265 | 9.7788 | 0.0523
GEN-2022-147 | 05 SOUTHWEST | 525481 | PLANT_X 6 | 230 | 23.6054 | 23.6544 | 0.049
GEN-2022-147 | 05 SOUTHWEST | 762467 | G18-015-TAP | 345 | 5.446 | 5.4942 | 0.0482
GEN-2022-147 | 05 SOUTHWEST | 762460 | GEN-2018-015 | 345 | 5.436 | 5.484 | 0.048
GEN-2022-147 | 05 SOUTHWEST | 525213 | SWISHER 6 | 230 | 10.8915 | 10.9352 | 0.0437
GEN-2022-147 | 05 SOUTHWEST | 526109 | SP-ERSKINE 3 | 115 | 11.6026 | 11.6454 | 0.0428
GEN-2022-147 | 05 SOUTHWEST | 526162 | LP-DOUD_TP 3 | 115 | 11.9562 | 11.9966 | 0.0404
GEN-2022-147 | 05 SOUTHWEST | 526481 | SP-WOLF_TP 3 | 115 | 11.4588 | 11.4945 | 0.0357
GEN-2022-147 | 05 SOUTHWEST | 526192 | MURPHY 3 | 115 | 11.0188 | 11.0535 | 0.0347
GEN-2022-147 | 05 SOUTHWEST | 526475 | YUMA_INT 3 | 115 | 11.2841 | 11.3179 | 0.0338
GEN-2022-147 | 05 SOUTHWEST | 526146 | INDIANA 3 | 115 | 9.8224 | 9.8557 | 0.0333
GEN-2022-147 | 05 SOUTHWEST | 526524 | WOLFFORTH 3 | 115 | 11.8701 | 11.902 | 0.0319
GEN-2022-147 | 05 SOUTHWEST | 526076 | STANTON_W 3 | 115 | 9.4196 | 9.4511 | 0.0315
GEN-2022-147 | 05 SOUTHWEST | 526435 | SUNDOWN 6 | 230 | 11.4566 | 11.4875 | 0.0309
GEN-2022-147 | 05 SOUTHWEST | 526213 | ALLEN 3 | 115 | 11.1708 | 11.201 | 0.0302
GEN-2022-147 | 05 SOUTHWEST | 526195 | QUINCY 3 | 115 | 10.3135 | 10.3427 | 0.0292
GEN-2022-147 | 05 SOUTHWEST | 527009 | BRU_SUB 6 | 230 | 15.5299 | 15.5572 | 0.0273
GEN-2022-147 | 05 SOUTHWEST | 527010 | OXYBRU 6 | 230 | 15.3928 | 15.4196 | 0.0268
GEN-2022-147 | 05 SOUTHWEST | 526176 | LP-DOUD 3 | 115 | 9.3363 | 9.361 | 0.0247
GEN-2022-147 | 05 SOUTHWEST | 527011 | XTO_MAHONEY6 | 230 | 15.1446 | 15.169 | 0.0244
GEN-2022-147 | 05 SOUTHWEST | 525461 | NEWHART 6 | 230 | 11.4806 | 11.5047 | 0.0241
GEN-2022-147 | 05 SOUTHWEST | 526934 | YOAKUM 3 | 115 | 20.108 | 20.1314 | 0.0234
GEN-2022-147 | 05 SOUTHWEST | 527149 | MUSTANG 6 | 230 | 16.6552 | 16.6783 | 0.0231
GEN-2022-147 | 05 SOUTHWEST | 527151 | GS-MUSTANG 6 | 230 | 16.6552 | 16.6783 | 0.0231
GEN-2022-147 | 05 SOUTHWEST | 525192 | KRESS_INT 3 | 115 | 12.4904 | 12.5132 | 0.0228
GEN-2022-147 | 05 SOUTHWEST | 763186 | GEN-2018-089 | 230 | 11.16 | 11.1828 | 0.0228
GEN-2022-147 | 05 SOUTHWEST | 526460 | AMOCO_SS 6 | 230 | 10.1254 | 10.1482 | 0.0228
GEN-2022-147 | 05 SOUTHWEST | 525212 | SWISHER 3 | 115 | 12.0541 | 12.0766 | 0.0225
GEN-2022-147 | 05 SOUTHWEST | 525460 | NEWHART 3 | 115 | 15.5585 | 15.5808 | 0.0223
GEN-2022-147 | 05 SOUTHWEST | 526483 | SP-WOLFORTH3 | 115 | 8.9296 | 8.9512 | 0.0216
GEN-2022-147 | 05 SOUTHWEST | 525454 | HALE_CNTY 3 | 115 | 10.5395 | 10.5608 | 0.0213
GEN-2022-147 | 05 SOUTHWEST | 525826 | TUCO_INT 2 | 69 | 8.2851 | 8.3063 | 0.0212
GEN-2022-147 | 05 SOUTHWEST | 526784 | AMOCOWASSON6 | 230 | 15.0462 | 15.0673 | 0.0211
GEN-2022-147 | 05 SOUTHWEST | 511456 | O.K.U.-7 | 345 | 5.9447 | 5.9651 | 0.0204
GEN-2022-147 | 05 SOUTHWEST | 511565 | OKLAUN HVDC7 | 345 | 5.9264 | 5.9467 | 0.0203
GEN-2022-147 | 05 SOUTHWEST | 526602 | WOODROW 3 | 115 | 9.7672 | 9.7871 | 0.0199
GEN-2022-147 | 05 SOUTHWEST | 761355 | GEN-2017-239 | 230 | 13.7011 | 13.7208 | 0.0197
GEN-2022-147 | 05 SOUTHWEST | 526236 | LP-WHEELOCK3 | 115 | 8.98 | 8.9994 | 0.0194
GEN-2022-147 | 05 SOUTHWEST | 527146 | MUSTANG 3 | 115 | 25.0166 | 25.0355 | 0.0189
GEN-2022-147 | 05 SOUTHWEST | 527894 | HOBBS_INT 6 | 230 | 23.6612 | 23.6799 | 0.0187
GEN-2022-147 | 05 SOUTHWEST | 515458 | BORDER 7 | 345 | 4.653 | 4.6703 | 0.0173
GEN-2022-147 | 05 SOUTHWEST | 526196 | SP-MILWAUKEE | 115 | 7.9237 | 7.9409 | 0.0172
GEN-2022-147 | 05 SOUTHWEST | 525549 | TOLK 7 | 345 | 12.3653 | 12.3819 | 0.0166
GEN-2022-147 | 05 SOUTHWEST | 526677 | GRASSLAND 6 | 230 | 6.5678 | 6.583 | 0.0152
GEN-2022-147 | 05 SOUTHWEST | 525480 | PLANT_X 3 | 115 | 15.1929 | 15.2078 | 0.0149
GEN-2022-147 | 05 SOUTHWEST | 527896 | HOBBS_INT 7 | 345 | 9.84 | 9.8549 | 0.0149
GEN-2022-147 | 05 SOUTHWEST | 516059 | BECKHAM7 | 345 | 5.1717 | 5.1865 | 0.0148
GEN-2022-147 | 05 SOUTHWEST | 762132 | GEN-2017-158 | 230 | 13.8361 | 13.8495 | 0.0134
GEN-2022-147 | 05 SOUTHWEST | 525780 | FLOYD_CNTY 3 | 115 | 7.0521 | 7.0652 | 0.0131
GEN-2022-147 | 05 SOUTHWEST | 527891 | HOBBS_INT 3 | 115 | 34.8973 | 34.9094 | 0.0121
GEN-2022-147 | 05 SOUTHWEST | 527867 | CUNNIGHM_S 6 | 230 | 20.2081 | 20.2201 | 0.012
GEN-2022-147 | 05 SOUTHWEST | 527028 | INK_BASIN 6 | 230 | 11.8672 | 11.879 | 0.0118
GEN-2022-147 | 05 SOUTHWEST | 526434 | SUNDOWN 3 | 115 | 11.2756 | 11.287 | 0.0114
GEN-2022-147 | 05 SOUTHWEST | 526736 | TERRY_CNTY 3 | 115 | 11.1956 | 11.2067 | 0.0111
GEN-2022-147 | 05 SOUTHWEST | 515375 | WWRDEHV7 | 345 | 18.2719 | 18.2827 | 0.0108
GEN-2022-147 | 05 SOUTHWEST | 523977 | HARRNG_WST 6 | 230 | 26.9956 | 27.0063 | 0.0107
GEN-2022-147 | 05 SOUTHWEST | 523978 | HARRNG_MID 6 | 230 | 26.9956 | 27.0063 | 0.0107
GEN-2022-147 | 05 SOUTHWEST | 523979 | HARRNG_EST 6 | 230 | 26.9956 | 27.0063 | 0.0107
GEN-2022-147 | 05 SOUTHWEST | 525585 | BLUECLDPOI 6 | 230 | 11.135 | 11.1455 | 0.0105
GEN-2022-147 | 05 SOUTHWEST | 525586 | NEEDMORE 6 | 230 | 11.135 | 11.1455 | 0.0105
GEN-2022-147 | 05 SOUTHWEST | 767221 | GEN-2022-012 | 345 | 18.0423 | 18.0528 | 0.0105
GEN-2022-147 | 05 SOUTHWEST | 767301 | GEN-2022-016 | 345 | 18.0423 | 18.0528 | 0.0105
GEN-2022-147 | 05 SOUTHWEST | 511468 | L.E.S.-7 | 345 | 13.0866 | 13.097 | 0.0104
GEN-2022-147 | 05 SOUTHWEST | 767321 | GEN-2022-017 | 345 | 17.8183 | 17.8286 | 0.0103
GEN-2022-147 | 05 SOUTHWEST | 588760 | GEN-2017-033 | 345 | 4.3281 | 4.3383 | 0.0102
GEN-2022-147 | 05 SOUTHWEST | 524044 | NICHOLS 6 | 230 | 26.1895 | 26.1996 | 0.0101
GEN-2022-147 | 05 SOUTHWEST | 526297 | LUBBCK_EST 2 | 69 | 8.3938 | 8.4039 | 0.0101
GEN-2022-147 | 05 SOUTHWEST | 763318 | GEN-2018-115 | 345 | 12.8479 | 12.8579 | 0.01
GEN-2022-147 | 05 SOUTHWEST | 526198 | SP-UPLAND | 115 | 6.0239 | 6.0339 | 0.01
GEN-2022-147 | 05 SOUTHWEST | 526676 | GRASSLAND 3 | 115 | 7.3689 | 7.3789 | 0.01
GEN-2022-147 | 05 SOUTHWEST | 525584 | BLUECLDCOL 6 | 230 | 10.5496 | 10.5591 | 0.0095
GEN-2022-147 | 05 SOUTHWEST | 526679 | CIRRUS_WND 6 | 230 | 5.152 | 5.1612 | 0.0092
GEN-2022-147 | 05 SOUTHWEST | 525763 | CALLAHAN 3 | 115 | 6.121 | 6.1302 | 0.0092
GEN-2022-147 | 05 SOUTHWEST | 525326 | COX 3 | 115 | 6.6752 | 6.6843 | 0.0091
GEN-2022-147 | 05 SOUTHWEST | 523959 | POTTER_CO 6 | 230 | 21.5838 | 21.5925 | 0.0087
GEN-2022-147 | 05 SOUTHWEST | 763527 | GEN-2019-012 | 345 | 16.2484 | 16.257 | 0.0086
GEN-2022-147 | 05 SOUTHWEST | 511467 | L.E.S.-4 | 138 | 24.8902 | 24.8987 | 0.0085
GEN-2022-147 | 05 SOUTHWEST | 527041 | ARCO_TP 3 | 115 | 14.2718 | 14.28 | 0.0082
GEN-2022-147 | 05 SOUTHWEST | 528353 | MADDOXG23 3 | 115 | 29.2796 | 29.2876 | 0.008
GEN-2022-147 | 05 SOUTHWEST | 764550 | G20-087-TAP | 345 | 12.7786 | 12.7866 | 0.008
GEN-2022-147 | 05 SOUTHWEST | 764555 | GEN-2020-087 | 345 | 12.7702 | 12.7782 | 0.008
GEN-2022-147 | 05 SOUTHWEST | 525803 | BLANCO 3 | 115 | 6.1587 | 6.1664 | 0.0077
GEN-2022-147 | 05 SOUTHWEST | 525801 | LRNZ_MPT 3 | 115 | 6.1578 | 6.1654 | 0.0076
GEN-2022-147 | 05 SOUTHWEST | 526656 | LYNN_CNTY 3 | 115 | 6.3395 | 6.3471 | 0.0076
GEN-2022-147 | 05 SOUTHWEST | 525226 | KRS_RURL_TP3 | 115 | 6.7716 | 6.779 | 0.0074
GEN-2022-147 | 05 SOUTHWEST | 525816 | TUCO_INT2 2 | 69 | 4.8986 | 4.906 | 0.0074
GEN-2022-147 | 05 SOUTHWEST | 527966 | KIOWA 3 | 115 | 17.1534 | 17.1607 | 0.0073
GEN-2022-147 | 05 SOUTHWEST | 524415 | AMA_SOUTH 6 | 230 | 14.0237 | 14.0306 | 0.0069
GEN-2022-147 | 05 SOUTHWEST | 524364 | RANDALL 3 | 115 | 21.703 | 21.7098 | 0.0068
GEN-2022-147 | 05 SOUTHWEST | 525414 | LAMTON 3 | 115 | 7.7384 | 7.7452 | 0.0068
GEN-2022-147 | 05 SOUTHWEST | 524010 | ROLLHILLS 6 | 230 | 20.1731 | 20.1798 | 0.0067
GEN-2022-147 | 05 SOUTHWEST | 525446 | RKYFORD_TP 3 | 115 | 9.3623 | 9.3689 | 0.0066
GEN-2022-147 | 05 SOUTHWEST | 526928 | PLAINS_INT 3 | 115 | 10.8103 | 10.8169 | 0.0066
GEN-2022-147 | 05 SOUTHWEST | 525225 | KRESS_RURAL3 | 115 | 6.2772 | 6.2835 | 0.0063
GEN-2022-147 | 05 SOUTHWEST | 528024 | RR_SVC_HV 3 | 115 | 15.0305 | 15.0367 | 0.0062
GEN-2022-147 | 05 SOUTHWEST | 528025 | RDRUNNER 3 | 115 | 15.0305 | 15.0367 | 0.0062
GEN-2022-147 | 05 SOUTHWEST | 524043 | NICHOLS 3 | 115 | 31.133 | 31.1391 | 0.0061
GEN-2022-147 | 05 SOUTHWEST | 525926 | CROSBY 3 | 115 | 5.4703 | 5.4764 | 0.0061
GEN-2022-147 | 05 SOUTHWEST | 527965 | KIOWA 7 | 345 | 8.0947 | 8.1008 | 0.0061
GEN-2022-147 | 05 SOUTHWEST | 525453 | HALE_CNTY 2 | 69 | 7.2167 | 7.2227 | 0.006
GEN-2022-147 | 05 SOUTHWEST | 527027 | INK_BASIN 3 | 115 | 13.9436 | 13.9496 | 0.006
GEN-2022-147 | 05 SOUTHWEST | 588460 | A16-008SUB | 115 | 13.9436 | 13.9496 | 0.006
GEN-2022-147 | 05 SOUTHWEST | 762866 | GEN-2018-052 | 115 | 14.7747 | 14.7807 | 0.006
GEN-2022-147 | 05 SOUTHWEST | 525124 | HART_INDUST3 | 115 | 7.7851 | 7.7911 | 0.006
GEN-2022-147 | 05 SOUTHWEST | 524365 | RANDALL 6 | 230 | 14.93 | 14.9358 | 0.0058
GEN-2022-147 | 05 SOUTHWEST | 525272 | KISER 3 | 115 | 5.5659 | 5.5717 | 0.0058
GEN-2022-147 | 05 SOUTHWEST | 524909 | ROOSEVELT 6 | 230 | 9.7141 | 9.7198 | 0.0057
GEN-2022-147 | 05 SOUTHWEST | 599955 | PNM-DC6 | 230 | 9.7141 | 9.7198 | 0.0057
GEN-2022-147 | 05 SOUTHWEST | 525779 | FLOYD_CNTY 2 | 69 | 5.8806 | 5.8861 | 0.0055
GEN-2022-147 | 05 SOUTHWEST | 525393 | ROCKYFORD 3 | 115 | 8.4687 | 8.4741 | 0.0054
GEN-2022-147 | 05 SOUTHWEST | 515376 | WWRDEHV4 | 138 | 24.101 | 24.1063 | 0.0053
GEN-2022-147 | 05 SOUTHWEST | 525291 | PLAINVW_TP 2 | 69 | 6.7757 | 6.781 | 0.0053
GEN-2022-147 | 05 SOUTHWEST | 526284 | PLANTERS 2 | 69 | 6.0501 | 6.0554 | 0.0053
GEN-2022-147 | 05 SOUTHWEST | 587990 | GEN-2016-121 | 115 | 13.8401 | 13.8454 | 0.0053
GEN-2022-147 | 05 SOUTHWEST | 765440 | GEN-2021-015 | 345 | 14.5232 | 14.5285 | 0.0053
GEN-2022-147 | 05 SOUTHWEST | 527047 | OXY_WILRD1 3 | 115 | 11.3791 | 11.3843 | 0.0052
GEN-2022-147 | 05 SOUTHWEST | 560071 | G16-003-TAP | 345 | 14.5238 | 14.529 | 0.0052
GEN-2022-147 | 05 SOUTHWEST | 760938 | G17-171-TAP | 345 | 10.4108 | 10.4159 | 0.0051
GEN-2022-147 | 05 SOUTHWEST | 760939 | GEN-2017-171 | 345 | 10.3545 | 10.3596 | 0.0051
GEN-2022-147 | 05 SOUTHWEST | 525179 | TULIA_TP 3 | 115 | 6.7762 | 6.7813 | 0.0051
GEN-2022-147 | 05 SOUTHWEST | 525440 | LC-S_OLTON+3 | 115 | 7.1821 | 7.1872 | 0.0051
GEN-2022-147 | 05 SOUTHWEST | 527276 | SEMINOLE 6 | 230 | 8.2764 | 8.2814 | 0.005
GEN-2022-147 | 05 SOUTHWEST | 515800 | GRACMNT7 | 345 | 16.2771 | 16.2821 | 0.005
GEN-2022-147 | 05 SOUTHWEST | 528230 | AGAVE_RHILL3 | 115 | 13.4119 | 13.4168 | 0.0049
GEN-2022-147 | 05 SOUTHWEST | 526310 | CLUTTER 2 | 69 | 5.6976 | 5.7023 | 0.0047
GEN-2022-147 | 05 SOUTHWEST | 524746 | CASTRO_CNTY3 | 115 | 10.0906 | 10.0952 | 0.0046
GEN-2022-147 | 05 SOUTHWEST | 763483 | GEN-2019-003 | 230 | 8.791 | 8.7956 | 0.0046
GEN-2022-147 | 05 SOUTHWEST | 524016 | ASARCO 3 | 115 | 27.0598 | 27.0643 | 0.0045
GEN-2022-147 | 05 SOUTHWEST | 527242 | AMERADA 3 | 115 | 11.8211 | 11.8256 | 0.0045
GEN-2022-147 | 05 SOUTHWEST | 525432 | SP-HALFWAY+2 | 69 | 6.1317 | 6.1361 | 0.0044
GEN-2022-147 | 05 SOUTHWEST | 527238 | ROZ 3 | 115 | 11.6623 | 11.6667 | 0.0044
GEN-2022-147 | 05 SOUTHWEST | 515961 | GUTHRIE7 | 345 | 11.5934 | 11.5978 | 0.0044
GEN-2022-147 | 05 SOUTHWEST | 528232 | OCHOA 3 | 115 | 12.6514 | 12.6558 | 0.0044
GEN-2022-147 | 05 SOUTHWEST | 525636 | LAMB_CNTY 3 | 115 | 8.6408 | 8.6451 | 0.0043
GEN-2022-147 | 05 SOUTHWEST | 528231 | AGAVE_RHIL23 | 115 | 12.5886 | 12.5929 | 0.0043
GEN-2022-147 | 05 SOUTHWEST | 527656 | CROSSROADS 7 | 345 | 7.8825 | 7.8868 | 0.0043
GEN-2022-147 | 05 SOUTHWEST | 527802 | EDDY_CNTY 7 | 345 | 7.3374 | 7.3417 | 0.0043
GEN-2022-147 | 05 SOUTHWEST | 599960 | EPTNP-D6 | 230 | 9.6277 | 9.632 | 0.0043
GEN-2022-147 | 05 SOUTHWEST | 515407 | TATONGA7 | 345 | 17.2797 | 17.2839 | 0.0042
GEN-2022-147 | 05 SOUTHWEST | 524414 | AMA_SOUTH 3 | 115 | 17.3882 | 17.3923 | 0.0041
GEN-2022-147 | 05 SOUTHWEST | 526086 | SW_6786_N 2 | 69 | 5.2428 | 5.2468 | 0.004
GEN-2022-147 | 05 SOUTHWEST | 526087 | SW_6786_S 2 | 69 | 5.2428 | 5.2468 | 0.004
GEN-2022-147 | 05 SOUTHWEST | 525885 | SP-NEWDEAL 2 | 69 | 3.4783 | 3.4822 | 0.0039
GEN-2022-147 | 05 SOUTHWEST | 526452 | AMOCO_CRYO 3 | 115 | 6.6386 | 6.6425 | 0.0039
GEN-2022-147 | 05 SOUTHWEST | 527024 | ALLRED_SUB 3 | 115 | 11.304 | 11.3079 | 0.0039
GEN-2022-147 | 05 SOUTHWEST | 515497 | MATHWSN7 | 345 | 31.2433 | 31.2472 | 0.0039
GEN-2022-147 | 05 SOUTHWEST | 524822 | CURRY 3 | 115 | 11.3384 | 11.3421 | 0.0037
GEN-2022-147 | 05 SOUTHWEST | 524908 | ROOSEVELT 3 | 115 | 11.2464 | 11.2501 | 0.0037
GEN-2022-147 | 05 SOUTHWEST | 525056 | BC-EARTH 3 | 115 | 8.0793 | 8.0829 | 0.0036
GEN-2022-147 | 05 SOUTHWEST | 524875 | OASIS 6 | 230 | 7.8855 | 7.8891 | 0.0036
GEN-2022-147 | 05 SOUTHWEST | 760498 | G17-146-TAP | 230 | 7.9901 | 7.9937 | 0.0036
GEN-2022-147 | 05 SOUTHWEST | 525925 | CROSBY 2 | 69 | 5.4904 | 5.4939 | 0.0035
GEN-2022-147 | 05 SOUTHWEST | 525811 | LH-HARMONY 2 | 69 | 4.6615 | 4.665 | 0.0035
GEN-2022-147 | 05 SOUTHWEST | 527655 | RSVLT_CC_E 7 | 345 | 7.2691 | 7.2726 | 0.0035
GEN-2022-147 | 05 SOUTHWEST | 527020 | SIDEWINDER 7 | 230 | 17.672 | 17.6755 | 0.0035
GEN-2022-147 | 05 SOUTHWEST | 588560 | GEN-2017-011 | 345 | 11.9016 | 11.9051 | 0.0035
GEN-2022-147 | 05 SOUTHWEST | 524377 | FARMERS 3 | 115 | 15.8819 | 15.8853 | 0.0034
GEN-2022-147 | 05 SOUTHWEST | 527599 | SAGA_SDCOL 7 | 345 | 7.169 | 7.1724 | 0.0034
GEN-2022-147 | 05 SOUTHWEST | 527600 | SAGA_SMEAS 7 | 345 | 7.169 | 7.1724 | 0.0034
GEN-2022-147 | 05 SOUTHWEST | 527610 | SAGA_SCOL 7 | 345 | 7.169 | 7.1724 | 0.0034
GEN-2022-147 | 05 SOUTHWEST | 515951 | PERSIMN7 | 345 | 10.2855 | 10.2889 | 0.0034
GEN-2022-147 | 05 SOUTHWEST | 522800 | MU-TULIA 3 | 115 | 5.4573 | 5.4606 | 0.0033
GEN-2022-147 | 05 SOUTHWEST | 524623 | DEAFSMITH 6 | 230 | 8.2172 | 8.2205 | 0.0033
GEN-2022-147 | 05 SOUTHWEST | 527194 | LG-PLSHILL 3 | 115 | 8.3475 | 8.3507 | 0.0032
GEN-2022-147 | 05 SOUTHWEST | 515444 | MCNOWND7 | 345 | 20.319 | 20.3222 | 0.0032
GEN-2022-147 | 05 SOUTHWEST | 528185 | N_LOVING 7 | 345 | 5.961 | 5.9642 | 0.0032
GEN-2022-147 | 05 SOUTHWEST | 760494 | GEN-2017-146 | 230 | 7.6973 | 7.7005 | 0.0032
GEN-2022-147 | 05 SOUTHWEST | 525731 | SP-ABERNTHY2 | 69 | 3.1651 | 3.1682 | 0.0031
GEN-2022-147 | 05 SOUTHWEST | 524009 | CHERRY 3 | 115 | 19.3301 | 19.3332 | 0.0031
GEN-2022-147 | 05 SOUTHWEST | 524404 | OWENSCORN 3 | 115 | 15.5052 | 15.5083 | 0.0031
GEN-2022-147 | 05 SOUTHWEST | 524801 | NORRIS 3 | 115 | 10.3688 | 10.3719 | 0.0031
GEN-2022-147 | 05 SOUTHWEST | 527022 | APACHE_ROB 3 | 115 | 9.9986 | 10.0017 | 0.0031
GEN-2022-147 | 05 SOUTHWEST | 761250 | GEN-2017-233 | 345 | 19.7859 | 19.789 | 0.0031
GEN-2022-147 | 05 SOUTHWEST | 526792 | PRENTICE 3 | 115 | 6.3234 | 6.3264 | 0.003
GEN-2022-147 | 05 SOUTHWEST | 515852 | DGRASSE7 | 345 | 13.8049 | 13.8079 | 0.003
GEN-2022-147 | 05 SOUTHWEST | 524757 | BETHEL_COL13 | 115 | 8.5083 | 8.5113 | 0.003
GEN-2022-147 | 05 SOUTHWEST | 527000 | GAINES_PLNT7 | 230 | 18.07 | 18.073 | 0.003
GEN-2022-147 | 05 SOUTHWEST | 761229 | GEN-2017-150 | 345 | 19.7522 | 19.7552 | 0.003
GEN-2022-147 | 05 SOUTHWEST | 524768 | PLSNT_HILL 3 | 115 | 10.6437 | 10.6467 | 0.003
GEN-2022-147 | 05 SOUTHWEST | 587770 | GEN-2016-095 | 345 | 10.1178 | 10.1208 | 0.003
GEN-2022-147 | 05 SOUTHWEST | 524874 | OASIS 3 | 115 | 10.193 | 10.1959 | 0.0029
GEN-2022-147 | 05 SOUTHWEST | 526735 | TERRY_CNTY 2 | 69 | 7.3854 | 7.3883 | 0.0029
GEN-2022-147 | 05 SOUTHWEST | 525637 | LAMB_CNTY 6 | 230 | 5.558 | 5.5609 | 0.0029
GEN-2022-147 | 05 SOUTHWEST | 585440 | PRSIMN_CRK2 | 345 | 9.483 | 9.4859 | 0.0029
GEN-2022-147 | 05 SOUTHWEST | 527654 | RSVLT_CC_W 7 | 345 | 6.7088 | 6.7116 | 0.0028
GEN-2022-147 | 05 SOUTHWEST | 527666 | RSVLT_COL1 7 | 345 | 6.7088 | 6.7116 | 0.0028
GEN-2022-147 | 05 SOUTHWEST | 527667 | RSVLT_COL2 7 | 345 | 6.7088 | 6.7116 | 0.0028
GEN-2022-147 | 05 SOUTHWEST | 525915 | SP-CROSBY 2 | 69 | 4.9 | 4.9028 | 0.0028
GEN-2022-147 | 05 SOUTHWEST | 587740 | GEN-2016-091 | 345 | 9.794 | 9.7968 | 0.0028
GEN-2022-147 | 05 SOUTHWEST | 527598 | SAGA_NDCOL 7 | 345 | 6.4153 | 6.418 | 0.0027
GEN-2022-147 | 05 SOUTHWEST | 527601 | SAGA_NCOL 7 | 345 | 6.4153 | 6.418 | 0.0027
GEN-2022-147 | 05 SOUTHWEST | 524267 | BUSHLAND 6 | 230 | 10.1341 | 10.1368 | 0.0027
GEN-2022-147 | 05 SOUTHWEST | 515677 | BADGER 7 | 345 | 14.0407 | 14.0433 | 0.0026
GEN-2022-147 | 05 SOUTHWEST | 524388 | CROUSE_HIND3 | 115 | 13.9408 | 13.9434 | 0.0026
GEN-2022-147 | 05 SOUTHWEST | 524770 | PLSNT_HILL 6 | 230 | 6.5935 | 6.5961 | 0.0026
GEN-2022-147 | 05 SOUTHWEST | 526267 | LUBBCK_STH 2 | 69 | 4.5482 | 4.5508 | 0.0026
GEN-2022-147 | 05 SOUTHWEST | 528027 | RDRUNNER 7 | 345 | 5.471 | 5.4736 | 0.0026
GEN-2022-147 | 05 SOUTHWEST | 515585 | MAMTHPW7 | 345 | 13.7704 | 13.773 | 0.0026
GEN-2022-147 | 05 SOUTHWEST | 526655 | LYNN_CNTY 2 | 69 | 4.836 | 4.8386 | 0.0026
GEN-2022-147 | 05 SOUTHWEST | 525892 | MONROE 2 | 69 | 2.7834 | 2.7859 | 0.0025
GEN-2022-147 | 05 SOUTHWEST | 516146 | 25MILE 7 | 345 | 9.9916 | 9.9941 | 0.0025
GEN-2022-147 | 05 SOUTHWEST | 516159 | 25MILZ 7 | 345 | 9.98 | 9.9825 | 0.0025
GEN-2022-147 | 05 SOUTHWEST | 515425 | WWDPST 4 | 138 | 17.8025 | 17.8049 | 0.0024
GEN-2022-147 | 05 SOUTHWEST | 524397 | ARROWHEAD 3 | 115 | 14.1432 | 14.1456 | 0.0024
GEN-2022-147 | 05 SOUTHWEST | 526020 | HOCKLEY 3 | 115 | 5.6561 | 5.6585 | 0.0024
GEN-2022-147 | 05 SOUTHWEST | 761796 | GEN-2017-187 | 115 | 6.996 | 6.9984 | 0.0024
GEN-2022-147 | 05 SOUTHWEST | 515554 | BVRCNTY7 | 345 | 14.738 | 14.7403 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 524745 | CASTRO_CNTY2 | 69 | 9.1277 | 9.13 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 525853 | LH-WIL&ELN+2 | 69 | 2.6699 | 2.6722 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 525891 | WHITEHEAD 2 | 69 | 2.6824 | 2.6847 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 527021 | CORTEZ 3 | 115 | 8.5372 | 8.5395 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 527262 | SULPHUR 3 | 115 | 6.9277 | 6.93 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 525279 | WSTRIDGE_TP3 | 69 | 4.4641 | 4.4664 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 515825 | GRTWSRN7 | 345 | 8.5235 | 8.5258 | 0.0023
GEN-2022-147 | 05 SOUTHWEST | 515686 | BLUWND 7 | 345 | 12.7548 | 12.757 | 0.0022
GEN-2022-147 | 05 SOUTHWEST | 526205 | IVORY 2 | 69 | 4.111 | 4.1132 | 0.0022
GEN-2022-147 | 05 SOUTHWEST | 526256 | IVORY_TP 2 | 69 | 4.107 | 4.1092 | 0.0022
GEN-2022-147 | 05 SOUTHWEST | 525738 | HALECENTER 2 | 69 | 2.5822 | 2.5843 | 0.0021
GEN-2022-147 | 05 SOUTHWEST | 525745 | LH-HALECTR 2 | 69 | 2.5531 | 2.5552 | 0.0021
GEN-2022-147 | 05 SOUTHWEST | 515448 | CRSRDSW7 | 345 | 12.2058 | 12.2078 | 0.002
GEN-2022-147 | 05 SOUTHWEST | 523097 | HITCHLAND 7 | 345 | 15.1305 | 15.1325 | 0.002
GEN-2022-147 | 05 SOUTHWEST | 524338 | SOUTHEAST 3 | 115 | 11.6715 | 11.6735 | 0.002
GEN-2022-147 | 05 SOUTHWEST | 523101 | NOBLE_WND 7 | 345 | 15.0738 | 15.0758 | 0.002
GEN-2022-147 | 05 SOUTHWEST | 523961 | POTTER_CO 7 | 345 | 9.2726 | 9.2746 | 0.002
GEN-2022-147 | 05 SOUTHWEST | 528015 | PHANTOM 7 | 345 | 4.8874 | 4.8894 | 0.002
GEN-2022-147 | 05 SOUTHWEST | 523112 | NOVUS1 7 | 345 | 14.8453 | 14.8472 | 0.0019
GEN-2022-147 | 05 SOUTHWEST | 525191 | KRESS_INT 2 | 69 | 4.7207 | 4.7226 | 0.0019
GEN-2022-147 | 05 SOUTHWEST | 525203 | SW-KRESS 2 | 69 | 4.7207 | 4.7226 | 0.0019
GEN-2022-147 | 05 SOUTHWEST | 525413 | LAMTON 2 | 69 | 5.3559 | 5.3578 | 0.0019
GEN-2022-147 | 05 SOUTHWEST | 528195 | AGAVE_PDURO3 | 115 | 7.9442 | 7.946 | 0.0018
GEN-2022-147 | 05 SOUTHWEST | 525860 | SP-BECTON +2 | 69 | 2.3692 | 2.371 | 0.0018
GEN-2022-147 | 05 SOUTHWEST | 524924 | PORTALES 3 | 115 | 7.72 | 7.7217 | 0.0017
GEN-2022-147 | 05 SOUTHWEST | 525425 | CORNER 2 | 69 | 3.8042 | 3.8059 | 0.0017
GEN-2022-147 | 05 SOUTHWEST | 525723 | CNTYLINE_TP2 | 69 | 2.3143 | 2.316 | 0.0017
GEN-2022-147 | 05 SOUTHWEST | 526075 | STANTON_E 2 | 69 | 3.395 | 3.3967 | 0.0017
GEN-2022-147 | 05 SOUTHWEST | 525153 | HAPPY_INT 2 | 69 | 5.3539 | 5.3555 | 0.0016
GEN-2022-147 | 05 SOUTHWEST | 587570 | ASGI1604 | 115 | 7.0545 | 7.0561 | 0.0016
GEN-2022-147 | 05 SOUTHWEST | 526694 | GRAHAM 3 | 115 | 2.9846 | 2.9862 | 0.0016
GEN-2022-147 | 05 SOUTHWEST | 515590 | PALDR2W7 | 345 | 12.9071 | 12.9087 | 0.0016
GEN-2022-147 | 05 SOUTHWEST | 515618 | BALKOW 7 | 345 | 12.353 | 12.3546 | 0.0016
GEN-2022-147 | 05 SOUTHWEST | 525316 | LH-PROVDNCE2 | 69 | 3.605 | 3.6066 | 0.0016
GEN-2022-147 | 05 SOUTHWEST | 525325 | COX 2 | 69 | 3.605 | 3.6066 | 0.0016
GEN-2022-147 | 05 SOUTHWEST | 525899 | SP-SHALLWTR2 | 69 | 2.2073 | 2.2089 | 0.0016
GEN-2022-147 | 05 SOUTHWEST | 526102 | SP-HETTLER 2 | 69 | 3.3439 | 3.3455 | 0.0016
GEN-2022-147 | 05 SOUTHWEST | 511431 | LWS S4 | 138 | 11.3521 | 11.3536 | 0.0015
GEN-2022-147 | 05 SOUTHWEST | 525271 | KISER 2 | 69 | 3.6826 | 3.6841 | 0.0015
GEN-2022-147 | 05 SOUTHWEST | 525936 | LH-CROSBY +2 | 69 | 3.6911 | 3.6926 | 0.0015
GEN-2022-147 | 05 SOUTHWEST | 525943 | HENDRICKS 2 | 69 | 3.6555 | 3.657 | 0.0015
GEN-2022-147 | 05 SOUTHWEST | 526506 | LG-DOCWEBR 2 | 69 | 5.2245 | 5.226 | 0.0015
GEN-2022-147 | 05 SOUTHWEST | 525724 | COUNTYLINE 2 | 69 | 2.0264 | 2.0278 | 0.0014
GEN-2022-147 | 05 SOUTHWEST | 526249 | ACCO 2 | 69 | 3.3447 | 3.3461 | 0.0014
GEN-2022-147 | 05 SOUTHWEST | 526693 | GRAHAM 2 | 69 | 3.5415 | 3.5429 | 0.0014
GEN-2022-147 | 05 SOUTHWEST | 525019 | MULSHVLY_TP3 | 115 | 5.3301 | 5.3315 | 0.0014
GEN-2022-147 | 05 SOUTHWEST | 525404 | LC-OLTON 2 | 69 | 4.6528 | 4.6542 | 0.0014
GEN-2022-147 | 05 SOUTHWEST | 515549 | MNCWND37 | 345 | 12.7912 | 12.7925 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 524777 | N_CLOVIS 3 | 115 | 6.9128 | 6.9141 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 525397 | OLTON 2 | 69 | 4.3408 | 4.3421 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 526019 | HOCKLEY 2 | 69 | 5.3442 | 5.3455 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 539801 | THISTLE7 | 345 | 15.0677 | 15.069 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 588630 | GEN-2017-018 | 345 | 15.0677 | 15.069 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 526159 | CARLISLE 2 | 69 | 2.6875 | 2.6888 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 526645 | LG-NH&WILN+2 | 69 | 3.3939 | 3.3952 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 525018 | MULESHVALLY3 | 115 | 5.0126 | 5.0139 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 525635 | LAMB_CNTY 2 | 69 | 6.1287 | 6.13 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 515634 | PALDR1W7 | 345 | 11.4121 | 11.4134 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 523095 | HITCHLAND 6 | 230 | 15.2283 | 15.2296 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 523323 | MCDWL_CREEK6 | 230 | 9.406 | 9.4073 | 0.0013
GEN-2022-147 | 05 SOUTHWEST | 526622 | GARZA 2 | 69 | 3.2731 | 3.2743 | 0.0012
GEN-2022-147 | 05 SOUTHWEST | 524290 | WILDOR2_JUS6 | 230 | 6.9409 | 6.9421 | 0.0012
GEN-2022-147 | 05 SOUTHWEST | 525256 | SW_9748 2 | 69 | 3.2791 | 3.2803 | 0.0012
GEN-2022-147 | 05 SOUTHWEST | 525143 | HAPPY_CTYTP2 | 69 | 4.7691 | 4.7703 | 0.0012
GEN-2022-147 | 05 SOUTHWEST | 511571 | RUSHSPR7 | 345 | 5.6739 | 5.675 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 524923 | PORTALES 2 | 69 | 7.8116 | 7.8127 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 524929 | RO-PORT_MTR2 | 69 | 7.8116 | 7.8127 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 524935 | KILGORE 3 | 115 | 6.3161 | 6.3172 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 525263 | W_PLAINVEW 2 | 69 | 3.1675 | 3.1686 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 525284 | WESTRIDGE 2 | 69 | 3.1774 | 3.1785 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 526228 | BATTON_S 2 | 69 | 2.8428 | 2.8439 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 525790 | FLOYDADA_TP2 | 69 | 2.6878 | 2.6889 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 525797 | S_FLOYDADA 2 | 69 | 2.6735 | 2.6746 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 525804 | LH-FLYDADA+2 | 69 | 2.6573 | 2.6584 | 0.0011
GEN-2022-147 | 05 SOUTHWEST | 515610 | FSHRTAP7 | 345 | 17.9503 | 17.9513 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 524694 | DS-#22 3 | 115 | 4.7774 | 4.7784 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 524963 | S_PORTALES 3 | 115 | 5.9357 | 5.9367 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 525650 | LC-LTTLFLD+2 | 69 | 5.1326 | 5.1336 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 762900 | GEN-2018-055 | 345 | 5.4105 | 5.4115 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 525339 | AIKEN_RURL 2 | 69 | 2.9235 | 2.9245 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 526073 | STANTON_N 2 | 69 | 1.749 | 1.75 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 526184 | SW_6878 2 | 69 | 2.2629 | 2.2639 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 526592 | DIEKEMPER 2 | 69 | 2.9655 | 2.9665 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 515582 | SLNGWND7 | 345 | 8.631 | 8.632 | 0.001
GEN-2022-147 | 05 SOUTHWEST | 515853 | DGRASSE4 | 138 | 14.6185 | 14.6194 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 763769 | GEN-2019-045 | 138 | 14.6185 | 14.6194 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 526009 | LC-LEVLND#22 | 69 | 4.4624 | 4.4633 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 526048 | LVLNDCTY_TP2 | 69 | 4.4624 | 4.4633 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 522805 | MU-FLOYDADA2 | 69 | 2.3171 | 2.318 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 525307 | E_PLAINVEW 2 | 69 | 2.6101 | 2.611 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 525338 | SW_3710 2 | 69 | 2.6957 | 2.6966 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 526130 | SP-CARLISLE2 | 69 | 2.2094 | 2.2103 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 526499 | LG-MEADOW 2 | 69 | 3.9133 | 3.9142 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 526513 | LG-TWO_DRAW2 | 69 | 2.9532 | 2.9541 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 514785 | WOODWRD4 | 138 | 13.5016 | 13.5025 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 523215 | GEN-2011-022 | 345 | 10.6366 | 10.6375 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 524885 | SN_JUAN_TAP6 | 230 | 4.636 | 4.6369 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 524977 | GREYHOUND 3 | 115 | 5.8505 | 5.8514 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 526562 | SLATON 2 | 69 | 2.5992 | 2.6001 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 527201 | SEAGRAVES 2 | 69 | 5.8165 | 5.8174 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 576395 | GEN-2010-014 | 345 | 10.6366 | 10.6375 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 576397 | G10014G11022 | 345 | 10.6366 | 10.6375 | 0.0009
GEN-2022-147 | 05 SOUTHWEST | 515398 | OUSPRT 4 | 138 | 9.7699 | 9.7707 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 524331 | PULLMAN 3 | 115 | 7.5185 | 7.5193 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 524889 | SN_JUAN_WND6 | 230 | 4.407 | 4.4078 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 525023 | BC-BAIL_MTR2 | 69 | 5.0935 | 5.0943 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 525027 | BAILEYCO 2 | 69 | 5.0935 | 5.0943 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 525298 | S_PLAINVEW 2 | 69 | 2.7094 | 2.7102 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 525351 | LH-AIKEN 2 | 69 | 2.2885 | 2.2893 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 525867 | ALLMON 2 | 69 | 2.3029 | 2.3037 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 525874 | LH-PETERBRG2 | 69 | 2.3056 | 2.3064 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 526116 | SP-IDALOU +2 | 69 | 2.3472 | 2.348 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 526726 | LG-DRAW 2 | 69 | 2.6597 | 2.6605 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 525687 | LC-LUMSCHAP2 | 69 | 4.8031 | 4.8039 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 527217 | MOSS 2 | 69 | 5.7076 | 5.7084 | 0.0008
GEN-2022-147 | 05 SOUTHWEST | 525132 | LC-N_OLTON 2 | 69 | 3.2052 | 3.2059 | 0.0007
GEN-2022-147 | 05 SOUTHWEST | 526049 | LVLAND_CITY2 | 69 | 4.0632 | 4.0639 | 0.0007
GEN-2022-147 | 05 SOUTHWEST | 526123 | VICKERS 2 | 69 | 2.1911 | 2.1918 | 0.0007
GEN-2022-147 | 05 SOUTHWEST | 526747 | LG-BROWNFLD2 | 69 | 3.7595 | 3.7602 | 0.0007
GEN-2022-147 | 05 SOUTHWEST | 587230 | GEN-2016-037 | 345 | 6.6656 | 6.6663 | 0.0007
GEN-2022-147 | 05 SOUTHWEST | 560078 | G16-037-TAP | 345 | 6.9142 | 6.9149 | 0.0007
GEN-2022-147 | 05 SOUTHWEST | 515394 | KEENAN 4 | 138 | 9.1316 | 9.1323 | 0.0007
GEN-2022-147 | 05 SOUTHWEST | 515877 | REDDIRT7 | 345 | 16.2066 | 16.2073 | 0.0007
GEN-2022-147 | 05 SOUTHWEST | 585190 | GEN-2015-082 | 345 | 7.2952 | 7.2958 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 515939 | MNCWND47 | 345 | 9.0373 | 9.0379 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 524941 | PORTALES#1 2 | 69 | 5.9642 | 5.9648 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 525017 | EMULESH&VLY2 | 69 | 4.1688 | 4.1694 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 525164 | SHAMRCK_PMP2 | 69 | 3.4372 | 3.4378 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 525657 | W_ANTON_TP 2 | 69 | 4.2814 | 4.282 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 525224 | KRESS_RURL 2 | 69 | 2.6538 | 2.6544 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 525358 | LOCKNEY 2 | 69 | 2.2809 | 2.2815 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 525906 | SP-ACUFF +2 | 69 | 2.0766 | 2.0772 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 526221 | BATTON_N 2 | 69 | 1.8619 | 1.8625 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 526416 | SLAUGTER_TP2 | 69 | 3.3119 | 3.3125 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 527212 | DIAMONDBACK3 | 115 | 3.6331 | 3.6337 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 524276 | WILDOR_WND 6 | 230 | 5.2026 | 5.2032 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 524523 | CANYON_EAST3 | 115 | 5.6388 | 5.6394 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 525620 | LTFLD_S&CTY2 | 69 | 4.3489 | 4.3495 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 511557 | CHISHOLM6 | 230 | 8.4167 | 8.4173 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 523551 | HUTCHISON 6 | 230 | 7.4883 | 7.4889 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 760284 | GEN-2017-220 | 345 | 18.439 | 18.4396 | 0.0006
GEN-2022-147 | 05 SOUTHWEST | 515600 | KNGFSHR7 | 345 | 12.2114 | 12.2119 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 515605 | CANADN7 | 345 | 13.2736 | 13.2741 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 524934 | ZODIAC 2 | 69 | 5.752 | 5.7525 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 525001 | W_MULESHOE 2 | 69 | 4.0024 | 4.0029 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 526666 | LG-CENTRAL 2 | 69 | 2.1311 | 2.1316 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 526754 | BROWNFIELD 2 | 69 | 3.2157 | 3.2162 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 524296 | SPNSPUR_WND7 | 345 | 4.6626 | 4.6631 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 524299 | SPNSPUR_COL7 | 345 | 4.6626 | 4.6631 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 524544 | SPRING_DRW 3 | 115 | 6.6748 | 6.6753 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 524728 | DS-CASTRO 2 | 69 | 4.4633 | 4.4638 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 525008 | MULESH_CTY 2 | 69 | 4.162 | 4.1625 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 525694 | HOBGOOD 2 | 69 | 3.5878 | 3.5883 | 0.0005
GEN-2022-147 | 05 SOUTHWEST | 765530 | GEN-2021-025 | 138 | 16.3803 | 16.3807 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 511422 | FLETCHR4 | 138 | 8.1366 | 8.137 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 511541 | SWEETWT6 | 230 | 7.4131 | 7.4135 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 511553 | CHISHOLM7 | 345 | 5.6482 | 5.6486 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 522892 | MU-BROWNFLD2 | 69 | 2.8811 | 2.8815 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 524948 | PORTALES#2 2 | 69 | 5.0505 | 5.0509 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 524962 | S_PORTALES 2 | 69 | 4.4874 | 4.4878 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 525129 | LC-HART 2 | 69 | 2.6748 | 2.6752 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 525136 | HAPPY_CTY 2 | 69 | 2.7555 | 2.7559 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 525365 | LH-CDARHLL+2 | 69 | 1.9289 | 1.9293 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 525390 | SPRINGLAKE 2 | 69 | 2.1783 | 2.1787 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 525613 | W_LITTLFLD 2 | 69 | 3.1003 | 3.1007 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 525671 | BAINER 2 | 69 | 3.6576 | 3.658 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 526002 | LC-WHITHRRL2 | 69 | 3.0025 | 3.0029 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 526638 | LG-NEWMOORE2 | 69 | 1.945 | 1.9454 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 526761 | BROWNFLD_TP2 | 69 | 2.978 | 2.9784 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 526971 | TOKIO_TP 2 | 69 | 3.8871 | 3.8875 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 527261 | SULPHUR 2 | 69 | 3.7077 | 3.7081 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 528040 | BATTLE_AXE 3 | 115 | 3.3993 | 3.3997 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 514796 | IODINE-4 | 138 | 7.6621 | 7.6625 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 524821 | CURRY 2 | 69 | 4.5881 | 4.5885 | 0.0004
GEN-2022-147 | 05 SOUTHWEST | 524969 | PORT_EFDC 2 | 69 | 4.1873 | 4.1876 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 524976 | MARKET_ST 2 | 69 | 4.2468 | 4.2471 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 511470 | LGORE-S2 | 69 | 7.2424 | 7.2427 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 515980 | MNCWND57 | 345 | 6.5985 | 6.5988 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 524679 | DIMMIT_S_TP2 | 69 | 3.0523 | 3.0526 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 524721 | DS-#15&#19+2 | 69 | 3.7142 | 3.7145 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 526583 | LG-HAKBERRY2 | 69 | 1.7186 | 1.7189 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 526711 | LG-DIXON 2 | 69 | 2.6342 | 2.6345 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 526777 | GOODPASTURE2 | 69 | 2.5322 | 2.5325 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 526985 | WELLMAN 2 | 69 | 3.0382 | 3.0385 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 526993 | LG-WELLMAN 2 | 69 | 3.263 | 3.2633 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 527229 | OZRK_MAH02 2 | 69 | 2.8659 | 2.8662 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 527253 | ADAIR 2 | 69 | 2.8567 | 2.857 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 527271 | LG-FOSTER +2 | 69 | 2.9608 | 2.9611 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 528240 | PONDEROSA 3 | 115 | 4.2783 | 4.2786 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 525372 | LH-LONESTAR2 | 69 | 1.5273 | 1.5276 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 525373 | LH-LNSTR_TP2 | 69 | 1.5799 | 1.5802 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 526799 | JST_CORNER 2 | 69 | 1.7252 | 1.7255 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 525122 | HART_INDUST2 | 69 | 2.0495 | 2.0498 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 525697 | PUMP/YH_TP 2 | 69 | 3.3222 | 3.3225 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 525995 | LC-HODGE_TP2 | 69 | 2.7265 | 2.7268 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 526042 | COBLE 2 | 69 | 2.3702 | 2.3705 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 526409 | SLAUGHTER 2 | 69 | 2.3401 | 2.3404 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 523103 | NOBLE_WND 3 | 115 | 12.2354 | 12.2357 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 523131 | GRPLNS-HV2-3 | 115 | 11.4578 | 11.4581 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 523771 | GRAPEVINE 6 | 230 | 5.8586 | 5.8589 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 523869 | CHAN+TASCOS6 | 230 | 4.4566 | 4.4569 | 0.0003
GEN-2022-147 | 05 SOUTHWEST | 511544 | DEMPSEY6 | 230 | 4.7389 | 4.7391 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 523111 | NOVUS1 3 | 115 | 8.7504 | 8.7506 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 511490 | ELKCITY6 | 230 | 6.4716 | 6.4718 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 511542 | BUFFCK6 | 230 | 5.72 | 5.7202 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 762834 | GEN-2018-049 | 345 | 6.6696 | 6.6698 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 526703 | YANCY_SUB 2 | 69 | 1.257 | 1.2572 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 524680 | DIMIT_SOUTH2 | 69 | 2.9976 | 2.9978 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 524681 | DIMMIT_EAST2 | 69 | 2.9236 | 2.9238 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 524688 | DS-#3 2 | 69 | 3.0974 | 3.0976 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 524994 | BC-LARIAT 2 | 69 | 2.4232 | 2.4234 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 524996 | BC-PROGRSS+2 | 69 | 2.8268 | 2.827 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 525038 | BAILEY_PMP 2 | 69 | 2.8285 | 2.8287 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 525116 | DS-#12 2 | 69 | 2.4847 | 2.4849 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 525119 | BC-SUNYSIDE2 | 69 | 1.3835 | 1.3837 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 525249 | LH-PLW&FNY+2 | 69 | 1.6829 | 1.6831 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 525379 | LH-SPLAINS 2 | 69 | 1.2619 | 1.2621 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 525592 | SUDANRURAL 2 | 69 | 1.8947 | 1.8949 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 525599 | LC-SANDHLL+2 | 69 | 2.1963 | 2.1965 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 525606 | AMHERST 2 | 69 | 2.4476 | 2.4478 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 525664 | LC-SPD&HART2 | 69 | 2.7738 | 2.774 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 525678 | W_ANTON 2 | 69 | 2.4711 | 2.4713 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 525708 | MIDAMERI#2 2 | 69 | 2.5588 | 2.559 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 525717 | WHITHARRAL 2 | 69 | 2.487 | 2.4872 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 526056 | E_LEVELLAND2 | 69 | 1.7521 | 1.7523 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 526576 | SOUTHLAND 2 | 69 | 1.4572 | 1.4574 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 526615 | YANCY_TP 2 | 69 | 1.3765 | 1.3767 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 526719 | BG-YANCY_TP2 | 69 | 1.355 | 1.3552 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 526770 | OZARK_MAHO 2 | 69 | 1.8821 | 1.8823 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 526821 | BG-JSTBG_TP2 | 69 | 1.3288 | 1.329 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 526965 | KINNEY 2 | 69 | 2.5633 | 2.5635 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 526979 | LG-JS_SMITH2 | 69 | 2.2108 | 2.211 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 526999 | UNION_TX 2 | 69 | 2.5896 | 2.5898 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 527211 | DIAMONDBACK2 | 69 | 3.0693 | 3.0695 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 527223 | LG-MC&SMNL+2 | 69 | 2.7464 | 2.7466 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 527247 | CEDARLAKE 2 | 69 | 2.667 | 2.6672 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 527250 | OXY_CEDRLKE2 | 69 | 2.6755 | 2.6757 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 527305 | LG-SAWYERFL2 | 69 | 2.2637 | 2.2639 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 528617 | LE-WAITS 2 | 69 | 3.7291 | 3.7293 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 528714 | LE-FORT_SW 2 | 69 | 3.5038 | 3.504 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 511547 | ROARK6 | 230 | 4.7168 | 4.717 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 515863 | REDCLF 4 | 138 | 6.988 | 6.9882 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 520601 | AVARD 4 | 138 | 6.6508 | 6.651 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 523823 | CARPENTER 7 | 345 | 6.6951 | 6.6953 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 539813 | TRANSFORMER | 345 | 9.0225 | 9.0227 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 539840 | GEN-2011-008 | 345 | 8.6601 | 8.6603 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 539841 | G-2011-008-1 | 345 | 7.4456 | 7.4458 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 763890 | GEN-2019-058 | 345 | 10.2028 | 10.203 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 764980 | GEN-2020-008 | 345 | 6.6951 | 6.6953 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 765490 | GEN-2021-021 | 345 | 6.3155 | 6.3157 | 0.0002
GEN-2022-147 | 05 SOUTHWEST | 523130 | GRPLNS-HV4-3 | 115 | 8.3848 | 8.3849 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 511503 | LAW WC2 | 69 | 4.7392 | 4.7393 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 514775 | TANGRTP2 | 69 | 5.003 | 5.0031 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 514779 | WDNITRO2 | 69 | 4.9904 | 4.9905 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 532783 | KINGMAN7 | 345 | 7.3088 | 7.3089 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 560577 | G06-44 | 115 | 7.9187 | 7.9188 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 900001 | TRAVERSE3 | 345 | 5.4544 | 5.4545 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 524477 | CAMPBELL_ST3 | 115 | 2.4638 | 2.4639 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 524486 | CAPROCK 3 | 115 | 2.8878 | 2.8879 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 524502 | NORTON 3 | 115 | 3.2354 | 3.2355 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 524783 | W_CLOVIS 2 | 69 | 2.5427 | 2.5428 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 525703 | YELLOWHOUSE2 | 69 | 2.1834 | 2.1835 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 527235 | LG-ASHMORE 2 | 69 | 2.3897 | 2.3898 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 528718 | LE-NEWTEX 2 | 69 | 2.7561 | 2.7562 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 599950 | LAMAR7 | 345 | 2.4555 | 2.4556 | 0.0001
GEN-2022-147 | 05 SOUTHWEST | 526807 | BG-JUSTBRG 2 | 69 | 0.8109 | 0.811 | 0.0001