## Executive Summary
Executive Summary: GEN-2022-009_010_083 Interim Availability Interconnection System Impact Study
Interconnection Customer GEN-2022-009, GEN-2022-010, and GEN-2022-083 (Group 01) have requested a Limited Operation or Interim Availability Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions (Scenarios Tab) at the time of service to determine the amount of Interconnection Capacity available to the interconnection customers listed under specific system conditions.
Once a GIA amendment to incorporate Interim GIA is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Interim Operation in accordance with the SPP study results.
Interim
In accordance with Section 11A of the GIP, Interim GIA, Interconnection Customers with a pending Interconnection Request that has an anticipated In-Service Date prior to the expected completion of the DISIS may request a study to evaluate the feasibility of Interim Interconnection Service.
Interim Interconnection Capacity conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Study Limitations
In the event that an Interconnection Request, with queue priority equal to or higher than a Interconnection Request, which was excluded as a study scenario achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study scenario is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
GENERATOR INTERCONNECTION MANUAL Version 2.2
https://www.spp.org/documents/71111/disis-study-manual.pdf
Models Used in Study
Power Flow Analysis: DISIS-2018-002/DISIS-2019-001 (2021 ITP Series)
Summer: 2023 (23SP), 2026 (26SP)
Winter: 2026 (26WP)
Stability Analysis: DISIS-2018-002/DISIS-2019-001 Phase 2 (P2) (2020 Series MDWG Dynamics)* * modified to exclude network upgrades assigned through DISIS-1702 and DISIS-1801
Summer: 2025 (25SP)
Winter: 2025 (25WP)
Short Circuit Analysis: DISIS-2018-002/DISIS-2019-001 Phase 2 (P2) (2020 Series MDWG Dynamics)
Summer: 2025 (25SP)
Author: SPP Generator Interconnection Department
Published: 06/10/2024

## Revision History
Revision History
Date | Author | Change Description
2024-04-02 | SPP | Draft.
2024-04-19 | SPP | Final.
2024-06-10 | SPP | GEN-2022-083 MW amount and LOIS amount corrected.

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Service | Area | POI | Status
GEN-2022-009 | 01 - North | 24 | DIS-22-1 | Thermal | 125 | 125 | None | ER | BEPC-SPP | Judson Substation 345 kV | DISIS STAGE
GEN-2022-010 | 01 - North | 24 | DIS-22-1 | Thermal | 250 | 250 | None | ER | BEPC-SPP | Judson Substation 345 kV | DISIS STAGE
GEN-2022-083 | 01 - North | 24 | DIS-22-1 | Thermal | 250 | 250 | None | ER | BEPC-SPP | Judson Substation 345 kV | DISIS STAGE
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | - | - | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal | 15.56 | - | - | ER/NR | MIDW | Saxman 115kV substation | DISIS STAGE
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal | 15.15 | - | - | ER/NR | BEPC-SPP | Siouxland 69kV | DISIS STAGE
GEN-2020-002 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 81 | - | - | ER | OPPD | 6846 Substation 69 kV | DISIS STAGE
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | - | - | ER/NR | BEPC-SPP | Lonesome Creek 115kV | DISIS STAGE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 6.5 | - | - | ER/NR | SUNC | Russell 115 kV Substation | DISIS STAGE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 13.5 | - | - | ER/NR | SUNC | Russell 115 kV Substation | DISIS STAGE
GIA-106 | 03 CENTRAL | 21.5 | DIS-19-1 PQ | Solar | 118.696 | - | - | ER/NR | AECI
GIA-106 | 03 CENTRAL | 21.5 | DIS-19-1 PQ | Solar | 115.692 | - | - | ER/NR | AECI
GIA-106 | 03 CENTRAL | 21.5 | DIS-19-1 PQ | Solar | 115.692 | - | - | ER/NR | AECI
GIA-107 | 03 CENTRAL | 21.5 | DIS-19-1 PQ | Solar | 125 | - | - | ER/NR | AECI
GIA-107 | 03 CENTRAL | 21.5 | DIS-19-1 PQ | Solar | 125 | - | - | ER/NR | AECI
GEN-2018-063 | 03 CENTRAL | 21 | DIS-18-2 | Solar | 57 | - | - | ER | EMDE | Sedalia Marshfield Springfield Nichols Street 69kV circuit | DISIS STAGE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | - | - | ER/NR | GRDA | Tonnece Substation 69kV | DISIS STAGE
GEN-2018-065 | 02 NEBRASKA | 21 | DIS-18-2 | WIND | 19.8 | - | - | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | WIND | 128.9 | - | - | ER | BEPC-SPP | 115kV Strandahl sub | DISIS STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | WIND | 126.1 | - | - | ER | BEPC-SPP | 115kV Strandahl sub | DISIS STAGE
GEN-2018-068 | 02 NEBRASKA | 21 | DIS-18-2 | WIND | 151.2 | - | - | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-068 | 02 NEBRASKA | 21 | DIS-18-2 | WIND | 151.2 | - | - | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2 | WIND | 125 | - | - | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | BATTERY | 151 | - | - | ER/NR | OGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | BATTERY | 151 | - | - | ER/NR | OGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | WIND | 78 | - | - | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | - | - | ER | AEPW | Farmland-Delaware 138kV line | DISIS STAGE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | WIND | 104.4 | - | - | ER | AEPW | Pittsburg 345kV Substation | DISIS STAGE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | WIND | 110.6 | - | - | ER | AEPW | Pittsburg 345kV Substation | DISIS STAGE
GEN-2018-083 | 02 NEBRASKA | 21 | DIS-18-2 | WIND | 125 | - | - | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | DISIS STAGE
GEN-2018-083 | 02 NEBRASKA | 21 | DIS-18-2 | WIND | 125 | - | - | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | DISIS STAGE
GEN-2018-088 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 130 | - | - | ER | AEPW | Lydia 345kV substation | DISIS STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | WIND | 196 | - | - | ER | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | WIND | 150 | - | - | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | WIND | 150 | - | - | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | - | - | ER | AEPW | Longwood 345kV substation | DISIS STAGE
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | BATTERY | 95 | - | - | ER | SUNC | Thistle 345kV substation | DISIS STAGE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 250 | - | - | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | DISIS STAGE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | BATTERY | 50 | - | - | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | DISIS STAGE
GEN-2018-116 | 03 CENTRAL | 21 | DIS-18-2 | Solar | 2.41 | - | - | ER/NR | SUNC | Frey Street 115kV bus | DISIS STAGE
GEN-2018-116 | 03 CENTRAL | 21 | DIS-18-2 | Solar | 147.59 | - | - | ER/NR | SUNC | Frey Street 115kV bus | DISIS STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | WIND | 231 | - | - | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | DISIS STAGE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | WIND | 200.22 | - | - | ER/NR | WERE | Renfrow-Viola 345 kV | DISIS STAGE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | - | - | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | - | - | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | BATTERY | 100 | - | - | ER | GRDA | Maid 161kV substation | DISIS STAGE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | - | - | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | - | - | ER | OPPD | S1263 Brock 161kV substation | DISIS STAGE
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | BATTERY | 230 | - | - | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-19-1 | BATTERY | 200 | - | - | ER/NR | OGE | Woodward 345kV substation | DISIS STAGE
GEN-2019-013 | 04 SOUTHEAST | 21 | DIS-19-1 | BATTERY | 50 | - | - | ER/NR | AEPW | Dempsey 230kV sub/Sweetwater 230kV | DISIS STAGE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | - | - | ER | EMDE | Dadeville 161kV Substation | DISIS STAGE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | - | - | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-023 | 01 NORTH | 21 | DIS-19-1 | WIND | 110 | - | - | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2019-023 | 01 NORTH | 21 | DIS-19-1 | BATTERY | 50 | - | - | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | WIND | 126 | - | - | ER/NR | SUNC | Spearville to Clark County 345 kV line | DISIS STAGE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | WIND | 126 | - | - | ER/NR | SUNC | Spearville to Clark County 345 kV line | DISIS STAGE
GEN-2019-035 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 80 | - | - | ER/NR | EMDE | Reeds Spring-Aurora 161kV Line | DISIS STAGE
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | - | - | ER/NR | BEPC-SPP | Leland Olds 345kV substation | DISIS STAGE
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | - | - | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | DISIS STAGE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 39 | - | - | ER/NR | NPPD | 115kV Monolith Substation | DISIS STAGE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 39 | - | - | ER/NR | NPPD | 115kV Monolith Substation | DISIS STAGE
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | - | - | ER | SUNC | North Fort Dodge 115kV Substation | DISIS STAGE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | - | - | ER | OGE | DeGrasse 138kV Substation | DISIS STAGE
GEN-2019-048 | 03 CENTRAL | 21 | DIS-19-1 | BATTERY | 50 | - | - | ER | KCPL | Duncan 69kV substation | DISIS STAGE
GEN-2019-051 | 03 CENTRAL | 21 | DIS-19-1 | BATTERY | 40 | - | - | ER/NR | SUNC | Frey St 115kV bus | DISIS STAGE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | BATTERY | 50 | - | - | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 2.78 | - | - | ER/NR | SUNC | Great Bend- Circle 230kV line | DISIS STAGE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 147.22 | - | - | ER/NR | SUNC | Great Bend- Circle 230kV line | DISIS STAGE
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 2.45 | - | - | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 147.55 | - | - | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 2.53 | - | - | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 147.47 | - | - | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | BATTERY | 50 | - | - | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | BATTERY | 180 | - | - | ER | AEPW | Overton-Northwest Henderson 138kV | DISIS STAGE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | BATTERY | 50 | - | - | ER/NR | SUNC | Great Bend - Circle 230kV line | DISIS STAGE
GEN-2019-069 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | - | - | ER | NPPD | Shell Creek-Hoskins 345kV Line | DISIS STAGE
GEN-2019-070 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 50 | - | - | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2019-073 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | - | - | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GIA-100 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 40 | - | - | ER/NR | AECI
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 460 | - | - | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 75 | - | - | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | - | - | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | - | - | ER/NR | AECI
GIA-105 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | - | - | ER/NR | AECI
GIA-99 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 470 | - | - | ER/NR | AECI
MPC4300 | 01 NORTH | 20.5 | DIS-18-2-PQ | WIND | 200 | - | - | ER/NR | OTP
MPC4300 | 01 NORTH | 20.5 | DIS-18-2-PQ | WIND | 200 | - | - | ER/NR | OTP
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | WIND | 40 | - | - | ER | WAPA |  | DISIS STAGE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | - | - | ER | KCPL |  | DISIS STAGE
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | - | - | ER | KCPL |  | DISIS STAGE
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | - | - | ER | KCPL |  | DISIS STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | - | - | ER | KCPL |  | DISIS STAGE
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | - | - | ER | KCPL |  | DISIS STAGE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | - | - | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | - | - | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | WIND | 150 | - | - | ER | SUNC | Cimarron 115kV Substation | IA PENDING
GEN-2018-010 | 01 NORTH | 20 | DIS-18-1 | BATTERY | 74.1 | - | - | ER/NR | BEPC-SPP | Neset 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | BATTERY | 74.1 | - | - | ER/NR | WFEC | Dover 138 kV Switching Station | IA PENDING
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | WIND | 74.1 | - | - | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 126 | - | - | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA PENDING
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 126 | - | - | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA PENDING
GEN-2018-021 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 74.1 | - | - | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | IA PENDING
GEN-2018-022 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 148.5 | - | - | ER/NR | KCPL | Mullen Creek 345kV Substation | DISIS STAGE
GEN-2018-022 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 148.5 | - | - | ER/NR | KCPL | Mullen Creek 345kV Substation | DISIS STAGE
GEN-2018-022 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 3 | - | - | ER/NR | KCPL | Mullen Creek 345kV Substation | DISIS STAGE
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | BATTERY | 100 | - | - | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | BATTERY | 200 | - | - | ER | OPPD | Fort Calhoun 345kV Substation | IA PENDING
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | BATTERY | 100 | - | - | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | BATTERY | 100 | - | - | ER | AEPW | Tulsa Power Station 138kV Substation | IA PENDING
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | BATTERY | 200 | - | - | ER | AEPW | Tulsa North 138kV Substation | IA PENDING
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | BATTERY | 100 | - | - | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | BATTERY | 50 | - | - | ER | KCPL | Blue Valley 161kV Substation | IA PENDING
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | WIND | 155 | - | - | ER | WERE | Neosho 345kV Substation | FACILITY STUDY STAGE
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | WIND | 155 | - | - | ER | WERE | Neosho 345kV Substation | FACILITY STUDY STAGE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | BATTERY | 200 | - | - | ER | OPPD | Cass County 345kV Substation | IA PENDING
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | BATTERY | 100 | - | - | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA PENDING
GEN-2018-039 | 01 NORTH | 20 | DIS-18-1 | Solar | 72 | - | - | ER/NR | WAPA | Edgeley 115kV substation | WITHDRAWN
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 167 | - | - | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA PENDING
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 167 | - | - | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA PENDING
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 166 | - | - | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA PENDING
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | - | - | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | - | - | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | - | - | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | - | - | ER | AEPW | Longwood 345kV Substation | IA PENDING
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | BATTERY | 70 | - | - | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | - | - | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA PENDING
GEN-2018-056 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 102.6 | - | - | ER/NR | WAPA | Grand Prairie 345kV | FACILITY STUDY STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | - | - | ER/NR | WERE | Gordon Evans 138kV | IA PENDING
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | WIND | 50 | - | - | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GIA-96 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | WIND | 97.5 | - | - | ER | AECI
IR39 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | WIND | 12.5 | - | - | ER/NR | ALTW
IR39 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | WIND | 139.38 | - | - | ER/NR | ALTW
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 180 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 290 | - | - | ER/NR | AMMO |  | IA PENDING
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 380 | - | - | ER/NR | AMMO |  | IA PENDING
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER | EES |  | IA PENDING
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | - | - | ER/NR | AMMO |  | IA PENDING
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 250 | - | - | ER/NR | MDU |  | IA PENDING
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | BATTERY | 20 | - | - | ER/NR | XEL |  | IA PENDING
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | WIND | 225 | - | - | ER/NR | ALTW |  | IA PENDING
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | XEL |  | IA PENDING
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | AMMO |  | IA PENDING
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | IA PENDING
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | AMMO |  | IA PENDING
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | IA PENDING
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER | ALTW |  | IA PENDING
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | - | - | ER/NR | AMMO |  | IA PENDING
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 | - | - | ER | ALTW |  | IA PENDING
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER | XEL |  | IA PENDING
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 | - | - | ER/NR | ALTW |  | IA PENDING
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | WIND | 165 | - | - | ER | ALTW |  | IA PENDING
J1181 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 200 | - | - | ER | ALTW |  | IA PENDING
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | - | - | ER/NR | AMMO |  | IA PENDING
J1191 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 64 | - | - | ER/NR | CWLD |  | IA PENDING
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 68.4 | - | - | ER/NR | AMIL |  | IA PENDING
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | BATTERY | 16.6 | - | - | ER/NR | AMIL |  | IA PENDING
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | - | - | ER | CLEC |  | IA PENDING
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | - | - | ER/NR | AMIL |  | IA PENDING
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | - | - | ER/NR | AMIL |  | IA PENDING
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | HYDRO | 30 | - | - | ER/NR | AMMO |  | IA PENDING
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | HYDRO | 30 | - | - | ER/NR | AMMO |  | IA PENDING
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 77.5 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 77.5 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 92.5 | - | - | ER/NR | AMIL |  | IA PENDING
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 92.5 | - | - | ER/NR | AMIL |  | IA PENDING
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | GRE |  | IA PENDING
J1231 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | - | - | ER/NR | BREC |  | IA PENDING
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER | EES |  | IA PENDING
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 165 | - | - | ER/NR | AMIL |  | IA PENDING
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | BATTERY | 50 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | AMMO |  | IA PENDING
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | WIND | 200 | - | - | ER | MEC |  | IA PENDING
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1298 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | ALTW |  | IA PENDING
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 149 | - | - | ER/NR | AMMO |  | IA PENDING
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 95 | - | - | ER/NR | SIPC |  | IA PENDING
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | AMIL |  | IA PENDING
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 75 | - | - | ER/NR | AMIL |  | IA PENDING
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 75 | - | - | ER/NR | AMIL |  | IA PENDING
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | XEL |  | IA PENDING
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | ALTW |  | IA PENDING
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | DPC |  | IA PENDING
J1325 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 40 | - | - | ER/NR | ALTW |  | IA PENDING
J1325 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 40 | - | - | ER/NR | ALTW |  | IA PENDING
J1352 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | AMMO |  | IA PENDING
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | GAS | 47.5 | - | - | ER/NR | ALTW |  | IA PENDING
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | GAS | 47.5 | - | - | ER/NR | ALTW |  | IA PENDING
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | WIND | 169.4 | - | - | ER | ALTW |  | IA PENDING
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | BATTERY | 0 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER | CLEC |  | IA PENDING
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | IA PENDING
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER | EES |  | IA PENDING
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | WIND | 90 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | WIND | 90 | - | - | ER/NR | EES-EAI |  | IA PENDING
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 105 | - | - | ER | EES |  | IA PENDING
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | ALTW |  | IA PENDING
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | IA PENDING
J1474 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 180 | - | - | ER/NR | XEL |  | IA PENDING
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 125 | - | - | ER | OTP |  | IA PENDING
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 125 | - | - | ER | OTP |  | IA PENDING
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 500 | - | - | ER/NR | AMMO |  | IA PENDING
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | WIND | 1000 | - | - | ER/NR | AMMO |  | IA PENDING
J1494 | 01 NORTH | 19.5 | DIS-18-1-PQ | BATTERY | 50 | - | - | ER/NR | XEL |  | NOT STARTED
J1495 | 01 NORTH | 19.5 | DIS-18-1-PQ | BATTERY | 50 | - | - | ER/NR | XEL |  | NOT STARTED
J1498 | 01 NORTH | 19.5 | DIS-18-1-PQ | BATTERY | 50 | - | - | ER/NR | XEL |  | NOT STARTED
J1503 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | ALTW |  | NOT STARTED
J1504 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | ALTW |  | NOT STARTED
J1509 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EMI |  | NOT STARTED
J1514 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1520 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 135 | - | - | ER/NR | ALTW |  | NOT STARTED
J1529 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | MEC |  | NOT STARTED
J1530 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | MEC |  | NOT STARTED
J1532 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | MEC |  | NOT STARTED
J1534 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | NOT STARTED
J1558 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1559 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1562 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 75 | - | - | ER/NR | ALTW |  | NOT STARTED
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 75 | - | - | ER/NR | ALTW |  | NOT STARTED
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | XEL |  | NOT STARTED
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | BATTERY | 61.9 | - | - | ER/NR | XEL |  | NOT STARTED
J1575 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 70 | - | - | ER/NR | OTP |  | NOT STARTED
J1577 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | NOT STARTED
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | NOT STARTED
J1582 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 160 | - | - | ER/NR | XEL |  | NOT STARTED
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | NOT STARTED
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | NOT STARTED
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | WIND | 100 | - | - | ER/NR | MEC |  | NOT STARTED
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | WIND | 100 | - | - | ER/NR | MEC |  | NOT STARTED
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 108.34 | - | - | ER | EES |  | NOT STARTED
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 108.33 | - | - | ER | EES |  | NOT STARTED
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 108.33 | - | - | ER | EES |  | NOT STARTED
J1602 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | BATTERY | 25 | - | - | ER/NR | EES |  | NOT STARTED
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | NOT STARTED
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | XEL |  | NOT STARTED
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 60 | - | - | ER/NR | XEL |  | NOT STARTED
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 60 | - | - | ER/NR | XEL |  | NOT STARTED
J1612 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 62.5 | - | - | ER | XEL |  | NOT STARTED
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 62.5 | - | - | ER | XEL |  | NOT STARTED
J1622 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | OTP |  | NOT STARTED
J1657 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER | XEL |  | NOT STARTED
J1669 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | - | - | ER | EES |  | NOT STARTED
J1670 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1671 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER | EES |  | NOT STARTED
J1672 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | EES-EMI |  | NOT STARTED
J1673 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | - | - | ER/NR | CLEC |  | NOT STARTED
J1709 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | BATTERY | 100 | - | - | ER | EES |  | NOT STARTED
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 107.5 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 19.9 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 172.6 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1723 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | BATTERY | 10 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1730 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 300 | - | - | ER/NR | XEL |  | NOT STARTED
J1747 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | - | - | ER/NR | EES-EMI |  | NOT STARTED
J1748 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EMI |  | NOT STARTED
J1754 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 200 | - | - | ER/NR | GRE |  | NOT STARTED
J1760 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 205 | - | - | ER/NR | EES |  | NOT STARTED
J1769 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 80 | - | - | ER | DPC |  | NOT STARTED
J1808 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 148 | - | - | ER | DPC |  | NOT STARTED
J1816 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1820 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | EES-EAI |  | NOT STARTED
J1826 | 01 NORTH | 19.5 | DIS-18-1-PQ | HYDRO | 4 | - | - | ER | XEL |  | NOT STARTED
J1827 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 90 | - | - | ER/NR | EES |  | NOT STARTED
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | GAS | 54.8 | - | - | ER/NR | EES |  | NOT STARTED
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | GAS | 27.7 | - | - | ER/NR | EES |  | NOT STARTED
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | GAS | 43.5 | - | - | ER/NR | EES |  | NOT STARTED
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | WIND | 135 | - | - | ER | EES-EAI |  | NOT STARTED
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | AMMO |  | IA PENDING
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | AMMO |  | IA PENDING
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 150 | - | - | ER | XEL |  | IA PENDING
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | AMMO |  | IA PENDING
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | - | - | ER/NR | AMMO |  | IA PENDING
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | WIND | 300 | - | - | ER | MEC |  | IA PENDING
J987 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | AMMO |  | IA PENDING
J994 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER/NR | AMMO |  | IA PENDING
MPC3600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER | OTP |  | DISIS STAGE
MPC3600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | - | - | ER | OTP |  | DISIS STAGE
MPC3700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 75 | - | - | ER | OTP |  | DISIS STAGE
MPC3700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 75 | - | - | ER | OTP |  | DISIS STAGE
MPC3800 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 250 | - | - | ER/NR | OTP |  | DISIS STAGE
MPC3900 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 151.2 | - | - | ER/NR | OTP
MPC4000 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 150 | - | - | ER/NR | OTP
MPC4000 | 01 NORTH | 19.5 | DIS-18-1-PQ | WIND | 150 | - | - | ER/NR | OTP
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | WIND | 75 | - | - | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 200 | - | - | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 200 | - | - | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | WIND | 122 | - | - | ER | KCPL | Holt County 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | WIND | 122 | - | - | ER | KCPL | Holt County 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | BATTERY | 19.8 | - | - | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | WIND | 90 | - | - | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | WIND | 90 | - | - | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | WIND | 130 | - | - | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | WIND | 130 | - | - | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | WIND | 100 | - | - | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | WIND | 100 | - | - | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-125 | 03 CENTRAL | 19 | DIS-17-2 | WIND | 252 | - | - | ER/NR | WERE | Swissvale 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-131 | 03 CENTRAL | 19 | DIS-17-2 | BATTERY | 29.6 | - | - | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-132 | 04 SOUTHEAST | 19 | DIS-17-2 | WIND | 200 | - | - | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-132 | 04 SOUTHEAST | 19 | DIS-17-2 | WIND | 200 | - | - | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | WIND | 200 | - | - | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | WIND | 250 | - | - | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | WIND | 295 | - | - | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | - | - | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | - | - | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | WIND | 100 | - | - | ER | WAPA | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | WIND | 100 | - | - | ER | WAPA | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | WIND | 151.8 | - | - | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | WIND | 258 | - | - | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | - | - | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | WIND | 75 | - | - | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | WIND | 75 | - | - | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | WIND | 75 | - | - | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | WIND | 75 | - | - | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-154 | 04 SOUTHEAST | 19 | DIS-17-2 | WIND | 255 | - | - | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | WIND | 132.5 | - | - | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | WIND | 132.5 | - | - | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | - | - | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-167 | 04 SOUTHEAST | 19 | DIS-17-2 | BATTERY | 52 | - | - | ER/NR | OKGE | Sunnyside 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | - | - | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | - | - | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | - | - | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | WIND | 150 | - | - | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | WIND | 150 | - | - | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | BATTERY | 52 | - | - | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | WIND | 300 | - | - | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | WIND | 128 | - | - | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | WIND | 200 | - | - | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | WIND | 200 | - | - | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 200 | - | - | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 200 | - | - | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 75 | - | - | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 75 | - | - | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 65 | - | - | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 65 | - | - | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | - | - | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | BATTERY | 128 | - | - | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | BATTERY | 11.64 | - | - | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | WIND | 250 | - | - | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-202 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 200 | - | - | ER/NR | SWPA | New Madrid - Sikeston 161kV | IA PENDING
GEN-2017-203 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 105 | - | - | ER | OKGE | Renfrow 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-203 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 105 | - | - | ER | OKGE | Renfrow 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-203 | 04 SOUTHEAST | 19 | DIS-17-2 | BATTERY | 35 | - | - | ER | OKGE | Renfrow 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-203 | 04 SOUTHEAST | 19 | DIS-17-2 | BATTERY | 35 | - | - | ER | OKGE | Renfrow 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-209 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 148 | - | - | ER | KCPL | LaCygne - Neosho 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-209 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 152 | - | - | ER | KCPL | LaCygne - Neosho 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-209 | 03 CENTRAL | 19 | DIS-17-2 | BATTERY | 50 | - | - | ER | KCPL | LaCygne - Neosho 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-209 | 03 CENTRAL | 19 | DIS-17-2 | BATTERY | 50 | - | - | ER | KCPL | LaCygne - Neosho 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Solar | 155 | - | - | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Solar | 155 | - | - | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | BATTERY | 50 | - | - | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | BATTERY | 50 | - | - | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | WIND | 100 | - | - | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | WIND | 100 | - | - | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | - | - | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | BATTERY | 152 | - | - | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | WIND | 90 | - | - | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | WIND | 90 | - | - | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | - | - | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | BATTERY | 201.6 | - | - | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | - | - | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | - | - | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | - | - | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | WIND | 215 | - | - | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | WIND | 115 | - | - | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | - | - | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | - | - | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | WIND | 1031 | - | - | ER/NR | AECI
GIA-85 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | BATTERY | 119.28 | - | - | ER/NR | AECI |  | DISIS STAGE
GIA-85 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | BATTERY | 29.82 | - | - | ER/NR | AECI |  | DISIS STAGE
GIA-85 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 119.28 | - | - | ER/NR | AECI |  | DISIS STAGE
GIA-85 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 29.82 | - | - | ER/NR | AECI |  | DISIS STAGE
GIA-85 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | BATTERY | 119.28 | - | - | ER/NR | AECI |  | DISIS STAGE
GIA-85 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 29.82 | - | - | ER/NR | AECI |  | DISIS STAGE
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | - | - | ER/NR | AECI
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | - | - | ER/NR | AECI
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | - | - | ER/NR | AECI
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | - | - | ER/NR | AECI
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | WIND | 128.8 | - | - | ER/NR | AECI
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | WIND | 123.2 | - | - | ER/NR | AECI
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | WIND | 56 | - | - | ER/NR | ALTW
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | WIND | 56 | - | - | ER/NR | ALTW
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | WIND | 110 | - | - | ER | XEL
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | WIND | 200 | - | - | ER | OTP
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | - | - | ER | DPC |  | DISIS STAGE
J803 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 32.5 | - | - | ER | XEL |  | DISIS STAGE
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | WIND | 200 | - | - | ER | ALTW
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | - | - | ER/NR | XEL |  | DISIS STAGE
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 125 | - | - | ER/NR | MEC |  | DISIS STAGE
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 125 | - | - | ER/NR | MEC |  | DISIS STAGE
J897 | 01 NORTH | 18.5 | DIS-17-2-PQ | WIND | 95 | - | - | ER | GRE
J897 | 01 NORTH | 18.5 | DIS-17-2-PQ | WIND | 95 | - | - | ER | GRE
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | WIND | 100 | - | - | ER | DPC
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | WIND | 93.6 | - | - | ER | XEL
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | WIND | 7.68 | - | - | ER | XEL
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | WIND | 300 | - | - | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | WIND | 201.6 | - | - | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | WIND | 190 | - | - | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | WIND | 200.1 | - | - | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | - | - | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | WIND | 138 | - | - | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | WIND | 162 | - | - | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 94 | - | - | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 95 | - | - | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | - | - | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | - | - | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | WIND | 140 | - | - | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | WIND | 100 | - | - | ER/NR | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | WIND | 100 | - | - | ER/NR | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | - | - | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 96.6 | - | - | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 103.5 | - | - | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | WIND | 102 | - | - | ER/NR | SPS | Cole 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | WIND | 300 | - | - | ER | BEPC-SPP | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | - | - | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | - | - | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | - | - | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | - | - | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | - | - | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | - | - | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | - | - | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | - | - | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-076 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | - | - | ER | AEPW | Chamber Springs 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | - | - | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | WIND | 20 | - | - | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | WIND | 130 | - | - | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 80.6 | - | - | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 119.4 | - | - | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | WIND | 100 | - | - | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | WIND | 100 | - | - | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 64 | - | - | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 64 | - | - | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | - | - | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | WIND | 5 | - | - | ER | BEPC-SPP
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | WIND | 90 | - | - | ER | SPS
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | WIND | 40 | - | - | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | WIND | 4.6 | - | - | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | WIND | 200 | - | - | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | WIND | 98.9 | - | - | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 303.6 | - | - | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | WIND | 200 | - | - | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 200 | - | - | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 100 | - | - | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 18.4 | - | - | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 132.5 | - | - | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | WIND | 302 | - | - | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | WIND | 300 | - | - | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 288 | - | - | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 282 | - | - | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 318 | - | - | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | - | - | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 172.5 | - | - | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 176 | - | - | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | WIND | 202 | - | - | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 2.5 | - | - | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 6.12 | - | - | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 187.5 | - | - | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 187.5 | - | - | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 187.5 | - | - | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 137.5 | - | - | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 50 | - | - | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 100 | - | - | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 200 | - | - | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 150 | - | - | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 200 | - | - | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 150 | - | - | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 175 | - | - | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | WIND | 175 | - | - | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | - | - | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | WIND | 302 | - | - | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | WIND | 302 | - | - | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | WIND | 134 | - | - | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | BATTERY | 20 | - | - | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | - | - | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | WIND | 302 | - | - | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | GAS TURBINE | 17 | - | - | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2017-006GIA-53 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | WIND | 238 | - | - | ER/NR | AECI
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | WIND | 0.4 | - | - | ER | SPS
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | WIND | 9.6 | - | - | ER | SPS
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 151.8 | - | - | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 151.8 | - | - | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | WIND | 200 | - | - | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 176 | - | - | ER | OKGE | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 248.4 | - | - | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | WIND | 202 | - | - | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 01 NORTH | 16 | DIS-16-1 | WIND | 100.05 | - | - | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | STEAM TURBINE | 14.5 | - | - | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | STEAM TURBINE | 14.5 | - | - | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-016 | 03 CENTRAL | 16 | DIS-16-1 | WIND | 78.2 | - | - | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 150 | - | - | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 300 | - | - | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | - | - | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 1.5 | - | - | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 200 | - | - | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 230 | - | - | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 186.46 | - | - | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 151 | - | - | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 161.64 | - | - | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | WIND | 149.5 | - | - | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | WIND | 149.5 | - | - | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 250.7 | - | - | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 9.8 | - | - | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 157.3 | - | - | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 175.74 | - | - | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 166.06 | - | - | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 250.7 | - | - | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 200 | - | - | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-070 | 05 SOUTHWEST | 16 | DIS-16-1 | WIND | 5.3 | - | - | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 200.1 | - | - | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-073 | 03 CENTRAL | 16 | DIS-16-1 | WIND | 220 | - | - | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 50 | - | - | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | BATTERY | 20 | - | - | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | WIND | 2.17 | - | - | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | WIND | 200 | - | - | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 04 SOUTHEAST | 15 | DIS-15-2 | WIND | 300 | - | - | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | WIND | 4.5 | - | - | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | WIND | 0.75 | - | - | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | WIND | 248.4 | - | - | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | WIND | 0.75 | - | - | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | WIND | 300 | - | - | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | WIND | 190.36 | - | - | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | WIND | 17.9 | - | - | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | WIND | 11.73 | - | - | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 04 SOUTHEAST | 15 | DIS-15-2 | WIND | 140 | - | - | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | 04 SOUTHEAST | 15 | DIS-15-2 | WIND | 110 | - | - | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 SOUTHEAST | 15 | DIS-15-2 | WIND | 140 | - | - | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 SOUTHEAST | 15 | DIS-15-2 | WIND | 110 | - | - | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 0.2 | - | - | ER | WAPA
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 0.2 | - | - | ER | WAPA
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 0.5 | - | - | ER/NR | BEPC-SPP
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 2 | - | - | ER/NR | WAPA
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 10 | - | - | ER/NR | XEL
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 0.5 | - | - | ER/NR | BEPC-SPP
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 5 | - | - | ER/NR | WAPA
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 0.5 | - | - | ER | BEPC-SPP
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 0.4 | - | - | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 3.5 | - | - | ER/NR | BEPC-SPP
GEN-2014-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | GAS | 5.86 | - | - | ER/NR | BEPC-SPP |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | GAS | 5.86 | - | - | ER/NR | BEPC-SPP |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
MPC2100 | 01 NORTH | 14.5 | DIS-15-2-PQ | WIND | 0.75 | - | - | ER | OTP
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | THERMAL | 6.13 | - | - | ER | SUNC
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | WIND | 16.11 | - | - | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | - | - | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | WIND | 150.36 | - | - | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | WIND | 150.36 | - | - | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | WIND | 208.26 | - | - | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | WIND | 11.73 | - | - | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | WIND | 103.27 | - | - | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | WIND | 103.27 | - | - | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | WIND | 6.72 | - | - | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | WIND | 6.72 | - | - | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | WIND | 2.42 | - | - | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | WIND | 5.11 | - | - | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | WIND | 5.11 | - | - | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | - | - | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | WIND | 26.77 | - | - | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | WIND | 17.23 | - | - | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | WIND | 0.41 | - | - | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | WIND | 1 | - | - | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | WIND | 200.6 | - | - | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | WIND | 10.53 | - | - | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | WIND | 3.96 | - | - | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | WIND | 5.67 | - | - | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | WIND | 0.11 | - | - | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | WIND | 1.65 | - | - | ER | SPS
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | WIND | 73.6 | - | - | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | WIND | 18.4 | - | - | ER | SPS
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | WIND | 18.4 | - | - | ER | SPS
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | WIND | 50.6 | - | - | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | WIND | 1.2 | - | - | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | WIND | 18.15 | - | - | ER | SPS
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | WIND | 1.8 | - | - | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | WIND | 0.72 | - | - | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006GIA-27 | 04 SOUTHEAST | 8 | PQ | WIND | 150 | - | - | ER | AECI
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | STEAM | 22.5 | - | - | ER | SUNC
GEN-2001-039M | 03 CENTRAL | 8 | PQ | WIND | 1 | - | - | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | WIND | 1.5 | - | - | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | WIND | 1.5 | - | - | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | WIND | 1 | - | - | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | WIND | 15 | - | - | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | WIND | 1.8 | - | - | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | WIND | 80 | - | - | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | WIND | 110 | - | - | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | WIND | 100 | - | - | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 8 | DIS-12-1 | WIND | 20.4 | - | - | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 8 | DIS-12-1 | WIND | 20.4 | - | - | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | - | - | ER | NPPD
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | WIND | 10 | - | - | ER | NPPD
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | WIND | 10 | - | - | ER | NPPD
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | WIND | 6.6 | - | - | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | WIND | 2 | - | - | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | WIND | 175 | - | - | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | WIND | 165.6 | - | - | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | WIND | 149.5 | - | - | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | WIND | 149.5 | - | - | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | WIND | 0.15 | - | - | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | WIND | 0.15 | - | - | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | WIND | 0.9 | - | - | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | WIND | 0.9 | - | - | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | WIND | 21.65 | - | - | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | WIND | 13.13 | - | - | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | WIND | 30.4 | - | - | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | WIND | 28.8 | - | - | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | WIND | 177.1 | - | - | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | WIND | 181.7 | - | - | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | WIND | 1 | - | - | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | WIND | 0.2 | - | - | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | WIND | 0.2 | - | - | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 3 | DIS-09-1 | WIND | 200.1 | - | - | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | WIND | 35.2 | - | - | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | WIND | 33.6 | - | - | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | WIND | 0.3 | - | - | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Scenarios
Generation Interconnection Number or Upgrade ID | Assigned Study | Service Type | Point of Interconnection or Upgrade Name | Project Capacity in Winter | Project Capacity in Summer | Steady-State ERIS Status or Available MW in Winter | Steady-State ERIS Status or Available MW in Summer | Steady-State NRIS Status or Available MW in Winter | Steady-State NRIS Status or Available MW in Summer | Stability Capacity Available (MW) for Winter | Stability Capacity Available (MW) for Summer
GEN-2022-009 | DIS-22-1 | ER | Judson Substation 345 kV | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
GEN-2022-010 | DIS-22-1 | ER | Judson Substation 345 kV | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
GEN-2022-083 | DIS-22-1 | ER | Judson Substation 345 kV | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00ALL | ERIS | Non-Converged | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00ALL | ERIS | Thermal | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00ALL | ERIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
01ALL | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None

## All Thermal
SOLUTIONTYPE | GROUP | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converged | 00ALL | N/A | N/A | " | Non-Converge |  |  |  |  | None
Thermal | 00ALL | N/A | N/A | " | None |  |  |  |  | None

## All Voltage
SOLUTION TYPE | GROUP | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00ALL | N/A | N/A | None | [7 empty] | None

## Stability Analysis Results
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
01 NORTH | 25S | Transfer | GROUP1_FAULT_1_P1 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_2_P1 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_3_P1 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_4_P1 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_5_P1 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_6_P1 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_7_P1 | 3 Phase fault on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_8_P1 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_9_P1 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_10_P1 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_11_P1 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_12_P1 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_13_P1 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_14_P1 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_15_P1 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_16_P1 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_17_P1 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_18_P1 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_19_P1 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_20_P1 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_21_P1 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Oscillatory response following the event due to non-convergence of the models of GEN-2018-067. | Disabling the mechanical models of the controllers at GEN-2018-067 resolves the issue. As the issue is also observed in the base case, the issue was not attributed to the study.
01 NORTH | 25S | Transfer | GROUP1_FAULT_22_P1 | 3 Phase fault on N.WILSTN-MW7115.00 (655936) 115 kV Bus a. Apply fault at the N.WILSTN-MW7115.00 (655936) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_23_P1 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to SE.WLSTN-MW7 (655938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_24_P1 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.3. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.4. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_25_P1 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_26_P1 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_27_P1 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_28_P1 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_29_P1 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_30_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. | Reclosing was removed.
01 NORTH | 25S | Transfer | GROUP1_FAULT_31_P1 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_32_P1 | 3 Phase fault on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_33_P1 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_34_P1 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_35_P1 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_36_P1 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_37_P1 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_38_P1 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_39_P1 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_40_P1 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_41_P1 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_42_P1 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_43_P1 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_44_P1 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_45_P1 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_46_P1 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_47_P1 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_48_P1 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_49_P1 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_50_P1 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_51_P1 | 3 Phase fault on MARLEY -LY7115.00 (655793) 115 kV Bus a. Apply fault at the MARLEY -LY7115.00 (655793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLEY -LY7 (655793) 115.0 kV to SANDRSON-LY7 (655794) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_52_P1 | 3 Phase fault on BLUEBUTE-MK7115.00 (655832) 115 kV Bus a. Apply fault at the BLUEBUTE-MK7115.00 (655832) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBUTE-MK7 (655832) 115.0 kV to VEEDER -MK7 (655849) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_53_P1 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to GRASSYBT-MK7 (655834) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_54_P1 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_55_P1 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_56_P1 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to NRTINDHL-MK7 (655850) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_57_P1 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_58_P1 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_59_P1 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_60_P1 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_61_P1 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_62_P1 | 3 Phase fault on BERG -MK7115.00 (655848) 115 kV Bus a. Apply fault at the BERG -MK7115.00 (655848) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG -MK7 (655848) 115.0 kV to BBCOMPTP-MK7 (655873) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_63_P1 | 3 Phase fault on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VEEDER -MK7 (655849) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_64_P1 | 3 Phase fault on ROOSEVLT-MK7115.00 (655855) 115 kV Bus a. Apply fault at the ROOSEVLT-MK7115.00 (655855) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVLT-MK7 (655855) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_65_P1 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_66_P1 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_67_P1 | 3 Phase fault on HORSECRK-MK7115.00 (655861) 115 kV Bus a. Apply fault at the HORSECRK-MK7115.00 (655861) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HORSECRK-MK7 (655861) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_68_P1 | 3 Phase fault on G9______-MK7115.00 (655871) 115 kV Bus a. Apply fault at the G9______-MK7115.00 (655871) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G9______-MK7 (655871) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_69_P1 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to BBCMPRSS-MK7 (655874) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_70_P1 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_71_P1 | 3 Phase fault on DPLWC___-MK7115.00 (655875) 115 kV Bus a. Apply fault at the DPLWC___-MK7115.00 (655875) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWC___-MK7 (655875) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_72_P1 | 3 Phase fault on DPLWCTAP-MK7115.00 (655876) 115 kV Bus a. Apply fault at the DPLWCTAP-MK7115.00 (655876) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWCTAP-MK7 (655876) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_73_P1 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to COYOTCHR-MK7 (655897) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_74_P1 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to FNCYBTAP-MK7 (655899) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_75_P1 | 3 Phase fault on DAP_____-MK7115.00 (655881) 115 kV Bus a. Apply fault at the DAP_____-MK7115.00 (655881) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAP_____-MK7 (655881) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_76_P1 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_77_P1 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_78_P1 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_79_P1 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_80_P1 | 3 Phase fault on FNCYBTAP-MK7115.00 (655899) 115 kV Bus a. Apply fault at the FNCYBTAP-MK7115.00 (655899) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNCYBTAP-MK7 (655899) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_81_P1 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_82_P1 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_83_P1 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_84_P1 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_85_P1 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_86_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_87_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_88_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_89_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_90_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_91_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_92_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_93_P1 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_94_P1 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_95_P1 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_96_P1 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_97_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. | Reclosing was removed.
01 NORTH | 25S | Transfer | GROUP1_FAULT_98_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_99_P1 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_100_P1 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_101_P1 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_102_P1 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_103_P1 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_104_P1 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_105_P1 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_106_P1 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_107_P1 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_108_P1 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_109_P1 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_110_P1 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_111_P1 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_112_P1 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_113_P1 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_114_P1 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_115_P1 | 3 Phase fault on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_116_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_117_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_118_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_119_P1 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_120_P1 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_121_P1 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_122_P1 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_123_P1 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_124_P1 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_125_P1 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_126_P1 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_127_P1 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_128_P1 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_129_P1 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_130_P1 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_1_P1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_2_P1 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_3_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_4_P1 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_5_P1 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_6_P1 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_7_P1 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_8_P1 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_9_P1 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_10_P1 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_11_P1 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_12_P1 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_13_P1 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_14_P1 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_15_P1 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_16_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_17_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_18_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_19_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_20_P1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_21_P1 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.3. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_22_P1 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_23_P1 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_24_P1 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_25_P1 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_26_P1 | 3 Phase fault on NUNDRWD-LNX3230.00 (652884) 230 kV Bus a. Apply fault at the NUNDRWD-LNX3230.00 (652884) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_27_P1 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_28_P1 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_29_P1 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_30_P1 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_31_P1 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_32_P1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_33_P1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_34_P1 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_35_P1 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_36_P1 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_37_P1 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_38_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_39_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_40_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_41_P1 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_42_P1 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_43_P1 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_44_P1 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_45_P1 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_46_P1 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_47_P1 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_48_P1 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_49_P1 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_50_P1 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_51_P1 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_52_P1 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_53_P1 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_54_P1 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_55_P1 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_56_P1 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_57_P1 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_58_P1 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_59_P1 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_60_P1 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_61_P1 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_1_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_2_P4 | Single Phase Fault with Stuck Breaker on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply Fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_3_P4 | Single Phase Fault with Stuck Breaker on LTLMUDY7 115.00 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 115.00 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_4_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_5_P4 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_6_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_7_P4 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_8_P4 | Single Phase Fault with Stuck Breaker on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply Fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.2. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.3. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.4. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.6. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_9_P4 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_10_P4 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_11_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_12_P4 | Single Phase Fault with Stuck Breaker on WATFORD7 115.00 (652408) 115 kV Bus a. Apply Fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD7 (652408) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_13_P4 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_14_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 b.3. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 b.4. CCR.KV3A-BE9 (659318) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #1 b.5. CCR.KV4A-BE9 (659319) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_15_P4 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_16_P4 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_17_P4 | Single Phase Fault with Stuck Breaker on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply Fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_18_P4 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | Yes | No | Yes | Oscillatory response following the event due to non-convergence of the models of GEN-2018-067. | Disabling the mechanical models of the controllers at GEN-2018-067 resolves the issue. As the issue is also observed in the base case, the issue was not attributed to the study.
01 NORTH | 25S | Transfer | GROUP1_FAULT_19_P4 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_20_P4 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | Yes | No | Yes | Oscillatory response following the event due to non-convergence of the models of GEN-2018-067. | Disabling the mechanical models of the controllers at GEN-2018-067 resolves the issue. As the issue is also observed in the base case, the issue was not attributed to the study.
01 NORTH | 25S | Transfer | GROUP1_FAULT_21_P4 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_22_P4 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_23_P4 | Single Phase Fault with Stuck Breaker on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply Fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit #1 b.3. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_24_P4 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_25_P4 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.4. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_26_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_27_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_28_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_29_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_30_P4 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_31_P4 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_32_P4 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_33_P4 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.3. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_34_P4 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.3. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_35_P4 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_36_P4 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_37_P4 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_38_P4 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.9. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 b.10. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_39_P4 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_40_P4 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_41_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_42_P4 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_43_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to WATFORD4 (652216) 230.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.2. WATFORD7 (652408) 115.0 kV to WATFORD4 (652216) 230.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_44_P4 | Single Phase Fault with Stuck Breaker on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply Fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VEEDER -MK7 (655849) 115.0 kV to BLUEBUTE-MK7 (655832) 115.0 kV Transmission Circuit #1 b.2. VEEDER -MK7 (655849) 115.0 kV to DAP_____-MK7 (655881) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_45_P4 | Single Phase Fault with Stuck Breaker on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply Fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON -MW7 (655925) 115.0 kV to STATELIN-MW7 (655924) 115.0 kV Transmission Circuit #1 b.2. JUDSON -MW7 (655925) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_46_P4 | Single Phase Fault with Stuck Breaker on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply Fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.2. NE.WLSTN-MW7 (655937) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_47_P4 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_48_P4 | Single Phase Fault with Stuck Breaker on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply Fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_49_P4 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_50_P4 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_51_P4 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 b.2. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_52_P4 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 b.2. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_53_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_54_P4 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 b.2. PATENTGT-BE3 (659390) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_55_P4 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EFORK_-BE334 (659600) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_56_P4 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_57_P4 | Single Phase Fault with Stuck Breaker on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply Fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CULBSN.E-BE7 (659262) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #1 b.2. CULBSN.E-BE7 (659262) 115.0 kV to SNAKEBTT-SH7 (655778) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_58_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_59_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_60_P4 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EASTFORK-MW7 (655957) 115.0 kV to N.MISRDG-MW7 (655933) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_61_P4 | Single Phase Fault with Stuck Breaker on EFORK_-BE334 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_62_P4 | Single Phase Fault with Stuck Breaker on EASTFORK-MW7 (655957) 115 kV Bus a. Apply Fault at the EASTFORK-MW7 (655957) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_63_P4 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_64_P4 | Single Phase Fault with Stuck Breaker on WILISTN4 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_65_P4 | Single Phase Fault with Stuck Breaker on WILLISTON27 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_66_P4 | Single Phase Fault with Stuck Breaker on WILISTN7 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_67_P4 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_68_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_69_P4 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_70_P4 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7 (659391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_71_P4 | Single Phase Fault with Stuck Breaker on LC_SWY.N-BE7 (659349) 115 kV Bus a. Apply Fault at the LC_SWY.N-BE7 (659349) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_72_P4 | Single Phase Fault with Stuck Breaker on TIMBERCK-MK7 (655844) 115 kV Bus a. Apply Fault at the TIMBERCK-MK7 (655844) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_73_P4 | Single Phase Fault with Stuck Breaker on KUMMERDG-MK7 (659388) 115 kV Bus a. Apply Fault at the KUMMERDG-MK7 (659388) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_74_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_FAULT_75_P4 | Single Phase Fault with Stuck Breaker on WATFORD7 (652408) 115 kV Bus a. Apply Fault at the WATFORD7 (652408) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_1_P4 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_2_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_3_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_4_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_5_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_6_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_7_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_8_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_9_P4 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_10_P4 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_11_P4 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_12_P4 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_13_P4 | Single Phase Fault with Stuck Breaker on MAPLE R3 345.00 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 345.00 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.4. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_14_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_15_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_16_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_17_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_18_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_19_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_20_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.3. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_21_P4 | Single Phase Fault with Stuck Breaker on BROWNSV4 230.00 (620325) 230 kV Bus a. Apply Fault at the BROWNSV4 230.00 (620325) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 41.6 kV Transmission Circuit #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_22_P4 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_23_P4 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_24_P4 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_25_P4 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.2. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.5. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.6. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.7. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.8. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.11. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.12. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.14. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.15. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.19. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.20. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.21. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.23. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_26_P4 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_27_P4 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_28_P4 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_29_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_30_P4 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_31_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_32_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_33_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_34_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_35_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_36_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_37_P4 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. RUGBY T (620179) 13.8 kV to RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_38_P4 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. HRDLKCOL9 (620114) 34.5 kV to G380 RUGBY W (620115) 0.6 kV Two Winding #1 b.3. HRDLKCOL9 (620114) 34.5 kV to RGBYCOL9 (620168) 34.5 kV Transmission Circuit #1 b.4. RGBYWND4 (620368) 230.0 kV to RGBYCOL9 (620168) 34.5 kV Two Winding #1 b.5. RGBYWND4 (620368) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_39_P4 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_40_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_41_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_42_P4 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_43_P4 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_44_P4 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_45_P4 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_46_P4 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_47_P4 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_48_P4 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_49_P4 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_50_P4 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_51_P4 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_52_P4 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_53_P4 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_54_P4 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_55_P4 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_56_P4 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_57_P4 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_58_P4 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_59_P4 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_60_P4 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_61_P4 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4230.00 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4230.00 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_62_P4 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_63_P4 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_64_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_65_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_66_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_67_P4 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_68_P4 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_69_P4 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_70_P4 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_71_P4 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_72_P4 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_73_P4 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_74_P4 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_75_P4 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_76_P4 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_77_P4 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_78_P4 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_79_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_80_P4 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_81_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_82_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_83_P4 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_84_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_85_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_86_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_87_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_88_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_89_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_90_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_91_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_92_P4 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_93_P4 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_94_P4 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_95_P4 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_96_P4 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_97_P4 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_98_P4 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_99_P4 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.3. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.4. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.5. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.7. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_100_P4 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_101_P4 | Single Phase Fault with Stuck Breaker on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply Fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_102_P4 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_103_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_104_P4 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_105_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_106_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_107_P4 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_108_P4 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_109_P4 | Single Phase Fault with Stuck Breaker on ASTORIA 3 345.00 (620483) 345 kV Bus a. Apply Fault at the ASTORIA 3 345.00 (620483) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASTORIA 3 (620483) 345.0 kV to BRKNGCO3 (601031) 345.0 kV Transmission Circuit #1 b.2. ASTORIA 3 (620483) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_110_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_111_P4 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to CSLTNET7 (620180) 115.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_112_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_113_P4 | Single Phase Fault with Stuck Breaker on TWIN BRKS 3 (620416) 345 kV Bus a. Apply Fault at the TWIN BRKS 3 (620416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_114_P4 | Single Phase Fault with Stuck Breaker on BSSOUTH3 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_115_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_117_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_118_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_119_P4 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_120_P4 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_121_P4 | Single Phase Fault with Stuck Breaker on ASTORIA 3 (620483) 345 kV Bus a. Apply Fault at the ASTORIA 3 (620483) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASTORIA 3 (620483) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_122_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_123_P4 | Single Phase Fault with Stuck Breaker on BUFFALO7 (620258) 115 kV Bus a. Apply Fault at the BUFFALO7 (620258) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_124_P4 | Single Phase Fault with Stuck Breaker on BLAIR-ER8 (655466) 69 kV Bus a. Apply Fault at the BLAIR-ER8 (655466) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER8 (655466) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Transfer | GROUP1_REGIONAL_FAULT_125_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 7 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_1_P1 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_2_P1 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_3_P1 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_4_P1 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_5_P1 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_6_P1 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_7_P1 | 3 Phase fault on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_8_P1 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_9_P1 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_10_P1 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_11_P1 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_12_P1 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_13_P1 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_14_P1 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_15_P1 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_16_P1 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_17_P1 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_18_P1 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_19_P1 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_20_P1 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_21_P1 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Oscillatory response following the event due to non-convergence of the models of GEN-2018-067. | Disabling the mechanical models of the controllers at GEN-2018-067 resolves the issue. As the issue is also observed in the base case, the issue was not attributed to the study.
01 NORTH | 25W | Transfer | GROUP1_FAULT_22_P1 | 3 Phase fault on N.WILSTN-MW7115.00 (655936) 115 kV Bus a. Apply fault at the N.WILSTN-MW7115.00 (655936) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_23_P1 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to SE.WLSTN-MW7 (655938) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_24_P1 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.3. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.4. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_25_P1 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_26_P1 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_27_P1 | 3 Phase fault on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_28_P1 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_29_P1 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_30_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_31_P1 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_32_P1 | 3 Phase fault on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_33_P1 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_34_P1 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_35_P1 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_36_P1 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_37_P1 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_38_P1 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_39_P1 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_40_P1 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_41_P1 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_42_P1 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_43_P1 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_44_P1 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_45_P1 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_46_P1 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_47_P1 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_48_P1 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_49_P1 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_50_P1 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_51_P1 | 3 Phase fault on MARLEY -LY7115.00 (655793) 115 kV Bus a. Apply fault at the MARLEY -LY7115.00 (655793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARLEY -LY7 (655793) 115.0 kV to SANDRSON-LY7 (655794) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_52_P1 | 3 Phase fault on BLUEBUTE-MK7115.00 (655832) 115 kV Bus a. Apply fault at the BLUEBUTE-MK7115.00 (655832) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBUTE-MK7 (655832) 115.0 kV to VEEDER -MK7 (655849) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_53_P1 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to GRASSYBT-MK7 (655834) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_54_P1 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_55_P1 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_56_P1 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to NRTINDHL-MK7 (655850) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_57_P1 | 3 Phase fault on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_58_P1 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_59_P1 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_60_P1 | 3 Phase fault on GRDNCRK2-MK7115.00 (655845) 115 kV Bus a. Apply fault at the GRDNCRK2-MK7115.00 (655845) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCRK2-MK7 (655845) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_61_P1 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_62_P1 | 3 Phase fault on BERG -MK7115.00 (655848) 115 kV Bus a. Apply fault at the BERG -MK7115.00 (655848) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG -MK7 (655848) 115.0 kV to BBCOMPTP-MK7 (655873) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_63_P1 | 3 Phase fault on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VEEDER -MK7 (655849) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_64_P1 | 3 Phase fault on ROOSEVLT-MK7115.00 (655855) 115 kV Bus a. Apply fault at the ROOSEVLT-MK7115.00 (655855) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVLT-MK7 (655855) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_65_P1 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_66_P1 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_67_P1 | 3 Phase fault on HORSECRK-MK7115.00 (655861) 115 kV Bus a. Apply fault at the HORSECRK-MK7115.00 (655861) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HORSECRK-MK7 (655861) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_68_P1 | 3 Phase fault on G9______-MK7115.00 (655871) 115 kV Bus a. Apply fault at the G9______-MK7115.00 (655871) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G9______-MK7 (655871) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_69_P1 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to BBCMPRSS-MK7 (655874) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_70_P1 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_71_P1 | 3 Phase fault on DPLWC___-MK7115.00 (655875) 115 kV Bus a. Apply fault at the DPLWC___-MK7115.00 (655875) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWC___-MK7 (655875) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_72_P1 | 3 Phase fault on DPLWCTAP-MK7115.00 (655876) 115 kV Bus a. Apply fault at the DPLWCTAP-MK7115.00 (655876) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DPLWCTAP-MK7 (655876) 115.0 kV to LITTLMS4-MK7 (655877) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_73_P1 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to COYOTCHR-MK7 (655897) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_74_P1 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to FNCYBTAP-MK7 (655899) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_75_P1 | 3 Phase fault on DAP_____-MK7115.00 (655881) 115 kV Bus a. Apply fault at the DAP_____-MK7115.00 (655881) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAP_____-MK7 (655881) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_76_P1 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_77_P1 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_78_P1 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_79_P1 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_80_P1 | 3 Phase fault on FNCYBTAP-MK7115.00 (655899) 115 kV Bus a. Apply fault at the FNCYBTAP-MK7115.00 (655899) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNCYBTAP-MK7 (655899) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_81_P1 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_82_P1 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_83_P1 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_84_P1 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_85_P1 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_86_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_87_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_88_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_89_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_90_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_91_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_92_P1 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_93_P1 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_94_P1 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_95_P1 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_96_P1 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_97_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_98_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_99_P1 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_100_P1 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_101_P1 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_102_P1 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_103_P1 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_104_P1 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_105_P1 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_106_P1 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_107_P1 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_108_P1 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_109_P1 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_110_P1 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_111_P1 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_112_P1 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_113_P1 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_114_P1 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_115_P1 | 3 Phase fault on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_116_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_117_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_118_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_119_P1 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_120_P1 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_121_P1 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_122_P1 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_123_P1 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_124_P1 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_125_P1 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_126_P1 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_127_P1 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_128_P1 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_129_P1 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_130_P1 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_1_P1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_2_P1 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_3_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_4_P1 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_5_P1 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_6_P1 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_7_P1 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_8_P1 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_9_P1 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_10_P1 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_11_P1 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_12_P1 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_13_P1 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_14_P1 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_15_P1 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_16_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_17_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_18_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_19_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_20_P1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_21_P1 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.3. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.4. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_22_P1 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_23_P1 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_24_P1 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_25_P1 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_26_P1 | 3 Phase fault on NUNDRWD-LNX3230.00 (652884) 230 kV Bus a. Apply fault at the NUNDRWD-LNX3230.00 (652884) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_27_P1 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_28_P1 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_29_P1 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_30_P1 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_31_P1 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_32_P1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_33_P1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_34_P1 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_35_P1 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_36_P1 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_37_P1 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_38_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_39_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_40_P1 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_41_P1 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_42_P1 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_43_P1 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_44_P1 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_45_P1 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_46_P1 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_47_P1 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_48_P1 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_49_P1 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_50_P1 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_51_P1 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_52_P1 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_53_P1 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_54_P1 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_55_P1 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_56_P1 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_57_P1 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_58_P1 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_59_P1 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_60_P1 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_61_P1 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_1_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_2_P4 | Single Phase Fault with Stuck Breaker on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply Fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_3_P4 | Single Phase Fault with Stuck Breaker on LTLMUDY7 115.00 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 115.00 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_4_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_5_P4 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_6_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_7_P4 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_8_P4 | Single Phase Fault with Stuck Breaker on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply Fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.2. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.3. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.4. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.6. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_9_P4 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_10_P4 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_11_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_12_P4 | Single Phase Fault with Stuck Breaker on WATFORD7 115.00 (652408) 115 kV Bus a. Apply Fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD7 (652408) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_13_P4 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_14_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 b.3. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 b.4. CCR.KV3A-BE9 (659318) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #1 b.5. CCR.KV4A-BE9 (659319) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_15_P4 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_16_P4 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_17_P4 | Single Phase Fault with Stuck Breaker on SNAKEBTT-SH7115.00 (655778) 115 kV Bus a. Apply Fault at the SNAKEBTT-SH7115.00 (655778) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SNAKEBTT-SH7 (655778) 115.0 kV to REDBANK -SH7 (655779) 115.0 kV Transmission Circuit #1 b.2. SNAKEBTT-SH7 (655778) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 b.3. SNAKEBTT-SH7 (655778) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. SNAKEBTT-SH7 (655778) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_18_P4 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | Yes | No | Yes | Oscillatory response following the event due to non-convergence of the models of GEN-2018-067. | Disabling the mechanical models of the controllers at GEN-2018-067 resolves the issue. As the issue is also observed in the base case, the issue was not attributed to the study.
01 NORTH | 25W | Transfer | GROUP1_FAULT_19_P4 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_20_P4 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | Yes | No | Yes | Oscillatory response following the event due to non-convergence of the models of GEN-2018-067. | Disabling the mechanical models of the controllers at GEN-2018-067 resolves the issue. As the issue is also observed in the base case, the issue was not attributed to the study.
01 NORTH | 25W | Transfer | GROUP1_FAULT_21_P4 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_22_P4 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_23_P4 | Single Phase Fault with Stuck Breaker on CHRRYCRK-MK7115.00 (655840) 115 kV Bus a. Apply Fault at the CHRRYCRK-MK7115.00 (655840) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit #1 b.3. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_24_P4 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_25_P4 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.4. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_26_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_27_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_28_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_29_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.3. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_30_P4 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_31_P4 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_32_P4 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_33_P4 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.3. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_34_P4 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.3. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_35_P4 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_36_P4 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_37_P4 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_38_P4 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.9. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 b.10. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_39_P4 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_40_P4 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_41_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_42_P4 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_43_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to WATFORD4 (652216) 230.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.2. WATFORD7 (652408) 115.0 kV to WATFORD4 (652216) 230.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_44_P4 | Single Phase Fault with Stuck Breaker on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply Fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VEEDER -MK7 (655849) 115.0 kV to BLUEBUTE-MK7 (655832) 115.0 kV Transmission Circuit #1 b.2. VEEDER -MK7 (655849) 115.0 kV to DAP_____-MK7 (655881) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_45_P4 | Single Phase Fault with Stuck Breaker on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply Fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON -MW7 (655925) 115.0 kV to STATELIN-MW7 (655924) 115.0 kV Transmission Circuit #1 b.2. JUDSON -MW7 (655925) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_46_P4 | Single Phase Fault with Stuck Breaker on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply Fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.2. NE.WLSTN-MW7 (655937) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_47_P4 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_48_P4 | Single Phase Fault with Stuck Breaker on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply Fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 b.2. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_49_P4 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_50_P4 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_51_P4 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 b.2. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_52_P4 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 b.2. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_53_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_54_P4 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 b.2. PATENTGT-BE3 (659390) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_55_P4 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EFORK_-BE334 (659600) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_56_P4 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_57_P4 | Single Phase Fault with Stuck Breaker on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply Fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CULBSN.E-BE7 (659262) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #1 b.2. CULBSN.E-BE7 (659262) 115.0 kV to SNAKEBTT-SH7 (655778) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_58_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_59_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_60_P4 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 b.2. EASTFORK-MW7 (655957) 115.0 kV to N.MISRDG-MW7 (655933) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_61_P4 | Single Phase Fault with Stuck Breaker on EFORK_-BE334 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EFORK_-BE334 (659600) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_62_P4 | Single Phase Fault with Stuck Breaker on EASTFORK-MW7 (655957) 115 kV Bus a. Apply Fault at the EASTFORK-MW7 (655957) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_63_P4 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_64_P4 | Single Phase Fault with Stuck Breaker on WILISTN4 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_65_P4 | Single Phase Fault with Stuck Breaker on WILLISTON27 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_66_P4 | Single Phase Fault with Stuck Breaker on WILISTN7 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_67_P4 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_68_P4 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_69_P4 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_70_P4 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7 (659391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_71_P4 | Single Phase Fault with Stuck Breaker on LC_SWY.N-BE7 (659349) 115 kV Bus a. Apply Fault at the LC_SWY.N-BE7 (659349) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_72_P4 | Single Phase Fault with Stuck Breaker on TIMBERCK-MK7 (655844) 115 kV Bus a. Apply Fault at the TIMBERCK-MK7 (655844) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_73_P4 | Single Phase Fault with Stuck Breaker on KUMMERDG-MK7 (659388) 115 kV Bus a. Apply Fault at the KUMMERDG-MK7 (659388) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_74_P4 | Single Phase Fault with Stuck Breaker on WATFORD4 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_FAULT_75_P4 | Single Phase Fault with Stuck Breaker on WATFORD7 (652408) 115 kV Bus a. Apply Fault at the WATFORD7 (652408) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_1_P4 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_2_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_3_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_4_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_5_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_6_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_7_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_8_P4 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_9_P4 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_10_P4 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_11_P4 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_12_P4 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS108 (605666) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_13_P4 | Single Phase Fault with Stuck Breaker on MAPLE R3 345.00 (620361) 345 kV Bus a. Apply Fault at the MAPLE R3 345.00 (620361) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BISON 3 (601067) 345.0 kV to MAPLE R3 (620361) 345.0 kV Transmission Circuit #1 b.3. MAPLER19 (620359) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #1 b.4. MAPLER29 (620360) 13.8 kV to MAPLE R3 (620361) 345.0 kV to MAPLE R4 (657754) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_14_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE1 9 (605740) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #5 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE1 9 (605740) 13.8 kV Three Winding #5 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_15_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRAYTON4 (657752) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_16_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_17_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRAIRIE2 9 (605741) 13.8 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE7 (657712) 115.0 kV Three Winding #8 b.2. PRAIRIE7 (657712) 115.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIRIE2 9 (605741) 13.8 kV Three Winding #8 b.4. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_18_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_19_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 b.3. PRAIRIE4 (657755) 230.0 kV to PRAIRIE3 (657946) 345.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_20_P4 | Single Phase Fault with Stuck Breaker on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply Fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 b.3. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_21_P4 | Single Phase Fault with Stuck Breaker on BROWNSV4 230.00 (620325) 230 kV Bus a. Apply Fault at the BROWNSV4 230.00 (620325) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROWNSV9 (620125) 41.6 kV to SUMMIT-9 (652326) 41.6 kV Transmission Circuit #2 b.2. BIGSTON4 (620314) 230.0 kV to BROWNSV4 (620325) 230.0 kV Transmission Circuit #1 b.3. BROWNSV4 (620325) 230.0 kV to BROWNSV9 (620125) 41.6 kV Two Winding #1 b.4. BROWNSV4 (620325) 230.0 kV to NEW EFFNGTN4 (620328) 230.0 kV Transmission Circuit #1 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_22_P4 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_23_P4 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_24_P4 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO9 (620158) 41.6 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV Three Winding #1 b.3. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_25_P4 | Single Phase Fault with Stuck Breaker on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply Fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.2. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 b.3. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.4. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.5. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.6. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.7. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.8. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.10. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.11. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.12. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.13. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.14. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.15. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.18. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.19. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.20. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.21. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #1 b.22. JAMSTN 9 (620169) 41.6 kV to JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV Three Winding #2 b.23. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.24. JAMSTWN7 (620269) 115.0 kV to JAMESTN3 (620369) 345.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_26_P4 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSS1 34.5 (620320) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #1 b.2. BSS2 34.5 (620321) 34.5 kV to BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV Three Winding #2 b.3. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 b.4. BSSOUTH4 (620322) 230.0 kV to BSSOUTH3 (620417) 345.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_27_P4 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.4. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_28_P4 | Single Phase Fault with Stuck Breaker on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply Fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.6. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z b.7. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_29_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_30_P4 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.6. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_31_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. TIOGA4 9 (661900) 13.8 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_32_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_33_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_34_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_35_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_36_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_37_P4 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. RUGBY T (620179) 13.8 kV to RUGBY 4 (620379) 230.0 kV to RUGBY_RB-CP7 (655660) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_38_P4 | Single Phase Fault with Stuck Breaker on RUGBY 4 230.00 (620379) 230 kV Bus a. Apply Fault at the RUGBY 4 230.00 (620379) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 b.2. HRDLKCOL9 (620114) 34.5 kV to G380 RUGBY W (620115) 0.6 kV Two Winding #1 b.3. HRDLKCOL9 (620114) 34.5 kV to RGBYCOL9 (620168) 34.5 kV Transmission Circuit #1 b.4. RGBYWND4 (620368) 230.0 kV to RGBYCOL9 (620168) 34.5 kV Two Winding #1 b.5. RGBYWND4 (620368) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_39_P4 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 b.2. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.3. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.4. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_40_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_41_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_42_P4 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.2. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_43_P4 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.2. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.3. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 b.4. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_44_P4 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.2. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.3. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 b.4. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_45_P4 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_46_P4 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_47_P4 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_48_P4 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_49_P4 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_50_P4 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD10 (652266) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_51_P4 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.4. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.5. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.6. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_52_P4 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_53_P4 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_54_P4 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.7. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_55_P4 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_56_P4 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.5. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.7. MAURINE9 (652247) 13.8 kV to MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_57_P4 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_58_P4 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | High Voltage recovery issue at the MI City HVDC Pole after tripping the HVDC Line | Tripping the shunt at MI City bus with the contingency action solves the issue and results in a stable response
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_59_P4 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | High Voltage recovery issue at the MI City HVDC Pole after tripping the HVDC Line | Tripping the shunt at MI City bus with the contingency action solves the issue and results in a stable response
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_60_P4 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE9 (652217) 13.8 kV to MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_61_P4 | Single Phase Fault with Stuck Breaker on PHILIP__-BE4230.00 (659192) 230 kV Bus a. Apply Fault at the PHILIP__-BE4230.00 (659192) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.5. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_62_P4 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_63_P4 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_64_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 9 (652293) 13.8 kV to WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_65_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_66_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_67_P4 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.4. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_68_P4 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_69_P4 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_70_P4 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.10. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.12. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_71_P4 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.5. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.6. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.7. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.8. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.9. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_72_P4 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.5. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_73_P4 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.4. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.5. GRANITF4 (652550) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_74_P4 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD9 (652267) 13.8 kV to NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_75_P4 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_76_P4 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.3. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_77_P4 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_78_P4 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_79_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_80_P4 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_81_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_82_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_83_P4 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_84_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_85_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_86_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_87_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_88_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_89_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_90_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_91_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_92_P4 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_93_P4 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_94_P4 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_95_P4 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.3. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.4. WAYSIDE4 (640404) 230.0 kV to WAYSIDE7 (640405) 115.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_96_P4 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_97_P4 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_98_P4 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.5. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_99_P4 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.3. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.4. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.5. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.7. FARGOSVC (652434) 13.2 kV to FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_100_P4 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.6. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.10. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_101_P4 | Single Phase Fault with Stuck Breaker on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply Fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 b.2. TWIN BRKS 3 (620416) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_102_P4 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 b.2. BSSOUTH3 (620417) 345.0 kV to TWIN BRKS 3 (620416) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_103_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_104_P4 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_105_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_106_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_107_P4 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BISON 3 (601067) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_108_P4 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. BLAIR-ER4 (655465) 230.0 kV to BIGSTON4 (620314) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_109_P4 | Single Phase Fault with Stuck Breaker on ASTORIA 3 345.00 (620483) 345 kV Bus a. Apply Fault at the ASTORIA 3 345.00 (620483) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASTORIA 3 (620483) 345.0 kV to BRKNGCO3 (601031) 345.0 kV Transmission Circuit #1 b.2. ASTORIA 3 (620483) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_110_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_111_P4 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to CSLTNET7 (620180) 115.0 kV Transmission Circuit #1 b.2. BUFFALO7 (620258) 115.0 kV to BUFFALO3 (620358) 345.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_112_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_113_P4 | Single Phase Fault with Stuck Breaker on TWIN BRKS 3 (620416) 345 kV Bus a. Apply Fault at the TWIN BRKS 3 (620416) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_114_P4 | Single Phase Fault with Stuck Breaker on BSSOUTH3 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_115_P4 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_117_P4 | Single Phase Fault with Stuck Breaker on WHITE 3 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHITE 3 (652537) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_118_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 4 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_119_P4 | Single Phase Fault with Stuck Breaker on BUFFALO3 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_120_P4 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER4 (655465) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_121_P4 | Single Phase Fault with Stuck Breaker on ASTORIA 3 (620483) 345 kV Bus a. Apply Fault at the ASTORIA 3 (620483) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASTORIA 3 (620483) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_122_P4 | Single Phase Fault with Stuck Breaker on FTRANDL4 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_123_P4 | Single Phase Fault with Stuck Breaker on BUFFALO7 (620258) 115 kV Bus a. Apply Fault at the BUFFALO7 (620258) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (620258) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_124_P4 | Single Phase Fault with Stuck Breaker on BLAIR-ER8 (655466) 69 kV Bus a. Apply Fault at the BLAIR-ER8 (655466) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAIR-ER8 (655466) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25W | Transfer | GROUP1_REGIONAL_FAULT_125_P4 | Single Phase Fault with Stuck Breaker on TIOGA4 7 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | 25S | Base | GROUP1_FAULT_21_P1 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Oscillatory response following the event due to non-convergence of the models of GEN-2018-067. | Disabling the mechanical models of the controllers at GEN-2018-067 resolves the issue. As the issue is also observed in the base case, the issue was not attributed to the study.
01 NORTH | 25W | Base | GROUP1_FAULT_21_P1 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Oscillatory response following the event due to non-convergence of the models of GEN-2018-067. | Disabling the mechanical models of the controllers at GEN-2018-067 resolves the issue. As the issue is also observed in the base case, the issue was not attributed to the study.
01 NORTH | 25S | Base | GROUP1_FAULT_30_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. | Reclosing was removed.
01 NORTH | 25S | Base | GROUP1_FAULT_97_P1 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to non-convergence. | Reclosing was removed.
01 NORTH | 25W | Base | GROUP1_REGIONAL_FAULT_58_P4 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | High Voltage recovery issue at the MI City HVDC Pole after tripping the HVDC Line | Tripping the shunt at MI City bus with the contingency action solves the issue and results in a stable response
01 NORTH | 25W | Base | GROUP1_REGIONAL_FAULT_59_P4 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.5. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | High Voltage recovery issue at the MI City HVDC Pole after tripping the HVDC Line | Tripping the shunt at MI City bus with the contingency action solves the issue and results in a stable response

## Short Circuit Analysis Results
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2022-009 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.6737 | 7.676 | 0.0023
GEN-2022-009 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 13.0371 | 13.0524 | 0.0153
GEN-2022-009 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 10.4818 | 10.5419 | 0.0601
GEN-2022-009 | 01 NORTH | 652216 | WATFORD4 | 230 | 7.2858 | 7.3309 | 0.0451
GEN-2022-009 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.1043 | 1.1043 | 0
GEN-2022-009 | 01 NORTH | 652391 | WILLISTON27 | 115 | 20.7022 | 20.9326 | 0.2304
GEN-2022-009 | 01 NORTH | 652400 | WILISTN4 | 230 | 13.4722 | 13.8272 | 0.355
GEN-2022-009 | 01 NORTH | 652408 | WATFORD7 | 115 | 9.2893 | 9.3155 | 0.0262
GEN-2022-009 | 01 NORTH | 652419 | KILDEER7 | 115 | 5.0931 | 5.0966 | 0.0035
GEN-2022-009 | 01 NORTH | 652421 | WILISTN7 | 115 | 20.687 | 20.9167 | 0.2297
GEN-2022-009 | 01 NORTH | 652424 | BELFELD3 | 345 | 7.096 | 7.1194 | 0.0234
GEN-2022-009 | 01 NORTH | 652425 | BELFELD4 | 230 | 9.9121 | 9.9328 | 0.0207
GEN-2022-009 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 5.0996 | 5.1051 | 0.0055
GEN-2022-009 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9759 | 0.9759 | 0
GEN-2022-009 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.9029 | 0.9029 | 0
GEN-2022-009 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.9097 | 0.9097 | 0
GEN-2022-009 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.6895 | 0.6895 | 0
GEN-2022-009 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6177 | 0.6177 | 0
GEN-2022-009 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1105 | 1.1105 | 0
GEN-2022-009 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.1164 | 1.1164 | 0
GEN-2022-009 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.1076 | 1.1076 | 0
GEN-2022-009 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5143 | 1.5143 | 0
GEN-2022-009 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.0234 | 1.0235 | 0.0001
GEN-2022-009 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9909 | 0.9909 | 0
GEN-2022-009 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.9913 | 0.9913 | 0
GEN-2022-009 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.552 | 1.552 | 0
GEN-2022-009 | 01 NORTH | 655778 | SNAKEBTT-SH7 | 115 | 8.0997 | 8.1132 | 0.0135
GEN-2022-009 | 01 NORTH | 655779 | REDBANK -SH7 | 115 | 4.7842 | 4.7889 | 0.0047
GEN-2022-009 | 01 NORTH | 655790 | HELMUT -LY7 | 115 | 5.7859 | 5.7903 | 0.0044
GEN-2022-009 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 1.9949 | 1.9958 | 0.0009
GEN-2022-009 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.6021 | 3.6049 | 0.0028
GEN-2022-009 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 6.9469 | 6.9726 | 0.0257
GEN-2022-009 | 01 NORTH | 655794 | SANDRSON-LY7 | 115 | 3.5458 | 3.5525 | 0.0067
GEN-2022-009 | 01 NORTH | 655795 | ROMO -LY7 | 115 | 2.9383 | 2.9429 | 0.0046
GEN-2022-009 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.2192 | 4.2236 | 0.0044
GEN-2022-009 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 4.1052 | 4.1121 | 0.0069
GEN-2022-009 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 8.1533 | 8.181 | 0.0277
GEN-2022-009 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 14.4323 | 14.4792 | 0.0469
GEN-2022-009 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 7.0203 | 7.0313 | 0.011
GEN-2022-009 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.1441 | 3.1466 | 0.0025
GEN-2022-009 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.6062 | 5.6139 | 0.0077
GEN-2022-009 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.6966 | 3.7022 | 0.0056
GEN-2022-009 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.128 | 4.1376 | 0.0096
GEN-2022-009 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 9.2893 | 9.3155 | 0.0262
GEN-2022-009 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 7.5429 | 7.5523 | 0.0094
GEN-2022-009 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.3083 | 3.3145 | 0.0062
GEN-2022-009 | 01 NORTH | 655843 | TRUEOIL -MK7 | 115 | 1.6273 | 1.6277 | 0.0004
GEN-2022-009 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.3464 | 5.3625 | 0.0161
GEN-2022-009 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.8171 | 4.8242 | 0.0071
GEN-2022-009 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.2334 | 4.2435 | 0.0101
GEN-2022-009 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 4.37 | 4.3779 | 0.0079
GEN-2022-009 | 01 NORTH | 655848 | BERG -MK7 | 115 | 5.8257 | 5.8398 | 0.0141
GEN-2022-009 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 10.0845 | 10.127 | 0.0425
GEN-2022-009 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.5152 | 3.5222 | 0.007
GEN-2022-009 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9324 | 2.9345 | 0.0021
GEN-2022-009 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5929 | 3.5961 | 0.0032
GEN-2022-009 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.5126 | 8.5304 | 0.0178
GEN-2022-009 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.5608 | 3.5661 | 0.0053
GEN-2022-009 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.9688 | 4.9763 | 0.0075
GEN-2022-009 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.6602 | 6.6852 | 0.025
GEN-2022-009 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.6081 | 2.6109 | 0.0028
GEN-2022-009 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 4.4028 | 4.4109 | 0.0081
GEN-2022-009 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.7758 | 3.7817 | 0.0059
GEN-2022-009 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.3395 | 2.3426 | 0.0031
GEN-2022-009 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.1669 | 3.1725 | 0.0056
GEN-2022-009 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 5.84 | 5.8542 | 0.0142
GEN-2022-009 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 5.9917 | 6.0067 | 0.015
GEN-2022-009 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 4.1133 | 4.1204 | 0.0071
GEN-2022-009 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 3.023 | 3.0281 | 0.0051
GEN-2022-009 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.7846 | 2.7889 | 0.0043
GEN-2022-009 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6822 | 2.6862 | 0.004
GEN-2022-009 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.9769 | 3.9858 | 0.0089
GEN-2022-009 | 01 NORTH | 655872 | G9TAP___-MK7 | 115 | 4.6106 | 4.6225 | 0.0119
GEN-2022-009 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 7.0897 | 7.1106 | 0.0209
GEN-2022-009 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 6.4641 | 6.4815 | 0.0174
GEN-2022-009 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 8.0606 | 8.0803 | 0.0197
GEN-2022-009 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.9097 | 8.9339 | 0.0242
GEN-2022-009 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.4654 | 5.4745 | 0.0091
GEN-2022-009 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 4.0329 | 4.0379 | 0.005
GEN-2022-009 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.8554 | 4.8626 | 0.0072
GEN-2022-009 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 5.8594 | 5.8737 | 0.0143
GEN-2022-009 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 13.5502 | 13.627 | 0.0768
GEN-2022-009 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 10.1366 | 10.1796 | 0.043
GEN-2022-009 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 7.9432 | 7.9695 | 0.0263
GEN-2022-009 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 5.5156 | 5.5283 | 0.0127
GEN-2022-009 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 4.2909 | 4.2985 | 0.0076
GEN-2022-009 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 5.1223 | 5.1331 | 0.0108
GEN-2022-009 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.4926 | 3.4995 | 0.0069
GEN-2022-009 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.3864 | 6.4094 | 0.023
GEN-2022-009 | 01 NORTH | 655891 | KILLDEER-MK7 | 115 | 4.9194 | 4.9227 | 0.0033
GEN-2022-009 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 4.073 | 4.0823 | 0.0093
GEN-2022-009 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.339 | 6.3489 | 0.0099
GEN-2022-009 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.5737 | 3.5768 | 0.0031
GEN-2022-009 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.4311 | 4.4371 | 0.006
GEN-2022-009 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.4866 | 3.4916 | 0.005
GEN-2022-009 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 5.3763 | 5.3883 | 0.012
GEN-2022-009 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1817 | 3.1847 | 0.003
GEN-2022-009 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 6.5065 | 6.5241 | 0.0176
GEN-2022-009 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 21.2779 | 21.3656 | 0.0877
GEN-2022-009 | 01 NORTH | 655924 | STATELIN-MW7 | 115 | 16.2294 | 16.293 | 0.0636
GEN-2022-009 | 01 NORTH | 655925 | JUDSON -MW7 | 115 | 15.9623 | 16.0867 | 0.1244
GEN-2022-009 | 01 NORTH | 655926 | SW.WLSTN-MW7 | 115 | 8.8937 | 8.9322 | 0.0385
GEN-2022-009 | 01 NORTH | 655931 | BLKTLTAP-MW7 | 115 | 8.1249 | 8.1714 | 0.0465
GEN-2022-009 | 01 NORTH | 655933 | N.MISRDG-MW7 | 115 | 15.9775 | 16.1365 | 0.159
GEN-2022-009 | 01 NORTH | 655934 | N.WLST_T-MW7 | 115 | 14.564 | 14.6962 | 0.1322
GEN-2022-009 | 01 NORTH | 655935 | NW.WLSTN-MW7 | 115 | 12.9177 | 13.0177 | 0.1
GEN-2022-009 | 01 NORTH | 655936 | N.WILSTN-MW7 | 115 | 14.2158 | 14.3424 | 0.1266
GEN-2022-009 | 01 NORTH | 655937 | NE.WLSTN-MW7 | 115 | 13.2014 | 13.3139 | 0.1125
GEN-2022-009 | 01 NORTH | 655938 | SE.WLSTN-MW7 | 115 | 8.5077 | 8.552 | 0.0443
GEN-2022-009 | 01 NORTH | 655940 | MONT -MW7 | 115 | 16.196 | 16.3059 | 0.1099
GEN-2022-009 | 01 NORTH | 655941 | STRNDAHL-MW7 | 115 | 7.5108 | 7.5256 | 0.0148
GEN-2022-009 | 01 NORTH | 655945 | WHEELS_T-MW7 | 115 | 9.363 | 9.4078 | 0.0448
GEN-2022-009 | 01 NORTH | 655955 | ZAHL -MW7 | 115 | 6.7429 | 6.7734 | 0.0305
GEN-2022-009 | 01 NORTH | 655956 | TYRONE -MW7 | 115 | 10.9198 | 11.0073 | 0.0875
GEN-2022-009 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 17.9807 | 18.2272 | 0.2465
GEN-2022-009 | 01 NORTH | 655958 | FOLVAG -MW7 | 115 | 14.3957 | 14.5473 | 0.1516
GEN-2022-009 | 01 NORTH | 655966 | OLIVER -MW7 | 115 | 6.8822 | 6.909 | 0.0268
GEN-2022-009 | 01 NORTH | 659060 | FINSTAD345 | 345 | 7.6435 | 7.6786 | 0.0351
GEN-2022-009 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 20.7554 | 20.8155 | 0.0601
GEN-2022-009 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 20.1693 | 20.2067 | 0.0374
GEN-2022-009 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 25.9182 | 25.9489 | 0.0307
GEN-2022-009 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.4312 | 5.4319 | 0.0007
GEN-2022-009 | 01 NORTH | 659112 | CULBRTSN-UM7 | 115 | 5.6288 | 5.6336 | 0.0048
GEN-2022-009 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 7.3222 | 7.3299 | 0.0077
GEN-2022-009 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 14.1087 | 14.2248 | 0.1161
GEN-2022-009 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 6.3673 | 6.3799 | 0.0126
GEN-2022-009 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 5.8274 | 5.8318 | 0.0044
GEN-2022-009 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 7.7871 | 7.7928 | 0.0057
GEN-2022-009 | 01 NORTH | 659181 | BICNTNIL-BE7 | 115 | 3.4478 | 3.4498 | 0.002
GEN-2022-009 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 14.5606 | 14.6083 | 0.0477
GEN-2022-009 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 11.7029 | 11.8078 | 0.1049
GEN-2022-009 | 01 NORTH | 659184 | ROUGHRDR-BE7 | 115 | 4.4426 | 4.4464 | 0.0038
GEN-2022-009 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.7636 | 3.7667 | 0.0031
GEN-2022-009 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 23.4559 | 23.4808 | 0.0249
GEN-2022-009 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 19.5948 | 19.6484 | 0.0536
GEN-2022-009 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 20.7554 | 20.8155 | 0.0601
GEN-2022-009 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.8934 | 9.8961 | 0.0027
GEN-2022-009 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.7327 | 7.7382 | 0.0055
GEN-2022-009 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.415 | 7.4165 | 0.0015
GEN-2022-009 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.5282 | 5.5332 | 0.005
GEN-2022-009 | 01 NORTH | 659248 | HALLIDAY-UM7 | 115 | 4.1691 | 4.1704 | 0.0013
GEN-2022-009 | 01 NORTH | 659262 | CULBSN.E-BE7 | 115 | 8.3408 | 8.3523 | 0.0115
GEN-2022-009 | 01 NORTH | 659269 | CULB_GEN-BE7 | 115 | 7.5832 | 7.5911 | 0.0079
GEN-2022-009 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 12.4095 | 12.4946 | 0.0851
GEN-2022-009 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.316 | 2.3165 | 0.0005
GEN-2022-009 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 9.9121 | 9.9328 | 0.0207
GEN-2022-009 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 11.5785 | 12.2497 | 0.6712
GEN-2022-009 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 13.5919 | 13.9972 | 0.4053
GEN-2022-009 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 9.6643 | 9.7674 | 0.1031
GEN-2022-009 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 13.9019 | 14.0176 | 0.1157
GEN-2022-009 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 7.759 | 7.7648 | 0.0058
GEN-2022-009 | 01 NORTH | 659347 | PIONEER1-BE7 | 115 | 16.2294 | 16.293 | 0.0636
GEN-2022-009 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 12.6714 | 12.7341 | 0.0627
GEN-2022-009 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 12.6716 | 12.7342 | 0.0626
GEN-2022-009 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 8.3854 | 8.4626 | 0.0772
GEN-2022-009 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 9.5998 | 9.6485 | 0.0487
GEN-2022-009 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 10.5053 | 10.5873 | 0.082
GEN-2022-009 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 12.3042 | 12.3415 | 0.0373
GEN-2022-009 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 8.0293 | 8.1106 | 0.0813
GEN-2022-009 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 15.0876 | 15.1829 | 0.0953
GEN-2022-009 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 10.201 | 10.4115 | 0.2105
GEN-2022-009 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 19.418 | 19.6323 | 0.2143
GEN-2022-009 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 5.0632 | 5.0893 | 0.0261
GEN-2022-009 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 20.7554 | 20.8155 | 0.0601
GEN-2022-009 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.823 | 4.8233 | 0.0003
GEN-2022-009 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 20.1693 | 20.2067 | 0.0374
GEN-2022-009 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 20.1693 | 20.2067 | 0.0374
GEN-2022-009 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 9.6643 | 9.7674 | 0.1031
GEN-2022-009 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.9402 | 1.9406 | 0.0004
GEN-2022-009 | 01 NORTH | 659443 | SKUNKHIL-RR7 | 115 | 1.7453 | 1.7457 | 0.0004
GEN-2022-009 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.7132 | 6.7203 | 0.0071
GEN-2022-009 | 01 NORTH | 659450 | BRADYWND 4 | 230 | 3.648 | 3.6496 | 0.0016
GEN-2022-009 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 19.314 | 19.5273 | 0.2133
GEN-2022-009 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 19.3265 | 19.5399 | 0.2134
GEN-2022-009 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 6.7288 | 6.7752 | 0.0464
GEN-2022-009 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.9402 | 1.9406 | 0.0004
GEN-2022-009 | 01 NORTH | 659576 | BEPCPRXCC1 3 | 345 | 19.8506 | 19.9041 | 0.0535
GEN-2022-009 | 01 NORTH | 659584 | BEPCPRXCC3 7 | 115 | 14.8189 | 14.9109 | 0.092
GEN-2022-009 | 01 NORTH | 659600 | EFORK_-BE334 | 345 | 9.4172 | 9.6972 | 0.28
GEN-2022-009 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 7.2045 | 7.2486 | 0.0441
GEN-2022-009 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 14.1087 | 14.2248 | 0.1161
GEN-2022-009 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 13.9897 | 14.0428 | 0.0531
GEN-2022-009 | 01 NORTH | 661087 | RAY JCT7 | 115 | 5.964 | 5.9763 | 0.0123
GEN-2022-009 | 01 NORTH | 661089 | LTLMUDY7 | 115 | 7.2434 | 7.2675 | 0.0241
GEN-2022-009 | 01 NORTH | 672603 | BDV 4 | 230 | 5.0771 | 5.0816 | 0.0045
GEN-2022-009 | 01 NORTH | 763021 | GEN-2018-067 | 115 | 7.5108 | 7.5256 | 0.0148
GEN-2022-009 | 01 NORTH | 763703 | GEN-2019-037 | 345 | 12.1851 | 12.1983 | 0.0132
GEN-2022-009 | 01 NORTH | 765050 | PIONEER_-BE3 | 345 | 9.2464 | 10.2016 | 0.9552
GEN-2022-010 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.6718 | 7.676 | 0.0042
GEN-2022-010 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 13.0248 | 13.0524 | 0.0276
GEN-2022-010 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 10.4337 | 10.5419 | 0.1082
GEN-2022-010 | 01 NORTH | 652216 | WATFORD4 | 230 | 7.2497 | 7.3309 | 0.0812
GEN-2022-010 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.1042 | 1.1043 | 0.0001
GEN-2022-010 | 01 NORTH | 652391 | WILLISTON27 | 115 | 20.5198 | 20.9326 | 0.4128
GEN-2022-010 | 01 NORTH | 652400 | WILISTN4 | 230 | 13.1984 | 13.8272 | 0.6288
GEN-2022-010 | 01 NORTH | 652408 | WATFORD7 | 115 | 9.2682 | 9.3155 | 0.0473
GEN-2022-010 | 01 NORTH | 652419 | KILDEER7 | 115 | 5.0903 | 5.0966 | 0.0063
GEN-2022-010 | 01 NORTH | 652421 | WILISTN7 | 115 | 20.505 | 20.9167 | 0.4117
GEN-2022-010 | 01 NORTH | 652424 | BELFELD3 | 345 | 7.0771 | 7.1194 | 0.0423
GEN-2022-010 | 01 NORTH | 652425 | BELFELD4 | 230 | 9.8955 | 9.9328 | 0.0373
GEN-2022-010 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 5.0951 | 5.1051 | 0.01
GEN-2022-010 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9758 | 0.9759 | 0.0001
GEN-2022-010 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.9029 | 0.9029 | 0
GEN-2022-010 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.9097 | 0.9097 | 0
GEN-2022-010 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.6895 | 0.6895 | 0
GEN-2022-010 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6177 | 0.6177 | 0
GEN-2022-010 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1105 | 1.1105 | 0
GEN-2022-010 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.1164 | 1.1164 | 0
GEN-2022-010 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.1075 | 1.1076 | 0.0001
GEN-2022-010 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5142 | 1.5143 | 0.0001
GEN-2022-010 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.0234 | 1.0235 | 0.0001
GEN-2022-010 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9909 | 0.9909 | 0
GEN-2022-010 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.9913 | 0.9913 | 0
GEN-2022-010 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.5519 | 1.552 | 0.0001
GEN-2022-010 | 01 NORTH | 655778 | SNAKEBTT-SH7 | 115 | 8.0888 | 8.1132 | 0.0244
GEN-2022-010 | 01 NORTH | 655779 | REDBANK -SH7 | 115 | 4.7804 | 4.7889 | 0.0085
GEN-2022-010 | 01 NORTH | 655790 | HELMUT -LY7 | 115 | 5.7824 | 5.7903 | 0.0079
GEN-2022-010 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 1.9942 | 1.9958 | 0.0016
GEN-2022-010 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.5999 | 3.6049 | 0.005
GEN-2022-010 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 6.9262 | 6.9726 | 0.0464
GEN-2022-010 | 01 NORTH | 655794 | SANDRSON-LY7 | 115 | 3.5404 | 3.5525 | 0.0121
GEN-2022-010 | 01 NORTH | 655795 | ROMO -LY7 | 115 | 2.9346 | 2.9429 | 0.0083
GEN-2022-010 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.2157 | 4.2236 | 0.0079
GEN-2022-010 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 4.0995 | 4.1121 | 0.0126
GEN-2022-010 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 8.131 | 8.181 | 0.05
GEN-2022-010 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 14.3947 | 14.4792 | 0.0845
GEN-2022-010 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 7.0113 | 7.0313 | 0.02
GEN-2022-010 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.1422 | 3.1466 | 0.0044
GEN-2022-010 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.6 | 5.6139 | 0.0139
GEN-2022-010 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.692 | 3.7022 | 0.0102
GEN-2022-010 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.1203 | 4.1376 | 0.0173
GEN-2022-010 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 9.2682 | 9.3155 | 0.0473
GEN-2022-010 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 7.5354 | 7.5523 | 0.0169
GEN-2022-010 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.3034 | 3.3145 | 0.0111
GEN-2022-010 | 01 NORTH | 655843 | TRUEOIL -MK7 | 115 | 1.627 | 1.6277 | 0.0007
GEN-2022-010 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.3334 | 5.3625 | 0.0291
GEN-2022-010 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.8115 | 4.8242 | 0.0127
GEN-2022-010 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.2253 | 4.2435 | 0.0182
GEN-2022-010 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 4.3636 | 4.3779 | 0.0143
GEN-2022-010 | 01 NORTH | 655848 | BERG -MK7 | 115 | 5.8144 | 5.8398 | 0.0254
GEN-2022-010 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 10.0504 | 10.127 | 0.0766
GEN-2022-010 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.5096 | 3.5222 | 0.0126
GEN-2022-010 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9307 | 2.9345 | 0.0038
GEN-2022-010 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5904 | 3.5961 | 0.0057
GEN-2022-010 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.4982 | 8.5304 | 0.0322
GEN-2022-010 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.5566 | 3.5661 | 0.0095
GEN-2022-010 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.9627 | 4.9763 | 0.0136
GEN-2022-010 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.6401 | 6.6852 | 0.0451
GEN-2022-010 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.6058 | 2.6109 | 0.0051
GEN-2022-010 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 4.3963 | 4.4109 | 0.0146
GEN-2022-010 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.7711 | 3.7817 | 0.0106
GEN-2022-010 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.337 | 2.3426 | 0.0056
GEN-2022-010 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.1624 | 3.1725 | 0.0101
GEN-2022-010 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 5.8286 | 5.8542 | 0.0256
GEN-2022-010 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 5.9797 | 6.0067 | 0.027
GEN-2022-010 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 4.1077 | 4.1204 | 0.0127
GEN-2022-010 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 3.0188 | 3.0281 | 0.0093
GEN-2022-010 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.781 | 2.7889 | 0.0079
GEN-2022-010 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6789 | 2.6862 | 0.0073
GEN-2022-010 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.9698 | 3.9858 | 0.016
GEN-2022-010 | 01 NORTH | 655872 | G9TAP___-MK7 | 115 | 4.6009 | 4.6225 | 0.0216
GEN-2022-010 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 7.0728 | 7.1106 | 0.0378
GEN-2022-010 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 6.4501 | 6.4815 | 0.0314
GEN-2022-010 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 8.0447 | 8.0803 | 0.0356
GEN-2022-010 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.8903 | 8.9339 | 0.0436
GEN-2022-010 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.4581 | 5.4745 | 0.0164
GEN-2022-010 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 4.0289 | 4.0379 | 0.009
GEN-2022-010 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.8496 | 4.8626 | 0.013
GEN-2022-010 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 5.848 | 5.8737 | 0.0257
GEN-2022-010 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 13.4887 | 13.627 | 0.1383
GEN-2022-010 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 10.1022 | 10.1796 | 0.0774
GEN-2022-010 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 7.922 | 7.9695 | 0.0475
GEN-2022-010 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 5.5054 | 5.5283 | 0.0229
GEN-2022-010 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 4.2848 | 4.2985 | 0.0137
GEN-2022-010 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 5.1135 | 5.1331 | 0.0196
GEN-2022-010 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.4871 | 3.4995 | 0.0124
GEN-2022-010 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.3679 | 6.4094 | 0.0415
GEN-2022-010 | 01 NORTH | 655891 | KILLDEER-MK7 | 115 | 4.9167 | 4.9227 | 0.006
GEN-2022-010 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 4.0655 | 4.0823 | 0.0168
GEN-2022-010 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.331 | 6.3489 | 0.0179
GEN-2022-010 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.5712 | 3.5768 | 0.0056
GEN-2022-010 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.4263 | 4.4371 | 0.0108
GEN-2022-010 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.4825 | 3.4916 | 0.0091
GEN-2022-010 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 5.3666 | 5.3883 | 0.0217
GEN-2022-010 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1792 | 3.1847 | 0.0055
GEN-2022-010 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 6.4924 | 6.5241 | 0.0317
GEN-2022-010 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 21.2075 | 21.3656 | 0.1581
GEN-2022-010 | 01 NORTH | 655924 | STATELIN-MW7 | 115 | 16.1784 | 16.293 | 0.1146
GEN-2022-010 | 01 NORTH | 655925 | JUDSON -MW7 | 115 | 15.8631 | 16.0867 | 0.2236
GEN-2022-010 | 01 NORTH | 655926 | SW.WLSTN-MW7 | 115 | 8.8628 | 8.9322 | 0.0694
GEN-2022-010 | 01 NORTH | 655931 | BLKTLTAP-MW7 | 115 | 8.0877 | 8.1714 | 0.0837
GEN-2022-010 | 01 NORTH | 655933 | N.MISRDG-MW7 | 115 | 15.8514 | 16.1365 | 0.2851
GEN-2022-010 | 01 NORTH | 655934 | N.WLST_T-MW7 | 115 | 14.4589 | 14.6962 | 0.2373
GEN-2022-010 | 01 NORTH | 655935 | NW.WLSTN-MW7 | 115 | 12.8379 | 13.0177 | 0.1798
GEN-2022-010 | 01 NORTH | 655936 | N.WILSTN-MW7 | 115 | 14.1151 | 14.3424 | 0.2273
GEN-2022-010 | 01 NORTH | 655937 | NE.WLSTN-MW7 | 115 | 13.1118 | 13.3139 | 0.2021
GEN-2022-010 | 01 NORTH | 655938 | SE.WLSTN-MW7 | 115 | 8.4723 | 8.552 | 0.0797
GEN-2022-010 | 01 NORTH | 655940 | MONT -MW7 | 115 | 16.1082 | 16.3059 | 0.1977
GEN-2022-010 | 01 NORTH | 655941 | STRNDAHL-MW7 | 115 | 7.4988 | 7.5256 | 0.0268
GEN-2022-010 | 01 NORTH | 655945 | WHEELS_T-MW7 | 115 | 9.3271 | 9.4078 | 0.0807
GEN-2022-010 | 01 NORTH | 655955 | ZAHL -MW7 | 115 | 6.7184 | 6.7734 | 0.055
GEN-2022-010 | 01 NORTH | 655956 | TYRONE -MW7 | 115 | 10.8502 | 11.0073 | 0.1571
GEN-2022-010 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 17.7863 | 18.2272 | 0.4409
GEN-2022-010 | 01 NORTH | 655958 | FOLVAG -MW7 | 115 | 14.2754 | 14.5473 | 0.2719
GEN-2022-010 | 01 NORTH | 655966 | OLIVER -MW7 | 115 | 6.8606 | 6.909 | 0.0484
GEN-2022-010 | 01 NORTH | 659060 | FINSTAD345 | 345 | 7.6153 | 7.6786 | 0.0633
GEN-2022-010 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 20.7071 | 20.8155 | 0.1084
GEN-2022-010 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 20.1391 | 20.2067 | 0.0676
GEN-2022-010 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 25.8935 | 25.9489 | 0.0554
GEN-2022-010 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.4307 | 5.4319 | 0.0012
GEN-2022-010 | 01 NORTH | 659112 | CULBRTSN-UM7 | 115 | 5.6249 | 5.6336 | 0.0087
GEN-2022-010 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 7.3161 | 7.3299 | 0.0138
GEN-2022-010 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 14.0163 | 14.2248 | 0.2085
GEN-2022-010 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 6.3572 | 6.3799 | 0.0227
GEN-2022-010 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 5.8239 | 5.8318 | 0.0079
GEN-2022-010 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 7.7826 | 7.7928 | 0.0102
GEN-2022-010 | 01 NORTH | 659181 | BICNTNIL-BE7 | 115 | 3.4461 | 3.4498 | 0.0037
GEN-2022-010 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 14.5223 | 14.6083 | 0.086
GEN-2022-010 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 11.6194 | 11.8078 | 0.1884
GEN-2022-010 | 01 NORTH | 659184 | ROUGHRDR-BE7 | 115 | 4.4395 | 4.4464 | 0.0069
GEN-2022-010 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.761 | 3.7667 | 0.0057
GEN-2022-010 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 23.4357 | 23.4808 | 0.0451
GEN-2022-010 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 19.5518 | 19.6484 | 0.0966
GEN-2022-010 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 20.7071 | 20.8155 | 0.1084
GEN-2022-010 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.8912 | 9.8961 | 0.0049
GEN-2022-010 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.7282 | 7.7382 | 0.01
GEN-2022-010 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.4137 | 7.4165 | 0.0028
GEN-2022-010 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.5241 | 5.5332 | 0.0091
GEN-2022-010 | 01 NORTH | 659248 | HALLIDAY-UM7 | 115 | 4.168 | 4.1704 | 0.0024
GEN-2022-010 | 01 NORTH | 659262 | CULBSN.E-BE7 | 115 | 8.3315 | 8.3523 | 0.0208
GEN-2022-010 | 01 NORTH | 659269 | CULB_GEN-BE7 | 115 | 7.5768 | 7.5911 | 0.0143
GEN-2022-010 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 12.3417 | 12.4946 | 0.1529
GEN-2022-010 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.3155 | 2.3165 | 0.001
GEN-2022-010 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 9.8955 | 9.9328 | 0.0373
GEN-2022-010 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 11.0876 | 12.2497 | 1.1621
GEN-2022-010 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 13.2812 | 13.9972 | 0.716
GEN-2022-010 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 9.5826 | 9.7674 | 0.1848
GEN-2022-010 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 13.8098 | 14.0176 | 0.2078
GEN-2022-010 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 7.7543 | 7.7648 | 0.0105
GEN-2022-010 | 01 NORTH | 659347 | PIONEER1-BE7 | 115 | 16.1784 | 16.293 | 0.1146
GEN-2022-010 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 12.6212 | 12.7341 | 0.1129
GEN-2022-010 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 12.6213 | 12.7342 | 0.1129
GEN-2022-010 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 8.3241 | 8.4626 | 0.1385
GEN-2022-010 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 9.5608 | 9.6485 | 0.0877
GEN-2022-010 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 10.4399 | 10.5873 | 0.1474
GEN-2022-010 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 12.2743 | 12.3415 | 0.0672
GEN-2022-010 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 7.9647 | 8.1106 | 0.1459
GEN-2022-010 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 15.0114 | 15.1829 | 0.1715
GEN-2022-010 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 10.0371 | 10.4115 | 0.3744
GEN-2022-010 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 19.2482 | 19.6323 | 0.3841
GEN-2022-010 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 5.0424 | 5.0893 | 0.0469
GEN-2022-010 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 20.7071 | 20.8155 | 0.1084
GEN-2022-010 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.8227 | 4.8233 | 0.0006
GEN-2022-010 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 20.1391 | 20.2067 | 0.0676
GEN-2022-010 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 20.1391 | 20.2067 | 0.0676
GEN-2022-010 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 9.5826 | 9.7674 | 0.1848
GEN-2022-010 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.9398 | 1.9406 | 0.0008
GEN-2022-010 | 01 NORTH | 659443 | SKUNKHIL-RR7 | 115 | 1.7451 | 1.7457 | 0.0006
GEN-2022-010 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.7075 | 6.7203 | 0.0128
GEN-2022-010 | 01 NORTH | 659450 | BRADYWND 4 | 230 | 3.6468 | 3.6496 | 0.0028
GEN-2022-010 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 19.145 | 19.5273 | 0.3823
GEN-2022-010 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 19.1573 | 19.5399 | 0.3826
GEN-2022-010 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 6.6918 | 6.7752 | 0.0834
GEN-2022-010 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.9398 | 1.9406 | 0.0008
GEN-2022-010 | 01 NORTH | 659576 | BEPCPRXCC1 3 | 345 | 19.8076 | 19.9041 | 0.0965
GEN-2022-010 | 01 NORTH | 659584 | BEPCPRXCC3 7 | 115 | 14.7454 | 14.9109 | 0.1655
GEN-2022-010 | 01 NORTH | 659600 | EFORK_-BE334 | 345 | 9.2025 | 9.6972 | 0.4947
GEN-2022-010 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 7.1692 | 7.2486 | 0.0794
GEN-2022-010 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 14.0163 | 14.2248 | 0.2085
GEN-2022-010 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 13.947 | 14.0428 | 0.0958
GEN-2022-010 | 01 NORTH | 661087 | RAY JCT7 | 115 | 5.9541 | 5.9763 | 0.0222
GEN-2022-010 | 01 NORTH | 661089 | LTLMUDY7 | 115 | 7.224 | 7.2675 | 0.0435
GEN-2022-010 | 01 NORTH | 672603 | BDV 4 | 230 | 5.0734 | 5.0816 | 0.0082
GEN-2022-010 | 01 NORTH | 763021 | GEN-2018-067 | 115 | 7.4988 | 7.5256 | 0.0268
GEN-2022-010 | 01 NORTH | 763703 | GEN-2019-037 | 345 | 12.1744 | 12.1983 | 0.0239
GEN-2022-010 | 01 NORTH | 765050 | PIONEER_-BE3 | 345 | 8.5959 | 10.2016 | 1.6057
GEN-2022-083 | 01 NORTH | 587030 | GEN-2016-004 | 230 | 7.6718 | 7.676 | 0.0042
GEN-2022-083 | 01 NORTH | 588210 | GEN-2016-130 | 345 | 13.0248 | 13.0524 | 0.0276
GEN-2022-083 | 01 NORTH | 588870 | GEN-2017-048 | 230 | 10.4337 | 10.5419 | 0.1082
GEN-2022-083 | 01 NORTH | 652216 | WATFORD4 | 230 | 7.2497 | 7.3309 | 0.0812
GEN-2022-083 | 01 NORTH | 652257 | DEVAUL 8 | 69 | 1.1042 | 1.1043 | 0.0001
GEN-2022-083 | 01 NORTH | 652391 | WILLISTON27 | 115 | 20.5198 | 20.9326 | 0.4128
GEN-2022-083 | 01 NORTH | 652400 | WILISTN4 | 230 | 13.1984 | 13.8272 | 0.6288
GEN-2022-083 | 01 NORTH | 652408 | WATFORD7 | 115 | 9.2682 | 9.3155 | 0.0473
GEN-2022-083 | 01 NORTH | 652419 | KILDEER7 | 115 | 5.0903 | 5.0966 | 0.0063
GEN-2022-083 | 01 NORTH | 652421 | WILISTN7 | 115 | 20.505 | 20.9167 | 0.4117
GEN-2022-083 | 01 NORTH | 652424 | BELFELD3 | 345 | 7.0771 | 7.1194 | 0.0423
GEN-2022-083 | 01 NORTH | 652425 | BELFELD4 | 230 | 9.8955 | 9.9328 | 0.0373
GEN-2022-083 | 01 NORTH | 652651 | FAIRVIEW 7 | 115 | 5.0951 | 5.1051 | 0.01
GEN-2022-083 | 01 NORTH | 655731 | LARK -MG8 | 69 | 0.9758 | 0.9759 | 0.0001
GEN-2022-083 | 01 NORTH | 655732 | FLASHER -MG8 | 69 | 0.9029 | 0.9029 | 0
GEN-2022-083 | 01 NORTH | 655740 | CANNON -MG8 | 69 | 0.9097 | 0.9097 | 0
GEN-2022-083 | 01 NORTH | 655741 | CEDAR -MG8 | 69 | 0.6895 | 0.6895 | 0
GEN-2022-083 | 01 NORTH | 655742 | GRANT -MG8 | 69 | 0.6177 | 0.6177 | 0
GEN-2022-083 | 01 NORTH | 655744 | DEVALTP -MG8 | 69 | 1.1105 | 1.1105 | 0
GEN-2022-083 | 01 NORTH | 655746 | DEVAUL -MG8 | 69 | 1.1164 | 1.1164 | 0
GEN-2022-083 | 01 NORTH | 655747 | DEVAUL -MG7 | 115 | 1.1075 | 1.1076 | 0.0001
GEN-2022-083 | 01 NORTH | 655748 | NEWSALEM-MG7 | 115 | 1.5142 | 1.5143 | 0.0001
GEN-2022-083 | 01 NORTH | 655749 | MANSWTCH-MG7 | 115 | 1.0234 | 1.0235 | 0.0001
GEN-2022-083 | 01 NORTH | 655750 | ROUGHRDR-MG7 | 115 | 0.9909 | 0.9909 | 0
GEN-2022-083 | 01 NORTH | 655751 | NRWSTMDN-MG7 | 115 | 0.9913 | 0.9913 | 0
GEN-2022-083 | 01 NORTH | 655752 | NWMDNTAP-MG7 | 115 | 1.5519 | 1.552 | 0.0001
GEN-2022-083 | 01 NORTH | 655778 | SNAKEBTT-SH7 | 115 | 8.0888 | 8.1132 | 0.0244
GEN-2022-083 | 01 NORTH | 655779 | REDBANK -SH7 | 115 | 4.7804 | 4.7889 | 0.0085
GEN-2022-083 | 01 NORTH | 655790 | HELMUT -LY7 | 115 | 5.7824 | 5.7903 | 0.0079
GEN-2022-083 | 01 NORTH | 655791 | SPRINGLK-LY7 | 115 | 1.9942 | 1.9958 | 0.0016
GEN-2022-083 | 01 NORTH | 655792 | NOHLEY -LY7 | 115 | 3.5999 | 3.6049 | 0.005
GEN-2022-083 | 01 NORTH | 655793 | MARLEY -LY7 | 115 | 6.9262 | 6.9726 | 0.0464
GEN-2022-083 | 01 NORTH | 655794 | SANDRSON-LY7 | 115 | 3.5404 | 3.5525 | 0.0121
GEN-2022-083 | 01 NORTH | 655795 | ROMO -LY7 | 115 | 2.9346 | 2.9429 | 0.0083
GEN-2022-083 | 01 NORTH | 655830 | MOUNTAIN-MK7 | 115 | 4.2157 | 4.2236 | 0.0079
GEN-2022-083 | 01 NORTH | 655831 | J12_____-MK7 | 115 | 4.0995 | 4.1121 | 0.0126
GEN-2022-083 | 01 NORTH | 655832 | BLUEBUTE-MK7 | 115 | 8.131 | 8.181 | 0.05
GEN-2022-083 | 01 NORTH | 655833 | GRSYBTTP-MK7 | 115 | 14.3947 | 14.4792 | 0.0845
GEN-2022-083 | 01 NORTH | 655834 | GRASSYBT-MK7 | 115 | 7.0113 | 7.0313 | 0.02
GEN-2022-083 | 01 NORTH | 655835 | LITTLKNF-MK7 | 115 | 3.1422 | 3.1466 | 0.0044
GEN-2022-083 | 01 NORTH | 655836 | OAKDALE -MK7 | 115 | 5.6 | 5.6139 | 0.0139
GEN-2022-083 | 01 NORTH | 655837 | ELMTREE -MK7 | 115 | 3.692 | 3.7022 | 0.0102
GEN-2022-083 | 01 NORTH | 655838 | INDIANHL-MK7 | 115 | 4.1203 | 4.1376 | 0.0173
GEN-2022-083 | 01 NORTH | 655840 | CHRRYCRK-MK7 | 115 | 9.2682 | 9.3155 | 0.0473
GEN-2022-083 | 01 NORTH | 655841 | ARNEGARD-MK7 | 115 | 7.5354 | 7.5523 | 0.0169
GEN-2022-083 | 01 NORTH | 655842 | HAYBUTTE-MK7 | 115 | 3.3034 | 3.3145 | 0.0111
GEN-2022-083 | 01 NORTH | 655843 | TRUEOIL -MK7 | 115 | 1.627 | 1.6277 | 0.0007
GEN-2022-083 | 01 NORTH | 655844 | TIMBERCK-MK7 | 115 | 5.3334 | 5.3625 | 0.0291
GEN-2022-083 | 01 NORTH | 655845 | GRDNCRK2-MK7 | 115 | 4.8115 | 4.8242 | 0.0127
GEN-2022-083 | 01 NORTH | 655846 | F9______-MK7 | 115 | 4.2253 | 4.2435 | 0.0182
GEN-2022-083 | 01 NORTH | 655847 | SWENSON -MK7 | 115 | 4.3636 | 4.3779 | 0.0143
GEN-2022-083 | 01 NORTH | 655848 | BERG -MK7 | 115 | 5.8144 | 5.8398 | 0.0254
GEN-2022-083 | 01 NORTH | 655849 | VEEDER -MK7 | 115 | 10.0504 | 10.127 | 0.0766
GEN-2022-083 | 01 NORTH | 655850 | NRTINDHL-MK7 | 115 | 3.5096 | 3.5222 | 0.0126
GEN-2022-083 | 01 NORTH | 655851 | BIGGULCH-MK7 | 115 | 2.9307 | 2.9345 | 0.0038
GEN-2022-083 | 01 NORTH | 655852 | L11_____-MK7 | 115 | 3.5904 | 3.5961 | 0.0057
GEN-2022-083 | 01 NORTH | 655853 | BEARCREK-MK7 | 115 | 8.4982 | 8.5304 | 0.0322
GEN-2022-083 | 01 NORTH | 655854 | SANDCREK-MK7 | 115 | 3.5566 | 3.5661 | 0.0095
GEN-2022-083 | 01 NORTH | 655855 | ROOSEVLT-MK7 | 115 | 4.9627 | 4.9763 | 0.0136
GEN-2022-083 | 01 NORTH | 655856 | STNJOHNY-MK7 | 115 | 6.6401 | 6.6852 | 0.0451
GEN-2022-083 | 01 NORTH | 655857 | MOCCASIN-MK7 | 115 | 2.6058 | 2.6109 | 0.0051
GEN-2022-083 | 01 NORTH | 655858 | TABLEBUT-MK7 | 115 | 4.3963 | 4.4109 | 0.0146
GEN-2022-083 | 01 NORTH | 655859 | CHARLSON-MK7 | 115 | 3.7711 | 3.7817 | 0.0106
GEN-2022-083 | 01 NORTH | 655861 | HORSECRK-MK7 | 115 | 2.337 | 2.3426 | 0.0056
GEN-2022-083 | 01 NORTH | 655863 | CARTWRIT-MK7 | 115 | 3.1624 | 3.1725 | 0.0101
GEN-2022-083 | 01 NORTH | 655864 | GRAIL -MK7 | 115 | 5.8286 | 5.8542 | 0.0256
GEN-2022-083 | 01 NORTH | 655865 | STATION8-MK7 | 115 | 5.9797 | 6.0067 | 0.027
GEN-2022-083 | 01 NORTH | 655866 | SNDCRKTP-MK7 | 115 | 4.1077 | 4.1204 | 0.0127
GEN-2022-083 | 01 NORTH | 655867 | TWNVLYTP-MK7 | 115 | 3.0188 | 3.0281 | 0.0093
GEN-2022-083 | 01 NORTH | 655869 | TWINVLLY-MK7 | 115 | 2.781 | 2.7889 | 0.0079
GEN-2022-083 | 01 NORTH | 655870 | TBGARDEN-MK7 | 115 | 2.6789 | 2.6862 | 0.0073
GEN-2022-083 | 01 NORTH | 655871 | G9______-MK7 | 115 | 3.9698 | 3.9858 | 0.016
GEN-2022-083 | 01 NORTH | 655872 | G9TAP___-MK7 | 115 | 4.6009 | 4.6225 | 0.0216
GEN-2022-083 | 01 NORTH | 655873 | BBCOMPTP-MK7 | 115 | 7.0728 | 7.1106 | 0.0378
GEN-2022-083 | 01 NORTH | 655874 | BBCMPRSS-MK7 | 115 | 6.4501 | 6.4815 | 0.0314
GEN-2022-083 | 01 NORTH | 655875 | DPLWC___-MK7 | 115 | 8.0447 | 8.0803 | 0.0356
GEN-2022-083 | 01 NORTH | 655876 | DPLWCTAP-MK7 | 115 | 8.8903 | 8.9339 | 0.0436
GEN-2022-083 | 01 NORTH | 655877 | LITTLMS4-MK7 | 115 | 5.4581 | 5.4745 | 0.0164
GEN-2022-083 | 01 NORTH | 655878 | CRESTWD_-MK7 | 115 | 4.0289 | 4.0379 | 0.009
GEN-2022-083 | 01 NORTH | 655879 | OASIS___-MK7 | 115 | 4.8496 | 4.8626 | 0.013
GEN-2022-083 | 01 NORTH | 655880 | SCHAFR_T-MK7 | 115 | 5.848 | 5.8737 | 0.0257
GEN-2022-083 | 01 NORTH | 655881 | DAP_____-MK7 | 115 | 13.4887 | 13.627 | 0.1383
GEN-2022-083 | 01 NORTH | 655882 | GALAXYTP-MK7 | 115 | 10.1022 | 10.1796 | 0.0774
GEN-2022-083 | 01 NORTH | 655883 | GALAXY -MK7 | 115 | 7.922 | 7.9695 | 0.0475
GEN-2022-083 | 01 NORTH | 655884 | DEMCKSLK-MK7 | 115 | 5.5054 | 5.5283 | 0.0229
GEN-2022-083 | 01 NORTH | 655885 | NRTHFORK-MK7 | 115 | 4.2848 | 4.2985 | 0.0137
GEN-2022-083 | 01 NORTH | 655886 | KEENE -MK7 | 115 | 5.1135 | 5.1331 | 0.0196
GEN-2022-083 | 01 NORTH | 655888 | BANKS -MK7 | 115 | 3.4871 | 3.4995 | 0.0124
GEN-2022-083 | 01 NORTH | 655889 | LC_GAS_P-MK7 | 115 | 6.3679 | 6.4094 | 0.0415
GEN-2022-083 | 01 NORTH | 655891 | KILLDEER-MK7 | 115 | 4.9167 | 4.9227 | 0.006
GEN-2022-083 | 01 NORTH | 655892 | ALEXANDR-MK7 | 115 | 4.0655 | 4.0823 | 0.0168
GEN-2022-083 | 01 NORTH | 655893 | DUNNCNTR-MK7 | 115 | 6.331 | 6.3489 | 0.0179
GEN-2022-083 | 01 NORTH | 655894 | HALLIDAY-MK7 | 115 | 3.5712 | 3.5768 | 0.0056
GEN-2022-083 | 01 NORTH | 655895 | GARDN-FB-MK7 | 115 | 4.4263 | 4.4371 | 0.0108
GEN-2022-083 | 01 NORTH | 655896 | KEENECRN-MK7 | 115 | 3.4825 | 3.4916 | 0.0091
GEN-2022-083 | 01 NORTH | 655897 | COYOTCHR-MK7 | 115 | 5.3666 | 5.3883 | 0.0217
GEN-2022-083 | 01 NORTH | 655898 | SCHAFER -MK7 | 115 | 3.1792 | 3.1847 | 0.0055
GEN-2022-083 | 01 NORTH | 655899 | FNCYBTAP-MK7 | 115 | 6.4924 | 6.5241 | 0.0317
GEN-2022-083 | 01 NORTH | 655906 | FINSTAD -MW7 | 115 | 21.2075 | 21.3656 | 0.1581
GEN-2022-083 | 01 NORTH | 655924 | STATELIN-MW7 | 115 | 16.1784 | 16.293 | 0.1146
GEN-2022-083 | 01 NORTH | 655925 | JUDSON -MW7 | 115 | 15.8631 | 16.0867 | 0.2236
GEN-2022-083 | 01 NORTH | 655926 | SW.WLSTN-MW7 | 115 | 8.8628 | 8.9322 | 0.0694
GEN-2022-083 | 01 NORTH | 655931 | BLKTLTAP-MW7 | 115 | 8.0877 | 8.1714 | 0.0837
GEN-2022-083 | 01 NORTH | 655933 | N.MISRDG-MW7 | 115 | 15.8514 | 16.1365 | 0.2851
GEN-2022-083 | 01 NORTH | 655934 | N.WLST_T-MW7 | 115 | 14.4589 | 14.6962 | 0.2373
GEN-2022-083 | 01 NORTH | 655935 | NW.WLSTN-MW7 | 115 | 12.8379 | 13.0177 | 0.1798
GEN-2022-083 | 01 NORTH | 655936 | N.WILSTN-MW7 | 115 | 14.1151 | 14.3424 | 0.2273
GEN-2022-083 | 01 NORTH | 655937 | NE.WLSTN-MW7 | 115 | 13.1118 | 13.3139 | 0.2021
GEN-2022-083 | 01 NORTH | 655938 | SE.WLSTN-MW7 | 115 | 8.4723 | 8.552 | 0.0797
GEN-2022-083 | 01 NORTH | 655940 | MONT -MW7 | 115 | 16.1082 | 16.3059 | 0.1977
GEN-2022-083 | 01 NORTH | 655941 | STRNDAHL-MW7 | 115 | 7.4988 | 7.5256 | 0.0268
GEN-2022-083 | 01 NORTH | 655945 | WHEELS_T-MW7 | 115 | 9.3271 | 9.4078 | 0.0807
GEN-2022-083 | 01 NORTH | 655955 | ZAHL -MW7 | 115 | 6.7184 | 6.7734 | 0.055
GEN-2022-083 | 01 NORTH | 655956 | TYRONE -MW7 | 115 | 10.8502 | 11.0073 | 0.1571
GEN-2022-083 | 01 NORTH | 655957 | EASTFORK-MW7 | 115 | 17.7863 | 18.2272 | 0.4409
GEN-2022-083 | 01 NORTH | 655958 | FOLVAG -MW7 | 115 | 14.2754 | 14.5473 | 0.2719
GEN-2022-083 | 01 NORTH | 655966 | OLIVER -MW7 | 115 | 6.8606 | 6.909 | 0.0484
GEN-2022-083 | 01 NORTH | 659060 | FINSTAD345 | 345 | 7.6153 | 7.6786 | 0.0633
GEN-2022-083 | 01 NORTH | 659101 | ANTELOPE-BE3 | 345 | 20.7071 | 20.8155 | 0.1084
GEN-2022-083 | 01 NORTH | 659105 | LELAND_O-BE3 | 345 | 20.1391 | 20.2067 | 0.0676
GEN-2022-083 | 01 NORTH | 659106 | LELAND_O-BE4 | 230 | 25.8935 | 25.9489 | 0.0554
GEN-2022-083 | 01 NORTH | 659109 | BASIN___-BE7 | 115 | 5.4307 | 5.4319 | 0.0012
GEN-2022-083 | 01 NORTH | 659112 | CULBRTSN-UM7 | 115 | 5.6249 | 5.6336 | 0.0087
GEN-2022-083 | 01 NORTH | 659124 | DICKINSN-BE4 | 230 | 7.3161 | 7.3299 | 0.0138
GEN-2022-083 | 01 NORTH | 659138 | NESET___-BE4 | 230 | 14.0163 | 14.2248 | 0.2085
GEN-2022-083 | 01 NORTH | 659143 | BLAISDEL-BE4 | 230 | 6.3572 | 6.3799 | 0.0227
GEN-2022-083 | 01 NORTH | 659151 | RICHLAND-BE7 | 115 | 5.8239 | 5.8318 | 0.0079
GEN-2022-083 | 01 NORTH | 659154 | LC_CT4-5-BE7 | 115 | 7.7826 | 7.7928 | 0.0102
GEN-2022-083 | 01 NORTH | 659181 | BICNTNIL-BE7 | 115 | 3.4461 | 3.4498 | 0.0037
GEN-2022-083 | 01 NORTH | 659182 | CHARL_CK-BE7 | 115 | 14.5223 | 14.6083 | 0.086
GEN-2022-083 | 01 NORTH | 659183 | CHARL_CK-BE3 | 345 | 11.6194 | 11.8078 | 0.1884
GEN-2022-083 | 01 NORTH | 659184 | ROUGHRDR-BE7 | 115 | 4.4395 | 4.4464 | 0.0069
GEN-2022-083 | 01 NORTH | 659185 | FOUREYES-RR7 | 115 | 3.761 | 3.7667 | 0.0057
GEN-2022-083 | 01 NORTH | 659199 | BASIN___-BE4 | 230 | 23.4357 | 23.4808 | 0.0451
GEN-2022-083 | 01 NORTH | 659212 | DGC_____-BE3 | 345 | 19.5518 | 19.6484 | 0.0966
GEN-2022-083 | 01 NORTH | 659218 | COTEAU__-RR3 | 345 | 20.7071 | 20.8155 | 0.1084
GEN-2022-083 | 01 NORTH | 659222 | COTEAU_1-RR8 | 69 | 9.8912 | 9.8961 | 0.0049
GEN-2022-083 | 01 NORTH | 659233 | DGC_____-BE4 | 230 | 7.7282 | 7.7382 | 0.01
GEN-2022-083 | 01 NORTH | 659236 | DGC UREA-BE8 | 69 | 7.4137 | 7.4165 | 0.0028
GEN-2022-083 | 01 NORTH | 659247 | MEDORA__-UM4 | 230 | 5.5241 | 5.5332 | 0.0091
GEN-2022-083 | 01 NORTH | 659248 | HALLIDAY-UM7 | 115 | 4.168 | 4.1704 | 0.0024
GEN-2022-083 | 01 NORTH | 659262 | CULBSN.E-BE7 | 115 | 8.3315 | 8.3523 | 0.0208
GEN-2022-083 | 01 NORTH | 659269 | CULB_GEN-BE7 | 115 | 7.5768 | 7.5911 | 0.0143
GEN-2022-083 | 01 NORTH | 659302 | CHARL_CK-BE4 | 230 | 12.3417 | 12.4946 | 0.1529
GEN-2022-083 | 01 NORTH | 659306 | S.HEART_-RR7 | 115 | 2.3155 | 2.3165 | 0.001
GEN-2022-083 | 01 NORTH | 659309 | S.HEART_-RR4 | 230 | 9.8955 | 9.9328 | 0.0373
GEN-2022-083 | 01 NORTH | 659333 | JUDSON__-BE3 | 345 | 11.0876 | 12.2497 | 1.1621
GEN-2022-083 | 01 NORTH | 659334 | JUDSON__-BE4 | 230 | 13.2812 | 13.9972 | 0.716
GEN-2022-083 | 01 NORTH | 659336 | TANDE___-BE3 | 345 | 9.5826 | 9.7674 | 0.1848
GEN-2022-083 | 01 NORTH | 659337 | TANDE___-BE4 | 230 | 13.8098 | 14.0176 | 0.2078
GEN-2022-083 | 01 NORTH | 659346 | LC_SWY.S-BE7 | 115 | 7.7543 | 7.7648 | 0.0105
GEN-2022-083 | 01 NORTH | 659347 | PIONEER1-BE7 | 115 | 16.1784 | 16.293 | 0.1146
GEN-2022-083 | 01 NORTH | 659348 | LC_CT1-3-BE7 | 115 | 12.6212 | 12.7341 | 0.1129
GEN-2022-083 | 01 NORTH | 659349 | LC_SWY.N-BE7 | 115 | 12.6213 | 12.7342 | 0.1129
GEN-2022-083 | 01 NORTH | 659362 | WHEELOCK-BE4 | 230 | 8.3241 | 8.4626 | 0.1385
GEN-2022-083 | 01 NORTH | 659363 | WHEELOCK-BE7 | 115 | 9.5608 | 9.6485 | 0.0877
GEN-2022-083 | 01 NORTH | 659384 | ROUNDUP_-BE3 | 345 | 10.4399 | 10.5873 | 0.1474
GEN-2022-083 | 01 NORTH | 659385 | ROUNDUP_-MK7 | 115 | 12.2743 | 12.3415 | 0.0672
GEN-2022-083 | 01 NORTH | 659387 | KUMMERDG-BE3 | 345 | 7.9647 | 8.1106 | 0.1459
GEN-2022-083 | 01 NORTH | 659388 | KUMMERDG-MK7 | 115 | 15.0114 | 15.1829 | 0.1715
GEN-2022-083 | 01 NORTH | 659390 | PATENTGT-BE3 | 345 | 10.0371 | 10.4115 | 0.3744
GEN-2022-083 | 01 NORTH | 659391 | PATENTGT-MK7 | 115 | 19.2482 | 19.6323 | 0.3841
GEN-2022-083 | 01 NORTH | 659404 | BURKE___-PP3 | 345 | 5.0424 | 5.0893 | 0.0469
GEN-2022-083 | 01 NORTH | 659420 | AV.LS-BD-BE3 | 345 | 20.7071 | 20.8155 | 0.1084
GEN-2022-083 | 01 NORTH | 659421 | BD.LS-AV-BE3 | 345 | 4.8227 | 4.8233 | 0.0006
GEN-2022-083 | 01 NORTH | 659422 | LO.LS-GR-BE3 | 345 | 20.1391 | 20.2067 | 0.0676
GEN-2022-083 | 01 NORTH | 659424 | LO.LS-FT-BE3 | 345 | 20.1391 | 20.2067 | 0.0676
GEN-2022-083 | 01 NORTH | 659427 | TN.LS-JD-BE3 | 345 | 9.5826 | 9.7674 | 0.1848
GEN-2022-083 | 01 NORTH | 659442 | 32STREET-RR7 | 115 | 1.9398 | 1.9406 | 0.0008
GEN-2022-083 | 01 NORTH | 659443 | SKUNKHIL-RR7 | 115 | 1.7451 | 1.7457 | 0.0006
GEN-2022-083 | 01 NORTH | 659448 | DAGLUM__-BE4 | 230 | 6.7075 | 6.7203 | 0.0128
GEN-2022-083 | 01 NORTH | 659450 | BRADYWND 4 | 230 | 3.6468 | 3.6496 | 0.0028
GEN-2022-083 | 01 NORTH | 659466 | PG.KU17A-BE7 | 115 | 19.145 | 19.5273 | 0.3823
GEN-2022-083 | 01 NORTH | 659467 | PG.KU19A-BE7 | 115 | 19.1573 | 19.5399 | 0.3826
GEN-2022-083 | 01 NORTH | 659479 | TRADEWND-UA3 | 345 | 6.6918 | 6.7752 | 0.0834
GEN-2022-083 | 01 NORTH | 659544 | PRNGHORN-RR7 | 115 | 1.9398 | 1.9406 | 0.0008
GEN-2022-083 | 01 NORTH | 659576 | BEPCPRXCC1 3 | 345 | 19.8076 | 19.9041 | 0.0965
GEN-2022-083 | 01 NORTH | 659584 | BEPCPRXCC3 7 | 115 | 14.7454 | 14.9109 | 0.1655
GEN-2022-083 | 01 NORTH | 659600 | EFORK_-BE334 | 345 | 9.2025 | 9.6972 | 0.4947
GEN-2022-083 | 01 NORTH | 661003 | WATFRDSOUTH4 | 230 | 7.1692 | 7.2486 | 0.0794
GEN-2022-083 | 01 NORTH | 661084 | TIOGA4 4 | 230 | 14.0163 | 14.2248 | 0.2085
GEN-2022-083 | 01 NORTH | 661085 | TIOGA4 7 | 115 | 13.947 | 14.0428 | 0.0958
GEN-2022-083 | 01 NORTH | 661087 | RAY JCT7 | 115 | 5.9541 | 5.9763 | 0.0222
GEN-2022-083 | 01 NORTH | 661089 | LTLMUDY7 | 115 | 7.224 | 7.2675 | 0.0435
GEN-2022-083 | 01 NORTH | 672603 | BDV 4 | 230 | 5.0734 | 5.0816 | 0.0082
GEN-2022-083 | 01 NORTH | 763021 | GEN-2018-067 | 115 | 7.4988 | 7.5256 | 0.0268
GEN-2022-083 | 01 NORTH | 763703 | GEN-2019-037 | 345 | 12.1744 | 12.1983 | 0.0239
GEN-2022-083 | 01 NORTH | 765050 | PIONEER_-BE3 | 345 | 8.5959 | 10.2016 | 1.6057