## Executive Summary
Executive Summary: GEN-2022-147 Interim Availability Interconnection System Impact Study
Interconnection Customer GEN-2022-147 (Group 05) has requested a Limited Operation or Interim Availability Interconnection System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions (Scenarios Tab) at the time of service to determine the amount of Interconnection Capacity available to the interconnection customers listed under specific system conditions.
Once a GIA amendment to incorporate Interim GIA is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Interim Operation in accordance with the SPP study results.
Interim
In accordance with Section 11A of the GIP, Interim GIA, Interconnection Customers with a pending Interconnection Request that has an anticipated In-Service Date prior to the expected completion of the DISIS may request a study to evaluate the feasibility of Interim Interconnection Service.
Interim Interconnection Capacity conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Study Limitations
In the event that an Interconnection Request, with queue priority equal to or higher than a Interconnection Request, which was excluded as a study scenario achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study scenario is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 2.0
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20230915.pdf
Models Used in Study
Power Flow Analysis: DISIS-2017-002 (Restudy)
Summer: 2023 (23SP), 2026 (26SP)
Winter: 2026 (26WP)
Stability Analysis: DISIS-2017-002 (Restudy) (2020 Series MDWG Dynamics)
Summer: 2025 (25SP)
Winter: 2025 (25WP)
Short Circuit Analysis: DISIS-2017-002 (Restudy) (2020 Series MDWG Dynamics)
Summer: 2025 (25SP)
Author: SPP Generator Interconnection Department
Published: 11/07/2023

## Revision History
Revision History
Date | Author | Change Description
2023-10-26 | SPP | Draft.
2023-11-07 | SPP | Final.

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Service | Area | POI | Status
GEN-2022-147 | 05 - Southwest | 24 | DIS-22-1 | Thermal | 203 | Full | None | ER/NR | SPS | Tuco 345kV | DISIS STAGE
GEN-2018-070 | 01 - North | 21 | DIS-18-2 | Wind | 18.31 |  |  | ER/NR | WAPA | Utica Junction 230 kV substation | DISIS STAGE
GEN-2019-001 | 03 - Central | 21 | DIS-19-1 | Wind | 25 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-018 | 03 - Central | 21 | DIS-19-1 | Thermal | 15.56 |  |  | ER/NR | MIDW | Saxman 115kV substation | DISIS STAGE
GEN-2019-019 | 01 - North | 21 | DIS-19-1 | Thermal | 15.15 |  |  | ER/NR | BEPC-SPP | Siouxland 69kV | DISIS STAGE
GEN-2020-002 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 81 |  |  | ER/NR | OPPD | 6846 Substation 69 kV | DISIS STAGE
GEN-2020-014 | 01 - North | 22 | DIS-20-1 | Thermal | 45 |  |  | ER/NR | BEPC-SPP | Lonesome Creek 115kV | DISIS STAGE
GEN-2020-056 | 03 - Central | 22 | DIS-20-1 | Solar | 20 |  |  | ER/NR | SUNC | Russell 115 kV Substation | DISIS STAGE
ASGI-2017-014 | 03 - Central | 19 | DIS-17-2 | Solar | 40 |  |  | ER/NR | KCPL | Post Oak 69 kV | DISIS STAGE
GEN-2017-105 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 75 |  |  | ER/NR | OPPD | Tekamah - Raun 161 kV Line | DISIS STAGE
GEN-2017-108 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | Stillwell - Clinton 161kV Line | DISIS STAGE
GEN-2017-111 | 03 - Central | 19 | DIS-17-2 | Solar | 152 |  |  | ER | KCPL | Clinton - Stilwell 161 kV Line Tap | DISIS STAGE
GEN-2017-115 | 03 - Central | 19 | DIS-17-2 | Wind | 244 |  |  | ER | KCPL | Holt County 345 kV | DISIS STAGE
GEN-2017-117 | 04 - Southeast | 19 | DIS-17-2 | Battery | 19.8 |  |  | ER/NR | WFEC | El Reno SW 138kV | DISIS STAGE
GEN-2017-119 | 03 - Central | 19 | DIS-17-2 | Wind | 180 |  |  | ER | SUNC | Elm Creek 345kV substation | DISIS STAGE
GEN-2017-120 | 03 - Central | 19 | DIS-17-2 | Wind | 260 |  |  | ER | WERE | Abilene Energy Center-Northview 115kV | DISIS STAGE
GEN-2017-121 | 03 - Central | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | WERE | Sumner 138kV | DISIS STAGE
GEN-2017-125 | 03 - Central | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-131 | 03 - Central | 19 | DIS-17-2 | Battery | 29.6 |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-132 | 04 - Southeast | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-133 | 04 - Southeast | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-134 | 04 - Southeast | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-137 | 04 - Southeast | 19 | DIS-17-2 | Wind | 295 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-140 | 04 - Southeast | 19 | DIS-17-2 | Solar | 160 |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-141 | 04 - Southeast | 19 | DIS-17-2 | Solar | 241.7 |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-144 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 200 |  |  | ER | WAPA | Holt County 345kV | DISIS STAGE
GEN-2017-146 | 05 - Southwest | 19 | DIS-17-2 | Wind | 151.8 |  |  | ER | SPS | Deaf Smith-Plant X 230kV | DISIS STAGE
GEN-2017-148 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | EMDE | Joplin 161kV sub | DISIS STAGE
GEN-2017-149 | 04 - Southeast | 19 | DIS-17-2 | Wind | 258 |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-150 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-151 | 05 - Southwest | 19 | DIS-17-2 | Wind | 300 |  |  | ER | SPS | TUCO-Oklaunion 345kV | DISIS STAGE
GEN-2017-152 | 04 - Southeast | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-154 | 04 - Southeast | 19 | DIS-17-2 | Wind | 255 |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-155 | 04 - Southeast | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | OKGE | Muskogee 345kV Substation | DISIS STAGE
GEN-2017-158 | 05 - Southwest | 19 | DIS-17-2 | Wind | 265 |  |  | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2017-164 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-166 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-167 | 04 - Southeast | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-168 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-169 | 04 - Southeast | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-171 | 04 - Southeast | 19 | DIS-17-2 | Solar | 150 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-172 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-173 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-175 | 01 - North | 19 | DIS-17-2 | Wind | 300 |  |  | ER | WAPA | Vfodnes-Utica Jct. 230kV | DISIS STAGE
GEN-2017-178 | 04 - Southeast | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-181 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-182 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 128 |  |  | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-183 | 03 - Central | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-184 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-187 | 05 - Southwest | 19 | DIS-17-2 | Solar | 150 |  |  | ER | SPS | Sulphur Springs 115kV Substation | DISIS STAGE
GEN-2017-188 | 03 - Central | 19 | DIS-17-2 | Solar | 130 |  |  | ER | EMDE | Asbury 161 kV | DISIS STAGE
GEN-2017-195 | 03 - Central | 19 | DIS-17-2 | Solar | 500.4 |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-196 | 03 - Central | 19 | DIS-17-2 | Battery | 128 |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-198 | 02 - Nebraska | 19 | DIS-17-2 | Battery | 11.64 |  |  | ER | OPPD | Jones St. No 1201 69kV substation | DISIS STAGE
GEN-2017-201 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | NPPD | Hoskins 345kV Substation | DISIS STAGE
GEN-2017-202 | 03 - Central | 19 | DIS-17-2 | Solar | 200 |  |  | ER/NR | SWPA | New Madrid - Sikeston 161kV | DISIS STAGE
GEN-2017-203 | 04 - Southeast | 19 | DIS-17-2 | Solar/Battery | 280 |  |  | ER | OKGE | Renfrow 345kV Substation | DISIS STAGE
GEN-2017-209 | 03 - Central | 19 | DIS-17-2 | Solar/Battery | 400 |  |  | ER | KCPL | LaCygne - Neosho 345kV | DISIS STAGE
GEN-2017-210 | 02 - Nebraska | 19 | DIS-17-2 | Solar/Battery | 410 |  |  | ER | NPPD | McCool 345kV Substation | DISIS STAGE
GEN-2017-214 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-215 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-216 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-220 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-221 | 03 - Central | 19 | DIS-17-2 | Battery | 152 |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-222 | 01 - North | 19 | DIS-17-2 | Wind | 180 |  |  | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2017-226 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-227 | 03 - Central | 19 | DIS-17-2 | Battery | 201.6 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-230 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | Tryon 138kV Substation | DISIS STAGE
GEN-2017-231 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | Branch 161kV Substation | DISIS STAGE
GEN-2017-232 | 04 - Southeast | 19 | DIS-17-2 | Solar | 52.2 |  |  | ER/NR | OKGE | Brown 138kV Substation | DISIS STAGE
GEN-2017-233 | 04 - Southeast | 19 | DIS-17-2 | Wind | 215 |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-234 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 115 |  |  | ER | NPPD | Spalding to North Loup 115kV | DISIS STAGE
GEN-2017-239 | 05 - Southwest | 19 | DIS-17-2 | Solar | 300 |  |  | ER | SPS | Mahoney 230kV Substation | DISIS STAGE
GIA-83 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 1031 |  |  | ER/NR | AECI | McCredie 345 kV
GIA-85 | 03 - Central | 18.5 | DIS-17-2-PQ | Battery | 447.3 |  |  | ER/NR | AECI | Morgan 345 kV | DISIS STAGE
GIA-86 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 103.68 |  |  | ER/NR | AECI | Thomas Hill 69 kV
GIA-88 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 92.09 |  |  | ER/NR | AECI | Eudora 69 kV
GIA-90 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 108 |  |  | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 104.4 |  |  | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 100 |  |  | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 252 |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
IR24 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  | ER/NR | ALTW | Murray Junction 69 kV substation
J545 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 110 |  |  | ER | XEL | Buffalo 115kV Substation
J722 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | OTP | Big Stone South 230kV Substation
J801 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 74 |  |  | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | DISIS STAGE
J803 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 32.5 |  |  | ER | XEL | Tracy 69 kV line | DISIS STAGE
J836 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | ALTW | Ledyard 345kV Substation
J874 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 150 |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line | DISIS STAGE
J877 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Solar | 250 |  |  | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | DISIS STAGE
J897 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 190 |  |  | ER | GRE | Prairie - Ramsey 230 kV line
J898 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 100 |  |  | ER | DPC | Rice - Beaver Creek 161kV line tap
J926 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 101.28 |  |  | ER | XEL | Pine Lake - Apple River 161 kV Line
GEN-2016-037 | 04 - Southeast | 18 | DIS-17-1 | Wind | 300 |  |  | ER | AEPW | Chisholm-Gracemont 345kV | FACILITY STUDY STAGE
GEN-2017-004 | 03 - Central | 18 | DIS-17-1 | Wind | 201.6 |  |  | ER | SUNC | Elm Creek - Summit 345 kV | FACILITY STUDY STAGE
GEN-2017-005 | 03 - Central | 18 | DIS-17-1 | Wind | 190 |  |  | ER | WERE | Marmaton - Litchfield 161 kV | FACILITY STUDY STAGE
GEN-2017-010 | 01 - North | 18 | DIS-17-1 | Wind | 200.1 |  |  | ER | WAPA | Rhame 230 kV Sub | FACILITY STUDY STAGE
GEN-2017-011 | 04 - Southeast | 18 | DIS-17-1 | Solar | 151.8 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | FACILITY STUDY STAGE
GEN-2017-014 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  | ER | WAPA | Philip Tap 230 kV | FACILITY STUDY STAGE
GEN-2017-018 | 03 - Central | 18 | DIS-17-1 | Solar | 189 |  |  | ER/NR | SUNC | Thistle 345 kV sub | FACILITY STUDY STAGE
GEN-2017-022 | 03 - Central | 18 | DIS-17-1 | Solar | 65 |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | FACILITY STUDY STAGE
GEN-2017-023 | 04 - Southeast | 18 | DIS-17-1 | Solar | 85 |  |  | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | FACILITY STUDY STAGE
GEN-2017-027 | 04 - Southeast | 18 | DIS-17-1 | Wind | 140 |  |  | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | FACILITY STUDY STAGE
GEN-2017-033 | 05 - Southwest | 18 | DIS-17-1 | Wind | 200 |  |  | ER/NR | AEPW | Oklaunion 345 kV sub | FACILITY STUDY STAGE
GEN-2017-036 | 04 - Southeast | 18 | DIS-17-1 | Solar | 100 |  |  | ER | WFEC | Snyder - Cache 138 kV | FACILITY STUDY STAGE
GEN-2017-040 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200.1 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-047 | 05 - Southwest | 18 | DIS-17-1 | Wind | 102 |  |  | ER/NR | SPS | Cole 115kV | FACILITY STUDY STAGE
GEN-2017-048 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  | ER | BEPC-SPP | Neset 230 kV Substation | FACILITY STUDY STAGE
GEN-2017-057 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Hosston 69kV | FACILITY STUDY STAGE
GEN-2017-061 | 04 - Southeast | 18 | DIS-17-1 | Solar | 101.5 |  |  | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | FACILITY STUDY STAGE
GEN-2017-068 | 03 - Central | 18 | DIS-17-1 | Solar | 103.5 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | FACILITY STUDY STAGE
GEN-2017-071 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-072 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-073 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | GRDA | Dry Gulch 161kV sub | FACILITY STUDY STAGE
GEN-2017-074 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE
GEN-2017-075 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Hugo-Sunnyside 345 kV | FACILITY STUDY STAGE
GEN-2017-076 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE
GEN-2017-077 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE
GEN-2017-086 | 03 - Central | 18 | DIS-17-1 | Wind | 150 |  |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2017-092 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-094 | 01 - North | 18 | DIS-17-1 | Wind | 200 |  |  | ER | WAPA | Fort Thompson-Huron 230 kV | FACILITY STUDY STAGE
GEN-2017-097 | 01 - North | 18 | DIS-17-1 | Solar | 128 |  |  | ER | WAPA | Underwood 115 kV Sub | FACILITY STUDY STAGE
GEN-2017-100 | 05 - Southwest | 18 | DIS-17-1 | Solar | 102.6 |  |  | ER/NR | SPS | Texas County 115kV | FACILITY STUDY STAGE
BEPCNDPW1 | 01 - North | 17.5 | DIS-17-1-PQ | Wind | 5 |  |  | ER | BEPC-SPP | NELSON 7
ASGI-2016-010 | 05 - Southwest | 17 | DIS-16-2 | Wind | 90 |  |  | ER | SPS | TEXAS_CNTY 3
GEN-2016-036 | 01 - North | 17 | DIS-16-2 | Wind | 44.6 |  |  | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  |  | ER | NPPD | Sweetwater 345kV | IA PENDING
GEN-2016-087 | 01 - North | 17 | DIS-16-2 | Wind | 98.9 |  |  | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 - Southeast | 17 | DIS-16-2 | Wind | 303.6 |  |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 - North | 17 | DIS-16-2 | Wind | 200 |  |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | 04 - Southeast | 17 | DIS-16-2 | Wind | 200 |  |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-097 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA PENDING
GEN-2016-102 | 04 - Southeast | 17 | DIS-16-2 | Wind | 150.9 |  |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-111 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-115 | 03 - Central | 17 | DIS-16-2 | Wind | 300 |  |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-118 | 04 - Southeast | 17 | DIS-16-2 | Wind | 288 |  |  | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 04 - Southeast | 17 | DIS-16-2 | Wind | 600 |  |  | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-121 | 05 - Southwest | 17 | DIS-16-2 | Solar | 110 |  |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 - Southeast | 17 | DIS-16-2 | Wind | 172.5 |  |  | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-128 | 04 - Southeast | 17 | DIS-16-2 | Wind | 176 |  |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 - North | 17 | DIS-16-2 | Wind | 202 |  |  | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 - Southeast | 17 | DIS-16-2 | Wind | 2.5 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 04 - Southeast | 17 | DIS-16-2 | Wind | 6.12 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-134 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-137 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-138 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-139 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-141 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-142 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-145 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-146 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-147 | 02 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  |  | ER | NPPD | Sidney 115 kV Sub | IA PENDING
GEN-2016-149 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 - Central | 17 | DIS-16-2 | Wind | 134 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-157 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-158 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 - Central | 17 | DIS-16-2 | Battery | 20 |  |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 - Southeast | 17 | DIS-16-2 | Solar | 73.5 |  |  | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 - Southwest | 17 | DIS-16-2 | Gas Turbine | 17 |  |  | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-006GIA-53 | 03 - Central | 16.5 | Dis-16-2-PQ | Wind | 238 |  |  | ER/NR | AECI | 5MARYVL
ASGI-2016-004 | 05 - Southwest | 16 | DIS-16-1 | Wind | 10 |  |  | ER | SPS | Palo Duro 115kV
GEN-2015-036 | 04 - Southeast | 16 | DIS-16-1 | Wind | 303.6 |  |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 - Southwest | 16 | DIS-16-1 | Wind | 200 |  |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 - Southeast | 16 | DIS-16-1 | Wind | 176 |  |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 - Southeast | 16 | DIS-16-1 | Wind | 248.4 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 01 - North | 16 | DIS-16-1 | Wind | 202 |  |  | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-007 | 01 - North | 16 | DIS-16-1 | Wind | 100.05 |  |  | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | 03 - Central | 16 | DIS-16-1 | Steam Turbine | 29 |  |  | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Central | 16 | DIS-16-1 | Wind | 78.2 |  |  | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-020 | 04 - Southeast | 16 | DIS-16-1 | WIND | 150 |  |  | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 - Nebraska | 16 | DIS-16-1 | WIND | 300 |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-030 | 04 - Southeast | 16 | DIS-16-1 | Solar | 100 |  |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 - Southeast | 16 | DIS-16-1 | Wind | 1.5 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 230 |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Central | 16 | DIS-16-1 | Wind | 299 |  |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-050 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | NPPD | Axtell - Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-051 | 04 - Southeast | 16 | DIS-16-1 | Wind | 9.8 |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 04 - Southeast | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-070 | 05 - Southwest | 16 | DIS-16-1 | Wind | 5.3 |  |  | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200.1 |  |  | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-073 | 03 - Central | 16 | DIS-16-1 | Wind | 220 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-075 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
GEN-2015-045 | 04 - Southeast | 15 | DIS-15-2 | Battery | 20 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 04 - Southeast | 15 | DIS-15-2 | Wind | 2.17 |  |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 - Southeast | 15 | DIS-15-2 | Wind | 200 |  |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 04 - Southeast | 15 | DIS-15-2 | Wind | 300 |  |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-055 | 04 - Southeast | 15 | DIS-15-2 | Solar | 40 |  |  | ER | WFEC | Erick 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-062 | 04 - Southeast | 15 | DIS-15-2 | Wind | 4.5 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 - Southeast | 15 | DIS-15-2 | Wind | 0.75 |  |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 - Southeast | 15 | DIS-15-2 | Wind | 248.4 |  |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | 03 - Central | 15 | DIS-15-2 | Wind | 0.75 |  |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 - Central | 15 | DIS-15-2 | Wind | 219.99 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 2 |  |  | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 10 |  |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2008-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 5 |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER | BEPC-SPP | Groton 115kV
GEN-2009-020AIS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.4 |  |  | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 3.5 |  |  | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2014-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Gas | 11.72 |  |  | ER/NR | BEPC-SPP | Williston 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
MPC02100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.75 |  |  | ER | OTP | Center - Mandan 230 kV
ASGI-2015-001 | 03 - Central | 14 | DIS-15-1 | Thermal | 6.13 |  |  | ER | SUNC | Ninnescah 115kV
GEN-2015-005 | 03 - Central | 14 | DIS-15-1 | Wind | 16.11 |  |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 - Southeast | 14 | DIS-15-1 | Solar | 120 |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 02 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 03 - Central | 14 | DIS-15-1 | Wind | 219.99 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 - Central | 14 | DIS-15-1 | Wind | 219.98 |  |  | ER | WERE | Tap Thistle - Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 - Central | 13 | DIS-14-2 | Wind | 2.42 |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 - Southwest | 13 | DIS-14-2 | Solar | 30 |  |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 05 - Southwest | 13 | DIS-14-2 | Wind | 44 |  |  | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 - Southeast | 13 | DIS-14-2 | Wind | 0.41 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 - Southeast | 13 | DIS-14-2 | Wind | 1 |  |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 - Central | 12 | DIS-14-1 | Wind | 200.6 |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 - Southeast | 12 | DIS-14-1 | Wind | 10.53 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 - Southeast | 12 | DIS-14-1 | Wind | 5.67 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 0.11 |  |  | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 - Southwest | 11 | DIS-13-2 | Wind | 1.65 |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-019 | 02 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-002 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 - Southwest | 9 | DIS-12-2 | Wind | 18.15 |  |  | ER | SPS | FE-Clovis Interchange 115kV
GEN-2012-024 | 03 - Central | 9 | DIS-12-2 | Wind | 1.8 |  |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 - Southeast | 9 | DIS-12-2 | Wind | 0.72 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006GIA-27 | 04 - Southeast | 8 | PQ | Wind | 150 |  |  | ER | AECI | Remington 138kV
ASGI-2012-006 | 03 - Central | 8 | DIS-12-1 | Steam | 22.5 |  |  | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-039M | 03 - Central | 8 | PQ | Wind | 1 |  |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 - Central | 8 | PQ | Wind | 3 |  |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 - Central | 8 | PQ | Wind | 1 |  |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 - Nebraska | 8 | PQ | Wind | 15 |  |  | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 - Southeast | 8 | PQ | Wind | 1.8 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 - Southwest | 8 | PQ | Wind | 290 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 - Southeast | 8 | DIS-12-1 | Wind | 40.8 |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBuffaloCountySolar | 02 - Nebraska | 8 | PQ | Solar | 10 |  |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 02 - Nebraska | 8 | PQ | Wind | 20 |  |  | ER | NPPD | Tekamah & Oakland 115kV
GEN-2011-037 | 04 - Southeast | 7 | DIS-11-2 | Wind | 6.6 |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 - Southeast | 7 | DIS-11-2 | Wind | 2 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 - Southeast | 6 | DIS-11-1 | Wind | 175 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 - Southeast | 6 | DIS-11-1 | Wind | 165.6 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 - Southwest | 6 | DIS-11-1 | Wind | 299 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-001 | 05 - Southwest | 5 | DIS-10-2 | Wind | 0.3 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 - Southeast | 5 | DIS-10-2 | Wind | 1.8 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 - Southwest | 4 | DIS-10-1 | Wind | 21.65 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 - Southwest | 4 | DIS-10-1 | Wind | 13.13 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 - Central | 4 | DIS-10-1 | Wind | 59.2 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-014 | 05 - Southwest | 4 | DIS-10-1 | Wind | 358.8 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-051 | 05 - Southwest | 3 | DIS-09-1 | Wind | 1 |  |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 - Nebraska | 3 | DIS-09-1 | Wind | 0.4 |  |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 - Central | 3 | DIS-09-1 | Wind | 200.1 |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 - Central | 2 | ICS1 | Wind | 68.8 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 - Southeast | 2 | ICS1 | Wind | 0.3 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Scenarios
Generation Interconnection Number or Upgrade ID | Assigned Study | Service Type | Point of Interconnection or Upgrade Name | Project Capacity in Winter | Project Capacity in Summer | Steady-State ERIS Status or Available MW in Winter | Steady-State ERIS Status or Available MW in Summer | Steady-State NRIS Status or Available MW in Winter | Steady-State NRIS Status or Available MW in Summer | Stability Capacity Available (MW) for Winter | Stability Capacity Available (MW) for Summer
GEN-2022-147 | DISIS-2022-001 | ERIS/NRIS | Tuco 345 kV substation | 203 | 196 | 203 | 196 | 203 | 196 | 203 | 196

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00ALL | ERIS | Non-Converged | None | 23SP, 26SP, 26WP | None | [7 empty] | None
05ALL | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
00ALL | ERIS | Thermal | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00ALL | ERIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00NR | NRIS | Non-Converged | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00NR | NRIS | Thermal | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00NR | NRIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None

## All Thermal
SOLUTIONTYPE | GROUP | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converged | 00ALL | N/A | N/A | " | Non-Converge |  |  |  |  | None
Non-Converged | 00NR | N/A | N/A | " | Non-Converge |  |  |  |  | None
Thermal | 00ALL | N/A | N/A | " | None |  |  |  |  | None
Thermal | 00NR | N/A | N/A | " | None |  |  |  |  | None

## All Voltage
SOLUTION TYPE | GROUP | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00ALL | N/A | N/A | None | [7 empty] | None
Voltage | 00NR | N/A | N/A | None | [7 empty] | None

## Stability Analysis Results
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
05 Southwest | Summer | Transfer | P1_Fault_001 | 3 Phase fault on RPPAPER4 138.00 (511512) 138 kV Bus a. Apply fault at the RPPAPER4 138.00 (511512) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 (511488) 138.0 kV to RPPAPER4 (511512) 138.0 kV Transmission Circuit #1 b.2. LWSTAP 4 (511439) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.3. LWSTAP 4 (511439) 138.0 kV to RPPAPER4 (511512) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_002 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_003 | 3 Phase fault on COMMTAP4 138.00 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 138.00 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.2. DUNCAN-4 (511453) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 b.3. COMMTAP4 (511494) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_004 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to SHERID4 (511474) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_005 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_006 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_007 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_008 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_009 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#1-1 (511416) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_010 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#2-1 (511415) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_011 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_012 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_013 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.4. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_014 | 3 Phase fault on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.2. LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_015 | 3 Phase fault on RKYFORD_TP 3115.00 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3115.00 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 (525414) 115.0 kV to LC-S_OLTON+3 (525440) 115.0 kV Transmission Circuit #1 b.2. LC-S_OLTON+3 (525440) 115.0 kV to RKYFORD_TP 3 (525446) 115.0 kV Transmission Circuit #1 b.3. ROCKYFORD 3 (525393) 115.0 kV to RKYFORD_TP 3 (525446) 115.0 kV Transmission Circuit #1 b.4. RKYFORD_TP 3 (525446) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_016 | 3 Phase fault on LAMTON 3115.00 (525414) 115 kV Bus a. Apply fault at the LAMTON 3115.00 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 (525414) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_017 | 3 Phase fault on LAMB_CNTY 3115.00 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3115.00 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_018 | 3 Phase fault on PRENTICE 3115.00 (526792) 115 kV Bus a. Apply fault at the PRENTICE 3115.00 (526792) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 (526736) 115.0 kV to PRENTICE 3 (526792) 115.0 kV Transmission Circuit #1 b.2. PRENTICE 3 (526792) 115.0 kV to YOAKUM 3 (526934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_019 | 3 Phase fault on TULIA_TP 3115.00 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3115.00 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MU-TULIA 3 (522800) 115.0 kV to TULIA_TP 3 (525179) 115.0 kV Transmission Circuit #1 b.2. HAPPY_INT 3 (525154) 115.0 kV to TULIA_TP 3 (525179) 115.0 kV Transmission Circuit #1 b.3. TULIA_TP 3 (525179) 115.0 kV to KRESS_INT 3 (525192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_020 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_021 | 3 Phase fault on CROSBY 3115.00 (525926) 115 kV Bus a. Apply fault at the CROSBY 3115.00 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 (525926) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_022 | 3 Phase fault on LP-DOUD_TP 3115.00 (526162) 115 kV Bus a. Apply fault at the LP-DOUD_TP 3115.00 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to LP-DOUD_TP 3 (526162) 115.0 kV Transmission Circuit #1 b.2. LP-DOUD_TP 3 (526162) 115.0 kV to LP-DOUD 3 (526176) 115.0 kV Transmission Circuit #1 b.3. LP-DOUD_TP 3 (526162) 115.0 kV to SP-WOLF_TP 3 (526481) 115.0 kV Transmission Circuit #1 b.4. YUMA_INT 3 (526475) 115.0 kV to SP-WOLF_TP 3 (526481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_023 | 3 Phase fault on CALLAHAN 3115.00 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3115.00 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 (525763) 115.0 kV to FLOYD_CNTY 3 (525780) 115.0 kV Transmission Circuit #1 b.2. COX 3 (525326) 115.0 kV to CALLAHAN 3 (525763) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_024 | 3 Phase fault on COX 3115.00 (525326) 115 kV Bus a. Apply fault at the COX 3115.00 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 (525326) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_025 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_026 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_027 | 3 Phase fault on MULSHVLY_TP3115.00 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3115.00 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 (525019) 115.0 kV to BAILEYCO 3 (525028) 115.0 kV Transmission Circuit #1 b.2. MULESHVALLY3 (525018) 115.0 kV to MULSHVLY_TP3 (525019) 115.0 kV Transmission Circuit #1 b.3. MULSHVLY_TP3 (525019) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_028 | 3 Phase fault on PLANT_X 3115.00 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3115.00 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_029 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_030 | 3 Phase fault on STANTON_W 3115.00 (526076) 115 kV Bus a. Apply fault at the STANTON_W 3115.00 (526076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.2. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_031 | 3 Phase fault on LUBBCK_STH 3115.00 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3115.00 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_032 | 3 Phase fault on BC-KELLEY +3115.00 (525050) 115 kV Bus a. Apply fault at the BC-KELLEY +3115.00 (525050) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 (524746) 115.0 kV to BC-KELLEY +3 (525050) 115.0 kV Transmission Circuit #1 b.2. BC-KELLEY +3 (525050) 115.0 kV to BC-EARTH 3 (525056) 115.0 kV Transmission Circuit #1 b.3. BC-EARTH 3 (525056) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_033 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to MURPHY 3 (526192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_034 | 3 Phase fault on ARCO_TP 3115.00 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3115.00 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 (526934) 115.0 kV to ARCO_TP 3 (527041) 115.0 kV Transmission Circuit #1 b.2. BENNETT 3 (527018) 115.0 kV to ARCO_TP 3 (527041) 115.0 kV Transmission Circuit #1 b.3. BENNETT 3 (527018) 115.0 kV to ODC_TP 3 (527051) 115.0 kV Transmission Circuit #1 b.4. ODC_TP 3 (527051) 115.0 kV to SHELL_CO2 3 (527062) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_035 | 3 Phase fault on SP-ERSKINE 3115.00 (526109) 115 kV Bus a. Apply fault at the SP-ERSKINE 3115.00 (526109) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ERSKINE 3 (526109) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.2. SP-ERSKINE 3 (526109) 115.0 kV to CARLISLE 3 (526160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_036 | 3 Phase fault on LG-PLSHILL 3115.00 (527194) 115 kV Bus a. Apply fault at the LG-PLSHILL 3115.00 (527194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 (526934) 115.0 kV to LG-PLSHILL 3 (527194) 115.0 kV Transmission Circuit #1 b.2. LG-PLSHILL 3 (527194) 115.0 kV to SEAGRAVES 3 (527202) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_037 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_038 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to SWISHER 3 (525212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_039 | 3 Phase fault on PLAINS_INT 3115.00 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3115.00 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 (526928) 115.0 kV to YOAKUM 3 (526934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_040 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_041 | 3 Phase fault on HART_INDUST3115.00 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3115.00 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 (525124) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 b.2. HART_INDUST3 (525124) 115.0 kV to LAMTON 3 (525414) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_042 | 3 Phase fault on N_PLAINVEW 3115.00 (525257) 115 kV Bus a. Apply fault at the N_PLAINVEW 3115.00 (525257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_PLAINVEW 3 (525257) 115.0 kV to KISER 3 (525272) 115.0 kV Transmission Circuit #1 b.2. KRS_RURL_TP3 (525226) 115.0 kV to N_PLAINVEW 3 (525257) 115.0 kV Transmission Circuit #1 b.3. KRESS_INT 3 (525192) 115.0 kV to KRS_RURL_TP3 (525226) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_043 | 3 Phase fault on KISER 3115.00 (525272) 115 kV Bus a. Apply fault at the KISER 3115.00 (525272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISER 3 (525272) 115.0 kV to COX 3 (525326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_044 | 3 Phase fault on BLANCO 3115.00 (525803) 115 kV Bus a. Apply fault at the BLANCO 3115.00 (525803) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCO 3 (525803) 115.0 kV to CROSBY 3 (525926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_045 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to BLANCO 3 (525803) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_046 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_047 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Summer | Base | P1_Fault_047 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Summer | Transfer | P1_Fault_048 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Summer | Base | P1_Fault_048 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Summer | Transfer | P1_Fault_049 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the Active Power Output of DEMPSEY_WTG1 was observed after fault settlement. The oscillations start at the end of this simulation and are not attributed to the fault. | Disable the Drive Train Model of DEMPSEY_WTG1 which caused oscillation after settlement of the fault
05 Southwest | Summer | Base | P1_Fault_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the Active Power Output of DEMPSEY_WTG1 was observed after fault settlement. The oscillations start at the end of this simulation and are not attributed to the fault. | Disable the Drive Train Model of DEMPSEY_WTG1 which caused oscillation after settlement of the fault
05 Southwest | Summer | Transfer | P1_Fault_051 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_052 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_053 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_054 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_055 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_056 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_057 | 3 Phase fault on FLE TAP4 138.00 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 138.00 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_058 | 3 Phase fault on LWSTAP 4 138.00 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 138.00 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 (511439) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_059 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_060 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to GEN-2017-033 (588760) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_061 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_062 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_063 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_064 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_065 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_066 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the Active Power Output of DEMPSEY_WTG1 was observed after fault settlement. The oscillations start at the end of this simulation and are not attributed to the fault. | Disable the Drive Train Model of DEMPSEY_WTG1 which caused oscillation after settlement of the fault
05 Southwest | Summer | Base | P1_Fault_066 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the Active Power Output of DEMPSEY_WTG1 was observed after fault settlement. The oscillations start at the end of this simulation and are not attributed to the fault. | Disable the Drive Train Model of DEMPSEY_WTG1 which caused oscillation after settlement of the fault
05 Southwest | Summer | Transfer | P1_Fault_067 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the Active Power Output of DEMPSEY_WTG1 was observed after fault settlement. The oscillations start at the end of this simulation and are not attributed to the fault. | Disable the Drive Train Model of DEMPSEY_WTG1 which caused oscillation after settlement of the fault
05 Southwest | Summer | Base | P1_Fault_067 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the Active Power Output of DEMPSEY_WTG1 was observed after fault settlement. The oscillations start at the end of this simulation and are not attributed to the fault. | Disable the Drive Train Model of DEMPSEY_WTG1 which caused oscillation after settlement of the fault
05 Southwest | Summer | Transfer | P1_Fault_068 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_069 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to RSHSPR1_MPT1 (511979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_070 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_071 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_072 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_073 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_074 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Summer | Base | P1_Fault_074 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Summer | Transfer | P1_Fault_075 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the Active Power Output of DEMPSEY_WTG1 was observed after fault settlement. The oscillations start at the end of this simulation and are not attributed to the fault. | Disable the Drive Train Model of DEMPSEY_WTG1 which caused oscillation after settlement of the fault
05 Southwest | Summer | Base | P1_Fault_075 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the Active Power Output of DEMPSEY_WTG1 was observed after fault settlement. The oscillations start at the end of this simulation and are not attributed to the fault. | Disable the Drive Train Model of DEMPSEY_WTG1 which caused oscillation after settlement of the fault
05 Southwest | Summer | Transfer | P1_Fault_076 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_077 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to GEN-2015-093 (563269) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_078 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_079 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillations observed in the active power output of GS-PHWD_GEN1 | Operational Steady State Fixes (generator voltage setpoints/transformer tap changes/shunt adjustments)
05 Southwest | Summer | Transfer | P1_Fault_080 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_081 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_082 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_083 | 3 Phase fault on PLSNT_HILL 6230.00 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6230.00 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 (524770) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_084 | 3 Phase fault on OASIS 6230.00 (524875) 230 kV Bus a. Apply fault at the OASIS 6230.00 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 (524875) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_085 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_086 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_087 | 3 Phase fault on MULSHVLY_TP3115.00 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3115.00 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 (525019) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_088 | 3 Phase fault on BC-EARTH 3115.00 (525056) 115 kV Bus a. Apply fault at the BC-EARTH 3115.00 (525056) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-EARTH 3 (525056) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_089 | 3 Phase fault on HART_INDUST3115.00 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3115.00 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 (525124) 115.0 kV to LAMTON 3 (525414) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_090 | 3 Phase fault on TULIA_TP 3115.00 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3115.00 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULIA_TP 3 (525179) 115.0 kV to KRESS_INT 3 (525192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_091 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to KRS_RURL_TP3 (525226) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_092 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_093 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_094 | 3 Phase fault on PLAINVW_TP 269.000 (525291) 69 kV Bus a. Apply fault at the PLAINVW_TP 269.000 (525291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINVW_TP 2 (525291) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_095 | 3 Phase fault on S_PLAINVEW 269.000 (525298) 69 kV Bus a. Apply fault at the S_PLAINVEW 269.000 (525298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_PLAINVEW 2 (525298) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_096 | 3 Phase fault on COX 3115.00 (525326) 115 kV Bus a. Apply fault at the COX 3115.00 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 (525326) 115.0 kV to CALLAHAN 3 (525763) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_097 | 3 Phase fault on LH-AIKEN 269.000 (525351) 69 kV Bus a. Apply fault at the LH-AIKEN 269.000 (525351) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LH-AIKEN 2 (525351) 69.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_098 | 3 Phase fault on LAMTON 3115.00 (525414) 115 kV Bus a. Apply fault at the LAMTON 3115.00 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 (525414) 115.0 kV to LC-S_OLTON+3 (525440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_099 | 3 Phase fault on SP-HALFWAY+269.000 (525432) 69 kV Bus a. Apply fault at the SP-HALFWAY+269.000 (525432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-HALFWAY+2 (525432) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_100 | 3 Phase fault on RKYFORD_TP 3115.00 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3115.00 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKYFORD_TP 3 (525446) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_101 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to PLANT_X 6 (525481) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_102 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to GEN-2017-176 (761439) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_103 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to SUNDOWN 6 (526435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_104 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to G17-146-TAP (760498) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_105 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to GEN-2017-217 (761523) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_106 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_107 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_108 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_109 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_110 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_111 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to GEN-2017-158 (762132) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_112 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_113 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_114 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_115 | 3 Phase fault on BLUECLDPOI 6230.00 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6230.00 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 (525585) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_116 | 3 Phase fault on NEEDMORE 6230.00 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6230.00 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 (525586) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_117 | 3 Phase fault on SP-ABERNTHY269.000 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY269.000 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 (525731) 69.0 kV to TUCO_INT2 2 (525816) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_118 | 3 Phase fault on HALECENTER 269.000 (525738) 69 kV Bus a. Apply fault at the HALECENTER 269.000 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 (525738) 69.0 kV to TUCO_INT 2 (525826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_119 | 3 Phase fault on CALLAHAN 3115.00 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3115.00 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 (525763) 115.0 kV to FLOYD_CNTY 3 (525780) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_120 | 3 Phase fault on FLOYD_CNTY 269.000 (525779) 69 kV Bus a. Apply fault at the FLOYD_CNTY 269.000 (525779) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 2 (525779) 69.0 kV to FLOYDADA_TP2 (525790) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_121 | 3 Phase fault on FLOYD_CNTY 269.000 (525779) 69 kV Bus a. Apply fault at the FLOYD_CNTY 269.000 (525779) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 2 (525779) 69.0 kV to LH-HARMONY 2 (525811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_122 | 3 Phase fault on LRNZ_MPT 3115.00 (525801) 115 kV Bus a. Apply fault at the LRNZ_MPT 3115.00 (525801) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LRNZ_MPT 3 (525801) 115.0 kV to BLANCO 3 (525803) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_123 | 3 Phase fault on TUCO_INT 269.000 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 269.000 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 (525826) 69.0 kV to LH-WIL&ELN+2 (525853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_124 | 3 Phase fault on TUCO_INT 269.000 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 269.000 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 (525826) 69.0 kV to SP-NEWDEAL 2 (525885) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_125 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_126 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to ANTELOPE_1 6 (525840) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_127 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Summer | Base | P1_Fault_127 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Summer | Transfer | P1_Fault_128 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency Relays cause trips in HALE_WNDG Units 1 to 3 | Frequency relay instances were disabled and the response remained stable
05 Southwest | Summer | Base | P1_Fault_128 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency Relays cause trips in HALE_WNDG Units 1 to 3 | Frequency relay instances were disabled and the response remained stable
05 Southwest | Summer | Transfer | P1_Fault_129 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency Relays cause trips in HALE_WNDG Units 1 to 3 | Frequency relay instances were disabled and the response remained stable
05 Southwest | Summer | Base | P1_Fault_129 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency Relays cause trips in HALE_WNDG Units 1 to 3 | Frequency relay instances were disabled and the response remained stable
05 Southwest | Summer | Transfer | P1_Fault_130 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_131 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_132 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_133 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to GEN-2022-147 (769921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_134 | 3 Phase fault on STANTON_W 3115.00 (526076) 115 kV Bus a. Apply fault at the STANTON_W 3115.00 (526076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_135 | 3 Phase fault on SP-ERSKINE 3115.00 (526109) 115 kV Bus a. Apply fault at the SP-ERSKINE 3115.00 (526109) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ERSKINE 3 (526109) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_136 | 3 Phase fault on SP-ERSKINE 3115.00 (526109) 115 kV Bus a. Apply fault at the SP-ERSKINE 3115.00 (526109) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ERSKINE 3 (526109) 115.0 kV to CARLISLE 3 (526160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_137 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to LP-DOUD_TP 3 (526162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_138 | 3 Phase fault on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 (526161) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_139 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_140 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_141 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_142 | 3 Phase fault on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_143 | 3 Phase fault on JONES 6230.00 (526337) 230 kV Bus a. Apply fault at the JONES 6230.00 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 (526337) 230.0 kV to GRASSLAND 6 (526677) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_144 | 3 Phase fault on SUNDOWN 6230.00 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6230.00 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 (526435) 230.0 kV to AMOCO_SS 6 (526460) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_145 | 3 Phase fault on SUNDOWN 6230.00 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6230.00 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 (526435) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_146 | 3 Phase fault on AMOCO_SS 6230.00 (526460) 230 kV Bus a. Apply fault at the AMOCO_SS 6230.00 (526460) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 (526460) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_147 | 3 Phase fault on GRASSLAND 6230.00 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6230.00 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 (526677) 230.0 kV to CIRRUS_WND 6 (526679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_148 | 3 Phase fault on AMOCOWASSON6230.00 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6230.00 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 (526784) 230.0 kV to MUSTANG 6 (527149) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_149 | 3 Phase fault on PRENTICE 3115.00 (526792) 115 kV Bus a. Apply fault at the PRENTICE 3115.00 (526792) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 (526792) 115.0 kV to YOAKUM 3 (526934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_150 | 3 Phase fault on YOAKUM 3115.00 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3115.00 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 (526934) 115.0 kV to ARCO_TP 3 (527041) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_151 | 3 Phase fault on YOAKUM 3115.00 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3115.00 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 (526934) 115.0 kV to LG-PLSHILL 3 (527194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_152 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to BRU_SUB 6 (527009) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_153 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to INK_BASIN 6 (527028) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_154 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to MUSTANG 6 (527149) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_155 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_156 | 3 Phase fault on BRU_SUB 6230.00 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6230.00 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 (527009) 230.0 kV to OXYBRU 6 (527010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_157 | 3 Phase fault on BRU_SUB 6230.00 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6230.00 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 (527009) 230.0 kV to XTO_MAHONEY6 (527011) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_158 | 3 Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 (527028) 230.0 kV to HOBBS_INT 6 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_159 | 3 Phase fault on MUSTANG 6230.00 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6230.00 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 (527149) 230.0 kV to SEMINOLE 6 (527276) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_160 | 3 Phase fault on RSVLT_CC_E 7345.00 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7345.00 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 (527655) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_161 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_162 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #ba c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_163 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #lx c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_164 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to GEN-2017-102 (762111) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_165 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_166 | 3 Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 (527867) 230.0 kV to HOBBS_INT 6 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_167 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to ANDREWS 6 (528604) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_168 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_169 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #uc c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_170 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #xa c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_171 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_172 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_173 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_174 | 3 Phase fault on G16-037-TAP 345.00 (560078) 345 kV Bus a. Apply fault at the G16-037-TAP 345.00 (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP (560078) 345.0 kV to GEN-2016-037 (587230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_175 | 3 Phase fault on GEN-2016-091345.00 (587740) 345 kV Bus a. Apply fault at the GEN-2016-091345.00 (587740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-091 (587740) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_176 | 3 Phase fault on G16-091-TAP 345.00 (587744) 345 kV Bus a. Apply fault at the G16-091-TAP 345.00 (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP (587744) 345.0 kV to GEN-2016-095 (587770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_177 | 3 Phase fault on G17-171-TAP 345.00 (760938) 345 kV Bus a. Apply fault at the G17-171-TAP 345.00 (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP (760938) 345.0 kV to GEN-2017-171 (760939) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_178 | 3 Phase fault on G17-171-TAP 345.00 (760938) 345 kV Bus a. Apply fault at the G17-171-TAP 345.00 (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP (760938) 345.0 kV to GEN-2017-171 (760939) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_179 | 3 Phase fault on G17-218TAP 230.00 (762174) 230 kV Bus a. Apply fault at the G17-218TAP 230.00 (762174) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-218TAP (762174) 230.0 kV to GEN-2017-218 (762175) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_180 | 3 Phase fault on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP (762216) 345.0 kV to GEN-2017-151 (762217) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_181 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to PNM-DC6 (599955) 230.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_182 | 3 Phase fault on MUSTANG 6230.00 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6230.00 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 (527149) 230.0 kV to GS-MUSTANG 6 (527151) 230.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_183 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the Active Power Output of DEMPSEY_WTG1 was observed after fault settlement. The oscillations start at the end of this simulation and are not attributed to the fault. | Disable the Drive Train Model of DEMPSEY_WTG1 which caused oscillation after settlement of the fault
05 Southwest | Summer | Base | P1_Fault_183 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the Active Power Output of DEMPSEY_WTG1 was observed after fault settlement. The oscillations start at the end of this simulation and are not attributed to the fault. | Disable the Drive Train Model of DEMPSEY_WTG1 which caused oscillation after settlement of the fault
05 Southwest | Summer | Transfer | P1_Fault_184 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to AMA_SOUTH 3 (524414) 115.0 kV to AMA_SO_TR1 1 (524410) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_185 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to ROOSEVELT 3 (524908) 115.0 kV to ROSEVLT_TR11 (524907) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_186 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to KRESS_INT 2 (525191) 69.0 kV to KRESS_TR1 1 (525190) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_187 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV to SWISHER_TR11 (525211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_188 | 3 Phase fault on COX 3115.00 (525326) 115 kV Bus a. Apply fault at the COX 3115.00 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 (525326) 115.0 kV to COX 2 (525325) 69.0 kV to COX_TR1 1 (525324) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_189 | 3 Phase fault on LAMTON 3115.00 (525414) 115 kV Bus a. Apply fault at the LAMTON 3115.00 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 (525414) 115.0 kV to LAMTON 2 (525413) 69.0 kV to LAMTON_TR1 1 (525412) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_190 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR1 1 (525451) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_191 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR2 1 (525452) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_192 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR21 (525458) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_193 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR11 (525459) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_194 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to PLANT_X 3 (525480) 115.0 kV to PLANTX_TR1 1 (525479) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_195 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_196 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_197 | 3 Phase fault on LAMB_CNTY 3115.00 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3115.00 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV to LAMB_TR1 1 (525631) 13.2 kV Three Winding #1 b.2. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV to LAMB_TR2 1 (525632) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_198 | 3 Phase fault on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_199 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV to FLOYD_TR1 1 (525777) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_200 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV to FLOYD_TR2 1 (525778) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_201 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT2 2 (525816) 69.0 kV to TUCO_TR7 1 (525814) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_202 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV to TUCO_TR5 1 (525822) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_203 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV to TUCO_TR6 1 (525823) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_204 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_205 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_206 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_207 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_208 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to CARLISLE 2 (526159) 69.0 kV to CRLSLE_TR2 1 (526158) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_209 | 3 Phase fault on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 (526161) 230.0 kV to CARLISLE 3 (526160) 115.0 kV to CRLSLE_TR1 1 (526157) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_210 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV to LBB_STH TR11 (526265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_211 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV to LBB_STH TR31 (526264) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_212 | 3 Phase fault on LUBBCK_EST 3115.00 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3115.00 (526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV to LBB_EST TR21 (526295) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_213 | 3 Phase fault on LUBBCK_EST 3115.00 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3115.00 (526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV to LBB_EST TR31 (526296) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_214 | 3 Phase fault on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV to LBB_EST TR11 (526294) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_215 | 3 Phase fault on WOLFFORTH 6230.00 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6230.00 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 (526525) 230.0 kV to WOLFFORTH 3 (526524) 115.0 kV to WOLFRTH_TR11 (526522) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_216 | 3 Phase fault on GRASSLAND 6230.00 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6230.00 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 (526677) 230.0 kV to GRASSLAND 3 (526676) 115.0 kV to GRASLND_TR11 (526674) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_217 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM 3 (526934) 115.0 kV to YOAKUM_TR1 1 (526931) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_218 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM 3 (526934) 115.0 kV to YOAKUM_TR2 1 (526932) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_219 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_220 | 3 Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 (527028) 230.0 kV to INK_BASIN 3 (527027) 115.0 kV to INKBASN_TR 1 (527026) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_221 | 3 Phase fault on MUSTANG 6230.00 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6230.00 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 (527149) 230.0 kV to MUSTANG 3 (527146) 115.0 kV to MUSTANG_TR11 (527143) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_222 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to HOBBS_INT 3 (527891) 115.0 kV to HOBBS_TR1 1 (527890) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_223 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to HOBBS_INT 3 (527891) 115.0 kV to HOBBS_TR2 1 (527889) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_224 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV to HOBBS_TR3 1 (527895) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_225 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to KIOWA 3 (527966) 115.0 kV to KIOWA_TR1 1 (527964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_226 | 3 Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 (528027) 345.0 kV to RDRUNNER 3 (528025) 115.0 kV to RDRNNER_TR11 (528023) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_227 | 3 Phase fault on OKLAUN 7 345.00 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7 345.00 (599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 (599891) 345.0 kV to OKLEHV24 (590001) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_228 | 3 Phase fault on OKLAUN 7 345.00 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7 345.00 (599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 (599891) 345.0 kV to OKLEHV14 (590003) 138.0 kV to OK1TERT (590004) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_229 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_230 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the Active Power Output of DEMPSEY_WTG1 was observed after fault settlement. The oscillations start at the end of this simulation and are not attributed to the fault. | Disable the Drive Train Model of DEMPSEY_WTG1 which caused oscillation after settlement of the fault
05 Southwest | Summer | Base | P1_Fault_230 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the Active Power Output of DEMPSEY_WTG1 was observed after fault settlement. The oscillations start at the end of this simulation and are not attributed to the fault. | Disable the Drive Train Model of DEMPSEY_WTG1 which caused oscillation after settlement of the fault
05 Southwest | Summer | Transfer | P1_Fault_231 | 3 Phase fault on OKLAUN HVDC7345.00 (511565) 345 kV Bus a. Apply fault at the OKLAUN HVDC7345.00 (511565) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN HVDC7 (511565) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_232 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_233 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_234 | 3 Phase fault on FLOYD_CNTY 269.000 (525779) 69 kV Bus a. Apply fault at the FLOYD_CNTY 269.000 (525779) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 2 (525779) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_235 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_236 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_237 | 3 Phase fault on HALE_WNDCL16230.00 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16230.00 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 (525957) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_238 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_239 | 3 Phase fault on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 (526161) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_240 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_241 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_242 | 3 Phase fault on OKLAUN 7 345.00 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7 345.00 (599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 (599891) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_243 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_244 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_245 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_246 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_247 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_248 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_249 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_250 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_251 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2015-082 (585190) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_252 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 7 (523101) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_253 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOVUS1 7 (523112) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_254 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_255 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_256 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_257 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_258 | 3 Phase fault on G16-003-TAP 345.00 (560071) 345 kV Bus a. Apply fault at the G16-003-TAP 345.00 (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to GEN-2016-003 (587020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_259 | 3 Phase fault on G16-003-TAP 345.00 (560071) 345 kV Bus a. Apply fault at the G16-003-TAP 345.00 (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to GEN-2017-011 (588560) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_260 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_261 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P1_Fault_263 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_001 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_002 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_003 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. G17-171-TAP (760938) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_004 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 6 (525531) 230.0 kV to TOLK_1 1 (525561) 24.0 kV Two Winding #1 b.2. TOLK_TR 1 (525537) 13.2 kV to TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV Three Winding #2 b.3. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 b.4. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.5. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #2 b.7. TOLK 6 (525531) 230.0 kV to TOLK_2 1 (525562) 24.0 kV Two Winding #1 b.8. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.9. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 b.10. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 b.11. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.12. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.13. TOLK 6 (525531) 230.0 kV to GEN-2017-158 (762132) 230.0 kV Transmission Circuit #1 b.14. TOLK 6 (525531) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #1 b.15. TOLK 6 (525531) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_005 | Single Phase Fault with Stuck Breaker on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply Fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.2. LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_006 | Single Phase Fault with Stuck Breaker on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply Fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBB_STH TR11 (526265) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #1 b.2. LBB_STH TR31 (526264) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #2 b.3. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.4. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 b.5. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_007 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply Fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBB_EST TR11 (526294) 13.2 kV to LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Three Winding #1 b.2. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_008 | Single Phase Fault with Stuck Breaker on AMOCO_SS 6230.00 (526460) 230 kV Bus a. Apply Fault at the AMOCO_SS 6230.00 (526460) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNDOWN 6 (526435) 230.0 kV to AMOCO_SS 6 (526460) 230.0 kV Transmission Circuit #1 b.2. AMOCO_SS 6 (526460) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_009 | Single Phase Fault with Stuck Breaker on GRASSLAND 6230.00 (526677) 230 kV Bus a. Apply Fault at the GRASSLAND 6230.00 (526677) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRASLND_TR11 (526674) 13.2 kV to GRASSLAND 6 (526677) 230.0 kV to GRASSLAND 3 (526676) 115.0 kV Three Winding #1 b.2. JONES 6 (526337) 230.0 kV to GRASSLAND 6 (526677) 230.0 kV Transmission Circuit #1 b.3. GRASSLAND 6 (526677) 230.0 kV to CIRRUS_WND 6 (526679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_010 | Single Phase Fault with Stuck Breaker on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply Fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALE_TR1 1 (525451) 13.2 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV Three Winding #1 b.2. HALE_TR2 1 (525452) 13.2 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV Three Winding #2 b.3. KRESS_INT 3 (525192) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.4. COX 3 (525326) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.5. LAMTON 3 (525414) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.6. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 b.7. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_011 | Single Phase Fault with Stuck Breaker on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply Fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMB_TR1 1 (525631) 13.2 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Three Winding #1 b.2. LAMB_TR2 1 (525632) 13.2 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Three Winding #2 b.3. LAMB_TR3 1 (525633) 13.2 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Three Winding #1 b.4. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.6. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 b.7. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_012 | Single Phase Fault with Stuck Breaker on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply Fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLOYD_TR1 1 (525777) 13.2 kV to FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV Three Winding #1 b.2. FLOYD_TR2 1 (525778) 13.2 kV to FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV Three Winding #2 b.3. CALLAHAN 3 (525763) 115.0 kV to FLOYD_CNTY 3 (525780) 115.0 kV Transmission Circuit #1 b.4. FLOYD_CNTY 3 (525780) 115.0 kV to BLANCO 3 (525803) 115.0 kV Transmission Circuit #1 b.5. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_013 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.2. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.3. TUCO_TR7 1 (525814) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT2 2 (525816) 69.0 kV Three Winding #1 b.4. TUCO_TR5 1 (525822) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #2 b.5. TUCO_TR6 1 (525823) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #1 b.6. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.7. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.8. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.9. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.13. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 b.14. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_014 | Single Phase Fault with Stuck Breaker on STANTON_W 3115.00 (526076) 115 kV Bus a. Apply Fault at the STANTON_W 3115.00 (526076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.2. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_015 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply Fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBB_EST TR11 (526294) 13.2 kV to LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Three Winding #1 b.2. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.4. LBB_EST TR21 (526295) 13.2 kV to LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV Three Winding #1 b.5. LBB_EST TR31 (526296) 13.2 kV to LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV Three Winding #2 b.6. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.7. CROSBY 3 (525926) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.8. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_016 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_017 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_018 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. G17-171-TAP (760938) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_019 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.2. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.3. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.4. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.5. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.6. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.7. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.8. TUCO_TR5 1 (525822) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #2 b.9. TUCO_TR6 1 (525823) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #1 b.10. TUCO_TR7 1 (525814) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT2 2 (525816) 69.0 kV Three Winding #1 b.14. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 b.15. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_020 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.2. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.3. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.4. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.7. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR5 1 (525822) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #2 b.10. TUCO_TR6 1 (525823) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #1 b.11. TUCO_TR7 1 (525814) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT2 2 (525816) 69.0 kV Three Winding #1 b.15. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 b.16. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_021 | Single Phase Fault with Stuck Breaker on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply Fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMTON 3 (525414) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.2. KRESS_INT 3 (525192) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.3. COX 3 (525326) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.4. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.5. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 b.6. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR1 1 (525451) 13.2 kV Three Winding #1 b.7. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR2 1 (525452) 13.2 kV Three Winding #2 b.10. PLAINVW_TP 2 (525291) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 b.11. S_PLAINVEW 2 (525298) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 b.12. SP-HALFWAY+2 (525432) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_022 | Single Phase Fault with Stuck Breaker on SP-ERSKINE 3115.00 (526109) 115 kV Bus a. Apply Fault at the SP-ERSKINE 3115.00 (526109) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SP-ERSKINE 3 (526109) 115.0 kV to CARLISLE 3 (526160) 115.0 kV Transmission Circuit #1 b.2. SP-ERSKINE 3 (526109) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.3. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.4. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_023 | Single Phase Fault with Stuck Breaker on LAMB_CNTY 269.000 (525635) 69 kV Bus a. Apply Fault at the LAMB_CNTY 269.000 (525635) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 b.2. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 b.3. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.4. LAMB_TR3 1 (525633) 13.2 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Three Winding #1 b.5. LAMB_TR1 1 (525631) 13.2 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Three Winding #1 b.7. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV to LAMB_TR2 1 (525632) 13.2 kV Three Winding #2 b.8. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 b.10. W_LITTLFLD 2 (525613) 69.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Transmission Circuit #1 b.11. LTFLD_S&CTY2 (525620) 69.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Transmission Circuit #1 b.12. LAMB_CNTY 2 (525635) 69.0 kV to LC-LTTLFLD+2 (525650) 69.0 kV Transmission Circuit #1 b.13. LAMB_CNTY 2 (525635) 69.0 kV to LC-LUMSCHAP2 (525687) 69.0 kV Transmission Circuit #1 b.16. LTFLD_S&CTY2 (525620) 69.0 kV to W_ANTON_TP 2 (525657) 69.0 kV Transmission Circuit #1 b.17. LC-LTTLFLD+2 (525650) 69.0 kV to W_ANTON_TP 2 (525657) 69.0 kV Transmission Circuit #1 b.18. W_ANTON_TP 2 (525657) 69.0 kV to LC-SPD&HART2 (525664) 69.0 kV Transmission Circuit #1 b.19. W_ANTON_TP 2 (525657) 69.0 kV to BAINER 2 (525671) 69.0 kV Transmission Circuit #1 b.20. LC-SPD&HART2 (525664) 69.0 kV to CNTYLINE_TP2 (525723) 69.0 kV Transmission Circuit #1 b.21. BAINER 2 (525671) 69.0 kV to W_ANTON 2 (525678) 69.0 kV Transmission Circuit #1 b.22. LC-LUMSCHAP2 (525687) 69.0 kV to HOBGOOD 2 (525694) 69.0 kV Transmission Circuit #1 b.23. HOBGOOD 2 (525694) 69.0 kV to PUMP/YH_TP 2 (525697) 69.0 kV Transmission Circuit #1 b.24. PUMP/YH_TP 2 (525697) 69.0 kV to YELLOWHOUSE2 (525703) 69.0 kV Transmission Circuit #1 b.25. PUMP/YH_TP 2 (525697) 69.0 kV to MIDAMERI#2 2 (525708) 69.0 kV Transmission Circuit #1 b.26. PHLLPPMP#2 2 (525701) 69.0 kV to YELLOWHOUSE2 (525703) 69.0 kV Transmission Circuit #1 b.27. MIDAMERI#2 2 (525708) 69.0 kV to WHITHARRAL 2 (525717) 69.0 kV Transmission Circuit #1 b.28. WHITHARRAL 2 (525717) 69.0 kV to LC-HODGE_TP2 (525995) 69.0 kV Transmission Circuit #1 b.29. AMHERST 2 (525606) 69.0 kV to W_LITTLFLD 2 (525613) 69.0 kV Transmission Circuit #1 b.30. LC-SANDHLL+2 (525599) 69.0 kV to AMHERST 2 (525606) 69.0 kV Transmission Circuit #1 b.31. SUDANRURAL 2 (525592) 69.0 kV to LC-SANDHLL+2 (525599) 69.0 kV Transmission Circuit #1 b.32. LC-BECK +2 (525045) 69.0 kV to SUDANRURAL 2 (525592) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_024 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 3115.00 (526298) 115 kV Bus a. Apply Fault at the LUBBCK_EST 3115.00 (526298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSBY 3 (525926) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.2. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.3. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.4. LBB_EST TR11 (526294) 13.2 kV to LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Three Winding #1 b.5. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV to LBB_EST TR21 (526295) 13.2 kV Three Winding #1 b.6. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV to LBB_EST TR31 (526296) 13.2 kV Three Winding #2 b.7. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 6 (526299) 230.0 kV to LBB_EST TR11 (526294) 13.2 kV Three Winding #1 b.10. PLANTERS 2 (526284) 69.0 kV to LUBBCK_EST 2 (526297) 69.0 kV Transmission Circuit #1 b.11. LUBBCK_EST 2 (526297) 69.0 kV to CLUTTER 2 (526310) 69.0 kV Transmission Circuit #1 b.12. LUBBCK_EST 2 (526297) 69.0 kV to SLATON 2 (526562) 69.0 kV Transmission Circuit #1 b.15. ACCO 2 (526249) 69.0 kV to CLUTTER 2 (526310) 69.0 kV Transmission Circuit #1 b.16. SW_6786_S 2 (526087) 69.0 kV to PLANTERS 2 (526284) 69.0 kV Transmission Circuit #1 b.17. STANTON_E 2 (526075) 69.0 kV to SW_6786_S 2 (526087) 69.0 kV Transmission Circuit #1 b.18. SW_6786_N 2 (526086) 69.0 kV to SW_6786_S 2 (526087) 69.0 kV Transmission Circuit #z1 b.19. STANTON_N 2 (526073) 69.0 kV to STANTON_E 2 (526075) 69.0 kV Transmission Circuit #z1 b.20. STANTON_N 2 (526073) 69.0 kV to SW_6786_N 2 (526086) 69.0 kV Transmission Circuit #1 b.21. SW_6786_N 2 (526086) 69.0 kV to SP-HETTLER 2 (526102) 69.0 kV Transmission Circuit #1 b.22. SP-HETTLER 2 (526102) 69.0 kV to SP-IDALOU +2 (526116) 69.0 kV Transmission Circuit #1 b.23. SP-IDALOU +2 (526116) 69.0 kV to VICKERS 2 (526123) 69.0 kV Transmission Circuit #1 b.24. SP-ACUFF +2 (525906) 69.0 kV to VICKERS 2 (526123) 69.0 kV Transmission Circuit #1 b.25. SP-ACUFF +2 (525906) 69.0 kV to CROSBY 2 (525925) 69.0 kV Transmission Circuit #1 b.26. SLATON 2 (526562) 69.0 kV to SP-SLATON 2 (526569) 69.0 kV Transmission Circuit #1 b.27. SP-SLATON 2 (526569) 69.0 kV to SOUTHLAND 2 (526576) 69.0 kV Transmission Circuit #1 b.28. SOUTHLAND 2 (526576) 69.0 kV to LG-HAKBERRY2 (526583) 69.0 kV Transmission Circuit #1 b.29. LG-HAKBERRY2 (526583) 69.0 kV to DIEKEMPER 2 (526592) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_025 | Single Phase Fault with Stuck Breaker on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply Fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALE_TR2 1 (525452) 13.2 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV Three Winding #2 b.2. LAMTON 3 (525414) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.3. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 b.4. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.5. KRESS_INT 3 (525192) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.6. COX 3 (525326) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.7. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR1 1 (525451) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_026 | Single Phase Fault with Stuck Breaker on MUSTANG 6230.00 (527149) 230 kV Bus a. Apply Fault at the MUSTANG 6230.00 (527149) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSTANG 6 (527149) 230.0 kV to MUSTANG_3 1 (527163) 19.0 kV Two Winding #1 b.2. YOAKUM 6 (526935) 230.0 kV to MUSTANG 6 (527149) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_027 | Single Phase Fault with Stuck Breaker on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply Fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. LBB_STH TR31 (526264) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #2 b.3. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 b.4. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 b.5. ALLEN 3 (526213) 115.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Transmission Circuit #1 b.6. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.7. WOODROW 3 (526602) 115.0 kV to LYNN_CNTY 3 (526656) 115.0 kV Transmission Circuit #1 b.8. LUBBCK_STH 3 (526268) 115.0 kV to WOODROW 3 (526602) 115.0 kV Transmission Circuit #1 b.9. LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV to LBB_STH TR11 (526265) 13.2 kV Three Winding #1 b.11. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_STH 2 (526267) 69.0 kV to LBB_STH TR21 (526266) 13.2 kV Three Winding #1 b.14. IVORY 2 (526205) 69.0 kV to LUBBCK_STH 2 (526267) 69.0 kV Transmission Circuit #1 b.15. IVORY_TP 2 (526256) 69.0 kV to LUBBCK_STH 2 (526267) 69.0 kV Transmission Circuit #1 b.19. IVORY 2 (526205) 69.0 kV to IVORY_TP 2 (526256) 69.0 kV Transmission Circuit #z1 b.20. ACCO 2 (526249) 69.0 kV to IVORY_TP 2 (526256) 69.0 kV Transmission Circuit #1 b.21. ACCO 2 (526249) 69.0 kV to CLUTTER 2 (526310) 69.0 kV Transmission Circuit #1 b.22. IVORY 2 (526205) 69.0 kV to BATTON_S 2 (526228) 69.0 kV Transmission Circuit #1 b.23. BATTON_N 2 (526221) 69.0 kV to BATTON_S 2 (526228) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_028 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply Fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. LBB_EST TR11 (526294) 13.2 kV to LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_029 | Single Phase Fault with Stuck Breaker on NEWHART 6230.00 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 b.2. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_030 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER_TR11 (525211) 13.2 kV to SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV Three Winding #1 b.2. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_031 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_032 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_033 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. TUCO_INT 6 (525830) 230.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_034 | Single Phase Fault with Stuck Breaker on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM_TR1 1 (526931) 13.2 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM 3 (526934) 115.0 kV Three Winding #1 b.2. NEEDMORE 6 (525586) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_035 | Single Phase Fault with Stuck Breaker on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AMOCO_SS 6 (526460) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6 (526935) 230.0 kV to INK_BASIN 6 (527028) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_036 | Single Phase Fault with Stuck Breaker on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply Fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. LBB_STH TR31 (526264) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #2 b.3. LBB_STH TR11 (526265) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #1 b.4. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 b.5. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_037 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_038 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.2. TUCO_INT 6 (525830) 230.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_039 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.2. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.3. TUCO_INT 6 (525830) 230.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_040 | Single Phase Fault with Stuck Breaker on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply Fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBB_STH TR11 (526265) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #1 b.2. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.3. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 b.4. LBB_STH TR31 (526264) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #2 b.5. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_041 | Single Phase Fault with Stuck Breaker on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply Fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.2. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. RSVLT_CC_E 7 (527655) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.4. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_CC_E 7 (527655) 345.0 kV Transmission Circuit #1 b.5. MILO_WND (577121) 34.5 kV to RSVLT_CC_E 7 (527655) 345.0 kV Two Winding #1 b.6. MILO_WIND 1 (527653) 0.7 kV to MILO_CB (577120) 34.5 kV Two Winding #1 b.7. RSVLT_GEN1 1 (527651) 0.7 kV to RSVLT_WIND11 (527658) 34.5 kV Two Winding #1 b.8. RSVLT_GEN2 1 (527652) 0.7 kV to RSVLT_WIND21 (527659) 34.5 kV Two Winding #1 b.9. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_COL1 7 (527666) 345.0 kV Transmission Circuit #1 b.10. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_COL2 7 (527667) 345.0 kV Transmission Circuit #1 b.11. SAGA_SCOL 7 (527610) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.12. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #ba b.13. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #lx b.14. CROSSROADS 7 (527656) 345.0 kV to GEN-2017-102 (762111) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_042 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_TR3 1 (527895) 13.2 kV to HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV Three Winding #1 | P4 | Yes | Yes | No | Yes | No | Yes | Yes | Transient Post Fault Voltage exceeds 1.2 p.u. and stabilizes above 1.1 p.u. at PHANTOM 3 115 kV and NORTH_LOVNG3 115 kV busbars | Operational Steady State Fixes (generator voltage setpoints/transformer tap changes/shunt adjustments)
05 Southwest | Summer | Transfer | P4_Fault_043 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_044 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_045 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_046 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_047 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.4. TUCO_INT 7 (525832) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_048 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_TR3 1 (527895) 13.2 kV to HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV Three Winding #1 | P4 | Yes | Yes | No | Yes | No | Yes | Yes | Transient Post Fault Voltage exceeds 1.2 p.u. and stabilizes above 1.1 p.u. at PHANTOM 3 115 kV and NORTH_LOVNG3 115 kV busbars | Operational Steady State Fixes (generator voltage setpoints/transformer tap changes/shunt adjustments)
05 Southwest | Summer | Transfer | P4_Fault_049 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_TR1 (526937) 13.2 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_050 | Single Phase Fault with Stuck Breaker on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 7 (528015) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.3. RDRNNER_TR11 (528023) 13.2 kV to RDRUNNER 7 (528027) 345.0 kV to RDRUNNER 3 (528025) 115.0 kV Three Winding #1 b.4. HOBBS_INT 7 (527896) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #uc b.5. HOBBS_INT 7 (527896) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #xa | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_051 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_052 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_053 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_054 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_055 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 b.4. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_056 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 b.4. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_057 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_058 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 b.4. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_059 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_060 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_061 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_062 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_063 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 b.6. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_064 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_065 | Single Phase Fault with Stuck Breaker on GRPLNS-CB2-134.500 (523126) 34.5 kV Bus a. Apply Fault at the GRPLNS-CB2-134.500 (523126) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_066 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.6. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_067 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_068 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_069 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_070 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_071 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_072 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_074 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #2 b.2. TOLK 6 (525531) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_075 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_076 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_077 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (762216) 345.0 kV to O.K.U.-7 (511456) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (762216) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_078 | Single Phase Fault with Stuck Breaker on WWDBORDT 345.00 (755000) 345 kV Bus a. Apply Fault at the WWDBORDT 345.00 (755000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDBORDT (755000) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. WWDBORDT (755000) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | No | Yes | Yes | Transient Post Fault Voltage exceeds 1.2 p.u. and stabilizes above 1.1 p.u. at Border 7 345 kV Busbar | Operational Steady State Fixes (generator voltage setpoints/transformer tap changes/shunt adjustments)
05 Southwest | Summer | Transfer | P4_Fault_079 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_080 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 b.2. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_081 | Single Phase Fault with Stuck Breaker on JONES 6230.00 (526337) 230 kV Bus a. Apply Fault at the JONES 6230.00 (526337) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES 6 (526337) 230.0 kV to LUBBCK_STH 6 (526269) 230.0 kV Transmission Circuit #1 b.2. JONES 6 (526337) 230.0 kV to LUBBCK_STH 6 (526269) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_082 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV to SWISHER_TR11 (525211) 13.2 kV Three Winding #1 b.4. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.5. SWISHER 6 (525213) 230.0 kV to Switched Shunt # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_083 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.3. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.4. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 b.5. TUCO_INT 7 (525832) 345.0 kV to GEN-2022-147 (769921) 345.0 kV Transmission Circuit #1 b.6. TUCO_INT 7 (525832) 345.0 kV to ELK_2 1 (525845) 18.0 kV Transformer #1 b.7. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.8. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_084 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.2. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 b.3. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 b.4. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.5. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.6. TOLK 6 (525531) 230.0 kV to GEN-2017-158 (762132) 230.0 kV Transmission Circuit #1 b.7. TOLK 6 (525531) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #1 b.8. TOLK 6 (525531) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #2 b.9. TOLK 6 (525531) 230.0 kV to TOLK_1 1 (525561) 24.0 kV Transformer #1 b.10. TOLK 6 (525531) 230.0 kV to TOLK_2 1 (525562) 24.0 kV Transformer #1 b.11. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #2 b.12. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_085 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 b.3. G17-151TAP (762216) 345.0 kV to GEN-2017-151 (762217) 345.0 kV Transmission Circuit #1 b.4. G17-151TAP (762216) 345.0 kV to Switched Shunt # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_086 | Single Phase Fault with Stuck Breaker on WWDBORDT 345.00 (755000) 345 kV Bus a. Apply Fault at the WWDBORDT 345.00 (755000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_087 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Summer | Transfer | P4_Fault_088 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 b.2. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 b.3. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.4. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 b.5. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.6. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.7. TUCO_INT 6 (525830) 230.0 kV to ANTELOPE_1 6 (525840) 230.0 kV Transmission Circuit #1 b.8. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.9. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.10. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.11. TUCO_SVC 1 (525820) 13.0 kV to TUCO_INT 6 (525830) 230.0 kV Transformer #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_001 | 3 Phase fault on RPPAPER4 138.00 (511512) 138 kV Bus a. Apply fault at the RPPAPER4 138.00 (511512) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 (511488) 138.0 kV to RPPAPER4 (511512) 138.0 kV Transmission Circuit #1 b.2. LWSTAP 4 (511439) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 b.3. LWSTAP 4 (511439) 138.0 kV to RPPAPER4 (511512) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_002 | 3 Phase fault on COMANC-4 138.00 (511437) 138 kV Bus a. Apply fault at the COMANC-4 138.00 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 (511437) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_003 | 3 Phase fault on COMMTAP4 138.00 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 138.00 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 b.2. DUNCAN-4 (511453) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 b.3. COMMTAP4 (511494) 138.0 kV to OMDUNCN4 (529304) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_004 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to SHERID4 (511474) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_005 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_006 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_007 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#4-1 (511414) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_008 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_009 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#1-1 (511416) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_010 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 (511466) 69.0 kV to L.E.S.-4 (511467) 138.0 kV to LES#2-1 (511415) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_011 | 3 Phase fault on ELKCITY6 230.00 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 230.00 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 (511490) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_012 | 3 Phase fault on SWEETWT6 230.00 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 230.00 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 (511541) 230.0 kV to CHISHOLM6 (511557) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_013 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.4. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_014 | 3 Phase fault on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.2. LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_015 | 3 Phase fault on RKYFORD_TP 3115.00 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3115.00 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 (525414) 115.0 kV to LC-S_OLTON+3 (525440) 115.0 kV Transmission Circuit #1 b.2. LC-S_OLTON+3 (525440) 115.0 kV to RKYFORD_TP 3 (525446) 115.0 kV Transmission Circuit #1 b.3. ROCKYFORD 3 (525393) 115.0 kV to RKYFORD_TP 3 (525446) 115.0 kV Transmission Circuit #1 b.4. RKYFORD_TP 3 (525446) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_016 | 3 Phase fault on LAMTON 3115.00 (525414) 115 kV Bus a. Apply fault at the LAMTON 3115.00 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 (525414) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_017 | 3 Phase fault on LAMB_CNTY 3115.00 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3115.00 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_018 | 3 Phase fault on PRENTICE 3115.00 (526792) 115 kV Bus a. Apply fault at the PRENTICE 3115.00 (526792) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 (526736) 115.0 kV to PRENTICE 3 (526792) 115.0 kV Transmission Circuit #1 b.2. PRENTICE 3 (526792) 115.0 kV to YOAKUM 3 (526934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_019 | 3 Phase fault on TULIA_TP 3115.00 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3115.00 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MU-TULIA 3 (522800) 115.0 kV to TULIA_TP 3 (525179) 115.0 kV Transmission Circuit #1 b.2. HAPPY_INT 3 (525154) 115.0 kV to TULIA_TP 3 (525179) 115.0 kV Transmission Circuit #1 b.3. TULIA_TP 3 (525179) 115.0 kV to KRESS_INT 3 (525192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_020 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_021 | 3 Phase fault on CROSBY 3115.00 (525926) 115 kV Bus a. Apply fault at the CROSBY 3115.00 (525926) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSBY 3 (525926) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_022 | 3 Phase fault on LP-DOUD_TP 3115.00 (526162) 115 kV Bus a. Apply fault at the LP-DOUD_TP 3115.00 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to LP-DOUD_TP 3 (526162) 115.0 kV Transmission Circuit #1 b.2. LP-DOUD_TP 3 (526162) 115.0 kV to LP-DOUD 3 (526176) 115.0 kV Transmission Circuit #1 b.3. LP-DOUD_TP 3 (526162) 115.0 kV to SP-WOLF_TP 3 (526481) 115.0 kV Transmission Circuit #1 b.4. YUMA_INT 3 (526475) 115.0 kV to SP-WOLF_TP 3 (526481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_023 | 3 Phase fault on CALLAHAN 3115.00 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3115.00 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 (525763) 115.0 kV to FLOYD_CNTY 3 (525780) 115.0 kV Transmission Circuit #1 b.2. COX 3 (525326) 115.0 kV to CALLAHAN 3 (525763) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_024 | 3 Phase fault on COX 3115.00 (525326) 115 kV Bus a. Apply fault at the COX 3115.00 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 (525326) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_025 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_026 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_027 | 3 Phase fault on MULSHVLY_TP3115.00 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3115.00 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 (525019) 115.0 kV to BAILEYCO 3 (525028) 115.0 kV Transmission Circuit #1 b.2. MULESHVALLY3 (525018) 115.0 kV to MULSHVLY_TP3 (525019) 115.0 kV Transmission Circuit #1 b.3. MULSHVLY_TP3 (525019) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_028 | 3 Phase fault on PLANT_X 3115.00 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3115.00 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_029 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_030 | 3 Phase fault on STANTON_W 3115.00 (526076) 115 kV Bus a. Apply fault at the STANTON_W 3115.00 (526076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.2. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_031 | 3 Phase fault on LUBBCK_STH 3115.00 (526268) 115 kV Bus a. Apply fault at the LUBBCK_STH 3115.00 (526268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_032 | 3 Phase fault on BC-KELLEY +3115.00 (525050) 115 kV Bus a. Apply fault at the BC-KELLEY +3115.00 (525050) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 (524746) 115.0 kV to BC-KELLEY +3 (525050) 115.0 kV Transmission Circuit #1 b.2. BC-KELLEY +3 (525050) 115.0 kV to BC-EARTH 3 (525056) 115.0 kV Transmission Circuit #1 b.3. BC-EARTH 3 (525056) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_033 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to MURPHY 3 (526192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_034 | 3 Phase fault on ARCO_TP 3115.00 (527041) 115 kV Bus a. Apply fault at the ARCO_TP 3115.00 (527041) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 (526934) 115.0 kV to ARCO_TP 3 (527041) 115.0 kV Transmission Circuit #1 b.2. BENNETT 3 (527018) 115.0 kV to ARCO_TP 3 (527041) 115.0 kV Transmission Circuit #1 b.3. BENNETT 3 (527018) 115.0 kV to ODC_TP 3 (527051) 115.0 kV Transmission Circuit #1 b.4. ODC_TP 3 (527051) 115.0 kV to SHELL_CO2 3 (527062) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_035 | 3 Phase fault on SP-ERSKINE 3115.00 (526109) 115 kV Bus a. Apply fault at the SP-ERSKINE 3115.00 (526109) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ERSKINE 3 (526109) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.2. SP-ERSKINE 3 (526109) 115.0 kV to CARLISLE 3 (526160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_036 | 3 Phase fault on LG-PLSHILL 3115.00 (527194) 115 kV Bus a. Apply fault at the LG-PLSHILL 3115.00 (527194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 (526934) 115.0 kV to LG-PLSHILL 3 (527194) 115.0 kV Transmission Circuit #1 b.2. LG-PLSHILL 3 (527194) 115.0 kV to SEAGRAVES 3 (527202) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_037 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_038 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to SWISHER 3 (525212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_039 | 3 Phase fault on PLAINS_INT 3115.00 (526928) 115 kV Bus a. Apply fault at the PLAINS_INT 3115.00 (526928) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINS_INT 3 (526928) 115.0 kV to YOAKUM 3 (526934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_040 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_041 | 3 Phase fault on HART_INDUST3115.00 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3115.00 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 (525124) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 b.2. HART_INDUST3 (525124) 115.0 kV to LAMTON 3 (525414) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_042 | 3 Phase fault on N_PLAINVEW 3115.00 (525257) 115 kV Bus a. Apply fault at the N_PLAINVEW 3115.00 (525257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N_PLAINVEW 3 (525257) 115.0 kV to KISER 3 (525272) 115.0 kV Transmission Circuit #1 b.2. KRS_RURL_TP3 (525226) 115.0 kV to N_PLAINVEW 3 (525257) 115.0 kV Transmission Circuit #1 b.3. KRESS_INT 3 (525192) 115.0 kV to KRS_RURL_TP3 (525226) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_043 | 3 Phase fault on KISER 3115.00 (525272) 115 kV Bus a. Apply fault at the KISER 3115.00 (525272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISER 3 (525272) 115.0 kV to COX 3 (525326) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_044 | 3 Phase fault on BLANCO 3115.00 (525803) 115 kV Bus a. Apply fault at the BLANCO 3115.00 (525803) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCO 3 (525803) 115.0 kV to CROSBY 3 (525926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_045 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to BLANCO 3 (525803) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_046 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_047 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Winter | Base | P1_Fault_047 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Winter | Transfer | P1_Fault_048 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Winter | Base | P1_Fault_048 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Winter | Transfer | P1_Fault_049 | 3 Phase fault on MINCO 7 345.00 (514801) 345 kV Bus a. Apply fault at the MINCO 7 345.00 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 (514801) 345.0 kV to GRACMNT7 (515800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_050 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_051 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_052 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_053 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_054 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_055 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_056 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT4 (515802) 138.0 kV to GRACMNT7 (515800) 345.0 kV to GRCMNT11 (515801) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_057 | 3 Phase fault on FLE TAP4 138.00 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 138.00 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 (511423) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_058 | 3 Phase fault on LWSTAP 4 138.00 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 138.00 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 (511439) 138.0 kV to L.E.S.-4 (511467) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_059 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_060 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to GEN-2017-033 (588760) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_061 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_062 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to ELGINJT4 (511486) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_063 | 3 Phase fault on L.E.S.-4 138.00 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 138.00 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 (511467) 138.0 kV to COMMTAP4 (511494) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_064 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_065 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_066 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_067 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_068 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_069 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to RSHSPR1_MPT1 (511979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_070 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_071 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_072 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_073 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_074 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Winter | Base | P1_Fault_074 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Winter | Transfer | P1_Fault_075 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_076 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_077 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to GEN-2015-093 (563269) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_078 | 3 Phase fault on GRACMNT7 345.00 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 345.00 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 (515800) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_079 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_080 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_081 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_082 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_083 | 3 Phase fault on PLSNT_HILL 6230.00 (524770) 230 kV Bus a. Apply fault at the PLSNT_HILL 6230.00 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNT_HILL 6 (524770) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_084 | 3 Phase fault on OASIS 6230.00 (524875) 230 kV Bus a. Apply fault at the OASIS 6230.00 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OASIS 6 (524875) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_085 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_086 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_087 | 3 Phase fault on MULSHVLY_TP3115.00 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3115.00 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 (525019) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_088 | 3 Phase fault on BC-EARTH 3115.00 (525056) 115 kV Bus a. Apply fault at the BC-EARTH 3115.00 (525056) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-EARTH 3 (525056) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_089 | 3 Phase fault on HART_INDUST3115.00 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3115.00 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 (525124) 115.0 kV to LAMTON 3 (525414) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_090 | 3 Phase fault on TULIA_TP 3115.00 (525179) 115 kV Bus a. Apply fault at the TULIA_TP 3115.00 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULIA_TP 3 (525179) 115.0 kV to KRESS_INT 3 (525192) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_091 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to KRS_RURL_TP3 (525226) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_092 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_093 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_094 | 3 Phase fault on PLAINVW_TP 269.000 (525291) 69 kV Bus a. Apply fault at the PLAINVW_TP 269.000 (525291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAINVW_TP 2 (525291) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_095 | 3 Phase fault on S_PLAINVEW 269.000 (525298) 69 kV Bus a. Apply fault at the S_PLAINVEW 269.000 (525298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_PLAINVEW 2 (525298) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_096 | 3 Phase fault on COX 3115.00 (525326) 115 kV Bus a. Apply fault at the COX 3115.00 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 (525326) 115.0 kV to CALLAHAN 3 (525763) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_097 | 3 Phase fault on LH-AIKEN 269.000 (525351) 69 kV Bus a. Apply fault at the LH-AIKEN 269.000 (525351) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LH-AIKEN 2 (525351) 69.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_098 | 3 Phase fault on LAMTON 3115.00 (525414) 115 kV Bus a. Apply fault at the LAMTON 3115.00 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 (525414) 115.0 kV to LC-S_OLTON+3 (525440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_099 | 3 Phase fault on SP-HALFWAY+269.000 (525432) 69 kV Bus a. Apply fault at the SP-HALFWAY+269.000 (525432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-HALFWAY+2 (525432) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_100 | 3 Phase fault on RKYFORD_TP 3115.00 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3115.00 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKYFORD_TP 3 (525446) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_101 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to PLANT_X 6 (525481) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_102 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to GEN-2017-176 (761439) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_103 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to SUNDOWN 6 (526435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_104 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to G17-146-TAP (760498) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_105 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to GEN-2017-217 (761523) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_106 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_107 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_108 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_109 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_110 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_111 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to GEN-2017-158 (762132) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_112 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_113 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_114 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_115 | 3 Phase fault on BLUECLDPOI 6230.00 (525585) 230 kV Bus a. Apply fault at the BLUECLDPOI 6230.00 (525585) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUECLDPOI 6 (525585) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_116 | 3 Phase fault on NEEDMORE 6230.00 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6230.00 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 (525586) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_117 | 3 Phase fault on SP-ABERNTHY269.000 (525731) 69 kV Bus a. Apply fault at the SP-ABERNTHY269.000 (525731) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ABERNTHY2 (525731) 69.0 kV to TUCO_INT2 2 (525816) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_118 | 3 Phase fault on HALECENTER 269.000 (525738) 69 kV Bus a. Apply fault at the HALECENTER 269.000 (525738) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALECENTER 2 (525738) 69.0 kV to TUCO_INT 2 (525826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_119 | 3 Phase fault on CALLAHAN 3115.00 (525763) 115 kV Bus a. Apply fault at the CALLAHAN 3115.00 (525763) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALLAHAN 3 (525763) 115.0 kV to FLOYD_CNTY 3 (525780) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_120 | 3 Phase fault on FLOYD_CNTY 269.000 (525779) 69 kV Bus a. Apply fault at the FLOYD_CNTY 269.000 (525779) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 2 (525779) 69.0 kV to FLOYDADA_TP2 (525790) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_121 | 3 Phase fault on FLOYD_CNTY 269.000 (525779) 69 kV Bus a. Apply fault at the FLOYD_CNTY 269.000 (525779) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 2 (525779) 69.0 kV to LH-HARMONY 2 (525811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_122 | 3 Phase fault on LRNZ_MPT 3115.00 (525801) 115 kV Bus a. Apply fault at the LRNZ_MPT 3115.00 (525801) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LRNZ_MPT 3 (525801) 115.0 kV to BLANCO 3 (525803) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_123 | 3 Phase fault on TUCO_INT 269.000 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 269.000 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 (525826) 69.0 kV to LH-WIL&ELN+2 (525853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_124 | 3 Phase fault on TUCO_INT 269.000 (525826) 69 kV Bus a. Apply fault at the TUCO_INT 269.000 (525826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 2 (525826) 69.0 kV to SP-NEWDEAL 2 (525885) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_125 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_126 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to ANTELOPE_1 6 (525840) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_127 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Winter | Base | P1_Fault_127 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation Crashes due to Non-Convergence in both TC and BC Cases | Removed Reclosing
05 Southwest | Winter | Transfer | P1_Fault_128 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_129 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_130 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_131 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_132 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | No | Yes | Yes | Transient Post Fault Voltage exceeds 1.2 p.u. and stabilizes above 1.1 p.u. at G17-151TAP 345.00 kV busbar | Operational Steady State Fixes (generator voltage setpoints/transformer tap changes/shunt adjustments)
05 Southwest | Winter | Transfer | P1_Fault_133 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to GEN-2022-147 (769921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_134 | 3 Phase fault on STANTON_W 3115.00 (526076) 115 kV Bus a. Apply fault at the STANTON_W 3115.00 (526076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_135 | 3 Phase fault on SP-ERSKINE 3115.00 (526109) 115 kV Bus a. Apply fault at the SP-ERSKINE 3115.00 (526109) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ERSKINE 3 (526109) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_136 | 3 Phase fault on SP-ERSKINE 3115.00 (526109) 115 kV Bus a. Apply fault at the SP-ERSKINE 3115.00 (526109) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SP-ERSKINE 3 (526109) 115.0 kV to CARLISLE 3 (526160) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_137 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to LP-DOUD_TP 3 (526162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_138 | 3 Phase fault on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 (526161) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_139 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_140 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_141 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_142 | 3 Phase fault on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_143 | 3 Phase fault on JONES 6230.00 (526337) 230 kV Bus a. Apply fault at the JONES 6230.00 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 (526337) 230.0 kV to GRASSLAND 6 (526677) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_144 | 3 Phase fault on SUNDOWN 6230.00 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6230.00 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 (526435) 230.0 kV to AMOCO_SS 6 (526460) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_145 | 3 Phase fault on SUNDOWN 6230.00 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6230.00 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 (526435) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_146 | 3 Phase fault on AMOCO_SS 6230.00 (526460) 230 kV Bus a. Apply fault at the AMOCO_SS 6230.00 (526460) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 (526460) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_147 | 3 Phase fault on GRASSLAND 6230.00 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6230.00 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 (526677) 230.0 kV to CIRRUS_WND 6 (526679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_148 | 3 Phase fault on AMOCOWASSON6230.00 (526784) 230 kV Bus a. Apply fault at the AMOCOWASSON6230.00 (526784) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOWASSON6 (526784) 230.0 kV to MUSTANG 6 (527149) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_149 | 3 Phase fault on PRENTICE 3115.00 (526792) 115 kV Bus a. Apply fault at the PRENTICE 3115.00 (526792) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRENTICE 3 (526792) 115.0 kV to YOAKUM 3 (526934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_150 | 3 Phase fault on YOAKUM 3115.00 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3115.00 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 (526934) 115.0 kV to ARCO_TP 3 (527041) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_151 | 3 Phase fault on YOAKUM 3115.00 (526934) 115 kV Bus a. Apply fault at the YOAKUM 3115.00 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 3 (526934) 115.0 kV to LG-PLSHILL 3 (527194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_152 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to BRU_SUB 6 (527009) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the active power output of multiple generators | Operational Steady State Fixes (generator voltage setpoints/transformer tap changes/shunt adjustments)
05 Southwest | Winter | Transfer | P1_Fault_153 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to INK_BASIN 6 (527028) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the active power output of multiple generators | Operational Steady State Fixes (generator voltage setpoints/transformer tap changes/shunt adjustments)
05 Southwest | Winter | Transfer | P1_Fault_154 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to MUSTANG 6 (527149) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-Dampening Oscillation in the active power output of multiple generators | Operational Steady State Fixes (generator voltage setpoints/transformer tap changes/shunt adjustments)
05 Southwest | Winter | Transfer | P1_Fault_155 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_156 | 3 Phase fault on BRU_SUB 6230.00 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6230.00 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 (527009) 230.0 kV to OXYBRU 6 (527010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_157 | 3 Phase fault on BRU_SUB 6230.00 (527009) 230 kV Bus a. Apply fault at the BRU_SUB 6230.00 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRU_SUB 6 (527009) 230.0 kV to XTO_MAHONEY6 (527011) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_158 | 3 Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 (527028) 230.0 kV to HOBBS_INT 6 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_159 | 3 Phase fault on MUSTANG 6230.00 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6230.00 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 (527149) 230.0 kV to SEMINOLE 6 (527276) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_160 | 3 Phase fault on RSVLT_CC_E 7345.00 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7345.00 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 (527655) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_161 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_162 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #ba c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_163 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #lx c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_164 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV to GEN-2017-102 (762111) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_165 | 3 Phase fault on EDDY_CNTY 7345.00 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7345.00 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 (527802) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_166 | 3 Phase fault on CUNNIGHM_S 6230.00 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6230.00 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 (527867) 230.0 kV to HOBBS_INT 6 (527894) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_167 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to ANDREWS 6 (528604) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_168 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_169 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #uc c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_170 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #xa c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_171 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_172 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to N_LOVING 7 (528185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_173 | 3 Phase fault on PHANTOM 7345.00 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7345.00 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 (528015) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_174 | 3 Phase fault on G16-037-TAP 345.00 (560078) 345 kV Bus a. Apply fault at the G16-037-TAP 345.00 (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP (560078) 345.0 kV to GEN-2016-037 (587230) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_175 | 3 Phase fault on GEN-2016-091345.00 (587740) 345 kV Bus a. Apply fault at the GEN-2016-091345.00 (587740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-091 (587740) 345.0 kV to G16-091-TAP (587744) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_176 | 3 Phase fault on G16-091-TAP 345.00 (587744) 345 kV Bus a. Apply fault at the G16-091-TAP 345.00 (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP (587744) 345.0 kV to GEN-2016-095 (587770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_177 | 3 Phase fault on G17-171-TAP 345.00 (760938) 345 kV Bus a. Apply fault at the G17-171-TAP 345.00 (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP (760938) 345.0 kV to GEN-2017-171 (760939) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_178 | 3 Phase fault on G17-171-TAP 345.00 (760938) 345 kV Bus a. Apply fault at the G17-171-TAP 345.00 (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP (760938) 345.0 kV to GEN-2017-171 (760939) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_179 | 3 Phase fault on G17-218TAP 230.00 (762174) 230 kV Bus a. Apply fault at the G17-218TAP 230.00 (762174) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-218TAP (762174) 230.0 kV to GEN-2017-218 (762175) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_180 | 3 Phase fault on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP (762216) 345.0 kV to GEN-2017-151 (762217) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_181 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to PNM-DC6 (599955) 230.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_182 | 3 Phase fault on MUSTANG 6230.00 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6230.00 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 (527149) 230.0 kV to GS-MUSTANG 6 (527151) 230.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_183 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Base | P1_Fault_183 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_184 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to AMA_SOUTH 3 (524414) 115.0 kV to AMA_SO_TR1 1 (524410) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_185 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to ROOSEVELT 3 (524908) 115.0 kV to ROSEVLT_TR11 (524907) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_186 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to KRESS_INT 2 (525191) 69.0 kV to KRESS_TR1 1 (525190) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_187 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV to SWISHER_TR11 (525211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_188 | 3 Phase fault on COX 3115.00 (525326) 115 kV Bus a. Apply fault at the COX 3115.00 (525326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 3 (525326) 115.0 kV to COX 2 (525325) 69.0 kV to COX_TR1 1 (525324) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_189 | 3 Phase fault on LAMTON 3115.00 (525414) 115 kV Bus a. Apply fault at the LAMTON 3115.00 (525414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMTON 3 (525414) 115.0 kV to LAMTON 2 (525413) 69.0 kV to LAMTON_TR1 1 (525412) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_190 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR1 1 (525451) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_191 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR2 1 (525452) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_192 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR21 (525458) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_193 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR11 (525459) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_194 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to PLANT_X 3 (525480) 115.0 kV to PLANTX_TR1 1 (525479) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_195 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_196 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_197 | 3 Phase fault on LAMB_CNTY 3115.00 (525636) 115 kV Bus a. Apply fault at the LAMB_CNTY 3115.00 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV to LAMB_TR1 1 (525631) 13.2 kV Three Winding #1 b.2. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV to LAMB_TR2 1 (525632) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_198 | 3 Phase fault on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_199 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV to FLOYD_TR1 1 (525777) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_200 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV to FLOYD_TR2 1 (525778) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_201 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT2 2 (525816) 69.0 kV to TUCO_TR7 1 (525814) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_202 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV to TUCO_TR5 1 (525822) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_203 | 3 Phase fault on TUCO_INT 3115.00 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3115.00 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV to TUCO_TR6 1 (525823) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_204 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_205 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_206 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_207 | 3 Phase fault on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_208 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV to CARLISLE 2 (526159) 69.0 kV to CRLSLE_TR2 1 (526158) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_209 | 3 Phase fault on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 (526161) 230.0 kV to CARLISLE 3 (526160) 115.0 kV to CRLSLE_TR1 1 (526157) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_210 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV to LBB_STH TR11 (526265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_211 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV to LBB_STH TR31 (526264) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_212 | 3 Phase fault on LUBBCK_EST 3115.00 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3115.00 (526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV to LBB_EST TR21 (526295) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_213 | 3 Phase fault on LUBBCK_EST 3115.00 (526298) 115 kV Bus a. Apply fault at the LUBBCK_EST 3115.00 (526298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV to LBB_EST TR31 (526296) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_214 | 3 Phase fault on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV to LBB_EST TR11 (526294) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_215 | 3 Phase fault on WOLFFORTH 6230.00 (526525) 230 kV Bus a. Apply fault at the WOLFFORTH 6230.00 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFFORTH 6 (526525) 230.0 kV to WOLFFORTH 3 (526524) 115.0 kV to WOLFRTH_TR11 (526522) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_216 | 3 Phase fault on GRASSLAND 6230.00 (526677) 230 kV Bus a. Apply fault at the GRASSLAND 6230.00 (526677) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRASSLAND 6 (526677) 230.0 kV to GRASSLAND 3 (526676) 115.0 kV to GRASLND_TR11 (526674) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_217 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM 3 (526934) 115.0 kV to YOAKUM_TR1 1 (526931) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_218 | 3 Phase fault on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM 3 (526934) 115.0 kV to YOAKUM_TR2 1 (526932) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_219 | 3 Phase fault on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_220 | 3 Phase fault on INK_BASIN 6230.00 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6230.00 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 (527028) 230.0 kV to INK_BASIN 3 (527027) 115.0 kV to INKBASN_TR 1 (527026) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_221 | 3 Phase fault on MUSTANG 6230.00 (527149) 230 kV Bus a. Apply fault at the MUSTANG 6230.00 (527149) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG 6 (527149) 230.0 kV to MUSTANG 3 (527146) 115.0 kV to MUSTANG_TR11 (527143) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_222 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to HOBBS_INT 3 (527891) 115.0 kV to HOBBS_TR1 1 (527890) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_223 | 3 Phase fault on HOBBS_INT 6230.00 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6230.00 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 (527894) 230.0 kV to HOBBS_INT 3 (527891) 115.0 kV to HOBBS_TR2 1 (527889) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_224 | 3 Phase fault on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV to HOBBS_TR3 1 (527895) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_225 | 3 Phase fault on KIOWA 7345.00 (527965) 345 kV Bus a. Apply fault at the KIOWA 7345.00 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 (527965) 345.0 kV to KIOWA 3 (527966) 115.0 kV to KIOWA_TR1 1 (527964) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_226 | 3 Phase fault on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 (528027) 345.0 kV to RDRUNNER 3 (528025) 115.0 kV to RDRNNER_TR11 (528023) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_227 | 3 Phase fault on OKLAUN 7 345.00 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7 345.00 (599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 (599891) 345.0 kV to OKLEHV24 (590001) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_228 | 3 Phase fault on OKLAUN 7 345.00 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7 345.00 (599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 (599891) 345.0 kV to OKLEHV14 (590003) 138.0 kV to OK1TERT (590004) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_229 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_230 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_231 | 3 Phase fault on OKLAUN HVDC7345.00 (511565) 345 kV Bus a. Apply fault at the OKLAUN HVDC7345.00 (511565) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN HVDC7 (511565) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_232 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_233 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_234 | 3 Phase fault on FLOYD_CNTY 269.000 (525779) 69 kV Bus a. Apply fault at the FLOYD_CNTY 269.000 (525779) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 2 (525779) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_235 | 3 Phase fault on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 (525780) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_236 | 3 Phase fault on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 (525830) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_237 | 3 Phase fault on HALE_WNDCL16230.00 (525957) 230 kV Bus a. Apply fault at the HALE_WNDCL16230.00 (525957) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_WNDCL16 (525957) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_238 | 3 Phase fault on CARLISLE 3115.00 (526160) 115 kV Bus a. Apply fault at the CARLISLE 3115.00 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 3 (526160) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_239 | 3 Phase fault on CARLISLE 6230.00 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6230.00 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 (526161) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_240 | 3 Phase fault on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_241 | 3 Phase fault on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 (527656) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_242 | 3 Phase fault on OKLAUN 7 345.00 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7 345.00 (599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 (599891) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_243 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_244 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_245 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_246 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_247 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_248 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_249 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_250 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_251 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2015-082 (585190) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_252 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 7 (523101) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_253 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOVUS1 7 (523112) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_254 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_255 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_256 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_257 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_258 | 3 Phase fault on G16-003-TAP 345.00 (560071) 345 kV Bus a. Apply fault at the G16-003-TAP 345.00 (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to GEN-2016-003 (587020) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_259 | 3 Phase fault on G16-003-TAP 345.00 (560071) 345 kV Bus a. Apply fault at the G16-003-TAP 345.00 (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP (560071) 345.0 kV to GEN-2017-011 (588560) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_260 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_261 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P1_Fault_262 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_001 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_002 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_003 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. G17-171-TAP (760938) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_004 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 6 (525531) 230.0 kV to TOLK_1 1 (525561) 24.0 kV Two Winding #1 b.2. TOLK_TR 1 (525537) 13.2 kV to TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV Three Winding #2 b.3. TOLK_TR 1 (525537) 13.2 kV to TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV Three Winding #1 b.4. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.5. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #2 b.7. TOLK 6 (525531) 230.0 kV to TOLK_2 1 (525562) 24.0 kV Two Winding #1 b.8. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.9. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 b.10. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 b.11. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.12. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.13. TOLK 6 (525531) 230.0 kV to GEN-2017-158 (762132) 230.0 kV Transmission Circuit #1 b.14. TOLK 6 (525531) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #1 b.15. TOLK 6 (525531) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_005 | Single Phase Fault with Stuck Breaker on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply Fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.2. LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_006 | Single Phase Fault with Stuck Breaker on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply Fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBB_STH TR11 (526265) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #1 b.2. LBB_STH TR31 (526264) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #2 b.3. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.4. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 b.5. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_007 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply Fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBB_EST TR11 (526294) 13.2 kV to LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Three Winding #1 b.2. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_008 | Single Phase Fault with Stuck Breaker on AMOCO_SS 6230.00 (526460) 230 kV Bus a. Apply Fault at the AMOCO_SS 6230.00 (526460) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNDOWN 6 (526435) 230.0 kV to AMOCO_SS 6 (526460) 230.0 kV Transmission Circuit #1 b.2. AMOCO_SS 6 (526460) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_009 | Single Phase Fault with Stuck Breaker on GRASSLAND 6230.00 (526677) 230 kV Bus a. Apply Fault at the GRASSLAND 6230.00 (526677) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRASLND_TR11 (526674) 13.2 kV to GRASSLAND 6 (526677) 230.0 kV to GRASSLAND 3 (526676) 115.0 kV Three Winding #1 b.2. JONES 6 (526337) 230.0 kV to GRASSLAND 6 (526677) 230.0 kV Transmission Circuit #1 b.3. GRASSLAND 6 (526677) 230.0 kV to CIRRUS_WND 6 (526679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_010 | Single Phase Fault with Stuck Breaker on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply Fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALE_TR1 1 (525451) 13.2 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV Three Winding #1 b.2. HALE_TR2 1 (525452) 13.2 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV Three Winding #2 b.3. KRESS_INT 3 (525192) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.4. COX 3 (525326) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.5. LAMTON 3 (525414) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.6. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 b.7. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_011 | Single Phase Fault with Stuck Breaker on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply Fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMB_TR1 1 (525631) 13.2 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Three Winding #1 b.2. LAMB_TR2 1 (525632) 13.2 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Three Winding #2 b.3. LAMB_TR3 1 (525633) 13.2 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Three Winding #1 b.4. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.6. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 b.7. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_012 | Single Phase Fault with Stuck Breaker on FLOYD_CNTY 3115.00 (525780) 115 kV Bus a. Apply Fault at the FLOYD_CNTY 3115.00 (525780) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLOYD_TR1 1 (525777) 13.2 kV to FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV Three Winding #1 b.2. FLOYD_TR2 1 (525778) 13.2 kV to FLOYD_CNTY 3 (525780) 115.0 kV to FLOYD_CNTY 2 (525779) 69.0 kV Three Winding #2 b.3. CALLAHAN 3 (525763) 115.0 kV to FLOYD_CNTY 3 (525780) 115.0 kV Transmission Circuit #1 b.4. FLOYD_CNTY 3 (525780) 115.0 kV to BLANCO 3 (525803) 115.0 kV Transmission Circuit #1 b.5. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_013 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.2. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.3. TUCO_TR7 1 (525814) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT2 2 (525816) 69.0 kV Three Winding #1 b.4. TUCO_TR5 1 (525822) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #2 b.5. TUCO_TR6 1 (525823) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #1 b.6. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.7. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.8. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.9. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.13. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 b.14. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_014 | Single Phase Fault with Stuck Breaker on STANTON_W 3115.00 (526076) 115 kV Bus a. Apply Fault at the STANTON_W 3115.00 (526076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.2. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_015 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply Fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBB_EST TR11 (526294) 13.2 kV to LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Three Winding #1 b.2. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.4. LBB_EST TR21 (526295) 13.2 kV to LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV Three Winding #1 b.5. LBB_EST TR31 (526296) 13.2 kV to LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV Three Winding #2 b.6. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.7. CROSBY 3 (525926) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.8. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_016 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_017 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV to LES#5-1 (511411) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_018 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. G17-171-TAP (760938) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_019 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.2. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.3. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.4. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.5. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.6. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.7. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.8. TUCO_TR5 1 (525822) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #2 b.9. TUCO_TR6 1 (525823) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #1 b.10. TUCO_TR7 1 (525814) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT2 2 (525816) 69.0 kV Three Winding #1 b.14. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 b.15. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_020 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.2. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.3. FLOYD_CNTY 3 (525780) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.4. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.5. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.6. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.7. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.8. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.9. TUCO_TR5 1 (525822) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #2 b.10. TUCO_TR6 1 (525823) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 2 (525826) 69.0 kV Three Winding #1 b.11. TUCO_TR7 1 (525814) 13.2 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_INT2 2 (525816) 69.0 kV Three Winding #1 b.15. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 b.16. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_021 | Single Phase Fault with Stuck Breaker on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply Fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMTON 3 (525414) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.2. KRESS_INT 3 (525192) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.3. COX 3 (525326) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.4. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.5. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 b.6. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR1 1 (525451) 13.2 kV Three Winding #1 b.7. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR2 1 (525452) 13.2 kV Three Winding #2 b.10. PLAINVW_TP 2 (525291) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 b.11. S_PLAINVEW 2 (525298) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 b.12. SP-HALFWAY+2 (525432) 69.0 kV to HALE_CNTY 2 (525453) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_022 | Single Phase Fault with Stuck Breaker on SP-ERSKINE 3115.00 (526109) 115 kV Bus a. Apply Fault at the SP-ERSKINE 3115.00 (526109) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SP-ERSKINE 3 (526109) 115.0 kV to CARLISLE 3 (526160) 115.0 kV Transmission Circuit #1 b.2. SP-ERSKINE 3 (526109) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 b.3. TUCO_INT 3 (525828) 115.0 kV to STANTON_W 3 (526076) 115.0 kV Transmission Circuit #1 b.4. STANTON_W 3 (526076) 115.0 kV to INDIANA 3 (526146) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_023 | Single Phase Fault with Stuck Breaker on LAMB_CNTY 269.000 (525635) 69 kV Bus a. Apply Fault at the LAMB_CNTY 269.000 (525635) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMB_CNTY 3 (525636) 115.0 kV to HOCKLEY 3 (526020) 115.0 kV Transmission Circuit #1 b.2. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 b.3. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.4. LAMB_TR3 1 (525633) 13.2 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Three Winding #1 b.5. LAMB_TR1 1 (525631) 13.2 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Three Winding #1 b.7. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 2 (525635) 69.0 kV to LAMB_TR2 1 (525632) 13.2 kV Three Winding #2 b.8. LAMB_CNTY 3 (525636) 115.0 kV to LAMB_CNTY 6 (525637) 230.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 b.10. W_LITTLFLD 2 (525613) 69.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Transmission Circuit #1 b.11. LTFLD_S&CTY2 (525620) 69.0 kV to LAMB_CNTY 2 (525635) 69.0 kV Transmission Circuit #1 b.12. LAMB_CNTY 2 (525635) 69.0 kV to LC-LTTLFLD+2 (525650) 69.0 kV Transmission Circuit #1 b.13. LAMB_CNTY 2 (525635) 69.0 kV to LC-LUMSCHAP2 (525687) 69.0 kV Transmission Circuit #1 b.16. LTFLD_S&CTY2 (525620) 69.0 kV to W_ANTON_TP 2 (525657) 69.0 kV Transmission Circuit #1 b.17. LC-LTTLFLD+2 (525650) 69.0 kV to W_ANTON_TP 2 (525657) 69.0 kV Transmission Circuit #1 b.18. W_ANTON_TP 2 (525657) 69.0 kV to LC-SPD&HART2 (525664) 69.0 kV Transmission Circuit #1 b.19. W_ANTON_TP 2 (525657) 69.0 kV to BAINER 2 (525671) 69.0 kV Transmission Circuit #1 b.20. LC-SPD&HART2 (525664) 69.0 kV to CNTYLINE_TP2 (525723) 69.0 kV Transmission Circuit #1 b.21. BAINER 2 (525671) 69.0 kV to W_ANTON 2 (525678) 69.0 kV Transmission Circuit #1 b.22. LC-LUMSCHAP2 (525687) 69.0 kV to HOBGOOD 2 (525694) 69.0 kV Transmission Circuit #1 b.23. HOBGOOD 2 (525694) 69.0 kV to PUMP/YH_TP 2 (525697) 69.0 kV Transmission Circuit #1 b.24. PUMP/YH_TP 2 (525697) 69.0 kV to YELLOWHOUSE2 (525703) 69.0 kV Transmission Circuit #1 b.25. PUMP/YH_TP 2 (525697) 69.0 kV to MIDAMERI#2 2 (525708) 69.0 kV Transmission Circuit #1 b.26. PHLLPPMP#2 2 (525701) 69.0 kV to YELLOWHOUSE2 (525703) 69.0 kV Transmission Circuit #1 b.27. MIDAMERI#2 2 (525708) 69.0 kV to WHITHARRAL 2 (525717) 69.0 kV Transmission Circuit #1 b.28. WHITHARRAL 2 (525717) 69.0 kV to LC-HODGE_TP2 (525995) 69.0 kV Transmission Circuit #1 b.29. AMHERST 2 (525606) 69.0 kV to W_LITTLFLD 2 (525613) 69.0 kV Transmission Circuit #1 b.30. LC-SANDHLL+2 (525599) 69.0 kV to AMHERST 2 (525606) 69.0 kV Transmission Circuit #1 b.31. SUDANRURAL 2 (525592) 69.0 kV to LC-SANDHLL+2 (525599) 69.0 kV Transmission Circuit #1 b.32. LC-BECK +2 (525045) 69.0 kV to SUDANRURAL 2 (525592) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_024 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 3115.00 (526298) 115 kV Bus a. Apply Fault at the LUBBCK_EST 3115.00 (526298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSBY 3 (525926) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.2. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.3. TUCO_INT 3 (525828) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.4. LBB_EST TR11 (526294) 13.2 kV to LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Three Winding #1 b.5. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV to LBB_EST TR21 (526295) 13.2 kV Three Winding #1 b.6. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 2 (526297) 69.0 kV to LBB_EST TR31 (526296) 13.2 kV Three Winding #2 b.7. LUBBCK_EST 3 (526298) 115.0 kV to LUBBCK_EST 6 (526299) 230.0 kV to LBB_EST TR11 (526294) 13.2 kV Three Winding #1 b.10. PLANTERS 2 (526284) 69.0 kV to LUBBCK_EST 2 (526297) 69.0 kV Transmission Circuit #1 b.11. LUBBCK_EST 2 (526297) 69.0 kV to CLUTTER 2 (526310) 69.0 kV Transmission Circuit #1 b.12. LUBBCK_EST 2 (526297) 69.0 kV to SLATON 2 (526562) 69.0 kV Transmission Circuit #1 b.15. ACCO 2 (526249) 69.0 kV to CLUTTER 2 (526310) 69.0 kV Transmission Circuit #1 b.16. SW_6786_S 2 (526087) 69.0 kV to PLANTERS 2 (526284) 69.0 kV Transmission Circuit #1 b.17. STANTON_E 2 (526075) 69.0 kV to SW_6786_S 2 (526087) 69.0 kV Transmission Circuit #1 b.18. SW_6786_N 2 (526086) 69.0 kV to SW_6786_S 2 (526087) 69.0 kV Transmission Circuit #z1 b.19. STANTON_N 2 (526073) 69.0 kV to STANTON_E 2 (526075) 69.0 kV Transmission Circuit #z1 b.20. STANTON_N 2 (526073) 69.0 kV to SW_6786_N 2 (526086) 69.0 kV Transmission Circuit #1 b.21. SW_6786_N 2 (526086) 69.0 kV to SP-HETTLER 2 (526102) 69.0 kV Transmission Circuit #1 b.22. SP-HETTLER 2 (526102) 69.0 kV to SP-IDALOU +2 (526116) 69.0 kV Transmission Circuit #1 b.23. SP-IDALOU +2 (526116) 69.0 kV to VICKERS 2 (526123) 69.0 kV Transmission Circuit #1 b.24. SP-ACUFF +2 (525906) 69.0 kV to VICKERS 2 (526123) 69.0 kV Transmission Circuit #1 b.25. SP-ACUFF +2 (525906) 69.0 kV to CROSBY 2 (525925) 69.0 kV Transmission Circuit #1 b.26. SLATON 2 (526562) 69.0 kV to SP-SLATON 2 (526569) 69.0 kV Transmission Circuit #1 b.27. SP-SLATON 2 (526569) 69.0 kV to SOUTHLAND 2 (526576) 69.0 kV Transmission Circuit #1 b.28. SOUTHLAND 2 (526576) 69.0 kV to LG-HAKBERRY2 (526583) 69.0 kV Transmission Circuit #1 b.29. LG-HAKBERRY2 (526583) 69.0 kV to DIEKEMPER 2 (526592) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_025 | Single Phase Fault with Stuck Breaker on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply Fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALE_TR2 1 (525452) 13.2 kV to HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV Three Winding #2 b.2. LAMTON 3 (525414) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.3. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 b.4. HALE_CNTY 3 (525454) 115.0 kV to TUCO_INT 3 (525828) 115.0 kV Transmission Circuit #1 b.5. KRESS_INT 3 (525192) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.6. COX 3 (525326) 115.0 kV to HALE_CNTY 3 (525454) 115.0 kV Transmission Circuit #1 b.7. HALE_CNTY 3 (525454) 115.0 kV to HALE_CNTY 2 (525453) 69.0 kV to HALE_TR1 1 (525451) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_026 | Single Phase Fault with Stuck Breaker on MUSTANG 6230.00 (527149) 230 kV Bus a. Apply Fault at the MUSTANG 6230.00 (527149) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSTANG 6 (527149) 230.0 kV to MUSTANG_3 1 (527163) 19.0 kV Two Winding #1 b.2. YOAKUM 6 (526935) 230.0 kV to MUSTANG 6 (527149) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_027 | Single Phase Fault with Stuck Breaker on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply Fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. LBB_STH TR31 (526264) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #2 b.3. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 b.4. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 b.5. ALLEN 3 (526213) 115.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Transmission Circuit #1 b.6. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Transmission Circuit #1 b.7. WOODROW 3 (526602) 115.0 kV to LYNN_CNTY 3 (526656) 115.0 kV Transmission Circuit #1 b.8. LUBBCK_STH 3 (526268) 115.0 kV to WOODROW 3 (526602) 115.0 kV Transmission Circuit #1 b.9. LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV to LBB_STH TR11 (526265) 13.2 kV Three Winding #1 b.11. LUBBCK_STH 3 (526268) 115.0 kV to LUBBCK_STH 2 (526267) 69.0 kV to LBB_STH TR21 (526266) 13.2 kV Three Winding #1 b.14. IVORY 2 (526205) 69.0 kV to LUBBCK_STH 2 (526267) 69.0 kV Transmission Circuit #1 b.15. IVORY_TP 2 (526256) 69.0 kV to LUBBCK_STH 2 (526267) 69.0 kV Transmission Circuit #1 b.19. IVORY 2 (526205) 69.0 kV to IVORY_TP 2 (526256) 69.0 kV Transmission Circuit #z1 b.20. ACCO 2 (526249) 69.0 kV to IVORY_TP 2 (526256) 69.0 kV Transmission Circuit #1 b.21. ACCO 2 (526249) 69.0 kV to CLUTTER 2 (526310) 69.0 kV Transmission Circuit #1 b.22. IVORY 2 (526205) 69.0 kV to BATTON_S 2 (526228) 69.0 kV Transmission Circuit #1 b.23. BATTON_N 2 (526221) 69.0 kV to BATTON_S 2 (526228) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_028 | Single Phase Fault with Stuck Breaker on LUBBCK_EST 6230.00 (526299) 230 kV Bus a. Apply Fault at the LUBBCK_EST 6230.00 (526299) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_EST 6 (526299) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. LBB_EST TR11 (526294) 13.2 kV to LUBBCK_EST 6 (526299) 230.0 kV to LUBBCK_EST 3 (526298) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_029 | Single Phase Fault with Stuck Breaker on NEWHART 6230.00 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 b.2. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_030 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER_TR11 (525211) 13.2 kV to SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV Three Winding #1 b.2. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_031 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_032 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_033 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR2 1 (525825) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #2 b.2. TUCO_INT 6 (525830) 230.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_034 | Single Phase Fault with Stuck Breaker on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM_TR1 1 (526931) 13.2 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM 3 (526934) 115.0 kV Three Winding #1 b.2. NEEDMORE 6 (525586) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_035 | Single Phase Fault with Stuck Breaker on YOAKUM 6230.00 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6230.00 (526935) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AMOCO_SS 6 (526460) 230.0 kV to YOAKUM 6 (526935) 230.0 kV Transmission Circuit #1 b.2. YOAKUM 6 (526935) 230.0 kV to INK_BASIN 6 (527028) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_036 | Single Phase Fault with Stuck Breaker on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply Fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. LBB_STH TR31 (526264) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #2 b.3. LBB_STH TR11 (526265) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #1 b.4. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 b.5. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_037 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_038 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.2. TUCO_INT 6 (525830) 230.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_039 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR4 1 (525821) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #1 b.2. TUCO_TR3 1 (525819) 13.2 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV Three Winding #2 b.3. TUCO_INT 6 (525830) 230.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_040 | Single Phase Fault with Stuck Breaker on LUBBCK_STH 6230.00 (526269) 230 kV Bus a. Apply Fault at the LUBBCK_STH 6230.00 (526269) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBB_STH TR11 (526265) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #1 b.2. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.3. LUBBCK_STH 6 (526269) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #2 b.4. LBB_STH TR31 (526264) 13.2 kV to LUBBCK_STH 6 (526269) 230.0 kV to LUBBCK_STH 3 (526268) 115.0 kV Three Winding #2 b.5. LUBBCK_STH 6 (526269) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_041 | Single Phase Fault with Stuck Breaker on CROSSROADS 7345.00 (527656) 345 kV Bus a. Apply Fault at the CROSSROADS 7345.00 (527656) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSSROADS 7 (527656) 345.0 kV to EDDY_CNTY 7 (527802) 345.0 kV Transmission Circuit #1 b.2. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.3. RSVLT_CC_E 7 (527655) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.4. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_CC_E 7 (527655) 345.0 kV Transmission Circuit #1 b.5. MILO_WND (577121) 34.5 kV to RSVLT_CC_E 7 (527655) 345.0 kV Two Winding #1 b.6. MILO_WIND 1 (527653) 0.7 kV to MILO_CB (577120) 34.5 kV Two Winding #1 b.7. RSVLT_GEN1 1 (527651) 0.7 kV to RSVLT_WIND11 (527658) 34.5 kV Two Winding #1 b.8. RSVLT_GEN2 1 (527652) 0.7 kV to RSVLT_WIND21 (527659) 34.5 kV Two Winding #1 b.9. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_COL1 7 (527666) 345.0 kV Transmission Circuit #1 b.10. RSVLT_CC_W 7 (527654) 345.0 kV to RSVLT_COL2 7 (527667) 345.0 kV Transmission Circuit #1 b.11. SAGA_SCOL 7 (527610) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 b.12. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #ba b.13. CROSSROADS 7 (527656) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #lx b.14. CROSSROADS 7 (527656) 345.0 kV to GEN-2017-102 (762111) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_042 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_TR3 1 (527895) 13.2 kV to HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_043 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_044 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_045 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM 6 (526935) 230.0 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.4. YOAKUM_TR1 (526937) 13.2 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_046 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_047 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.3. ELK_CT1 (525850) 345.0 kV to ELK_1 1 (525844) 18.0 kV Two Winding #1 b.4. TUCO_INT 7 (525832) 345.0 kV to ELK_2 1 (525845) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_048 | Single Phase Fault with Stuck Breaker on HOBBS_INT 7345.00 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7345.00 (527896) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOBBS_INT 7 (527896) 345.0 kV to KIOWA 7 (527965) 345.0 kV Transmission Circuit #1 b.2. HOBBS_TR3 1 (527895) 13.2 kV to HOBBS_INT 7 (527896) 345.0 kV to HOBBS_INT 6 (527894) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_049 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_TR1 (526937) 13.2 kV to YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_050 | Single Phase Fault with Stuck Breaker on RDRUNNER 7345.00 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7345.00 (528027) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHANTOM 7 (528015) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.2. KIOWA 7 (527965) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #1 b.3. RDRNNER_TR11 (528023) 13.2 kV to RDRUNNER 7 (528027) 345.0 kV to RDRUNNER 3 (528025) 115.0 kV Three Winding #1 b.4. HOBBS_INT 7 (527896) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #uc b.5. HOBBS_INT 7 (527896) 345.0 kV to RDRUNNER 7 (528027) 345.0 kV Transmission Circuit #xa | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_051 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_052 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_053 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_054 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_055 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 b.4. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_056 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 b.4. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_057 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_058 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 b.4. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_059 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_060 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_061 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_062 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_063 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 b.6. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_064 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_065 | Single Phase Fault with Stuck Breaker on GRPLNS-CB2-134.500 (523126) 34.5 kV Bus a. Apply Fault at the GRPLNS-CB2-134.500 (523126) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_066 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.5. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.6. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_067 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_068 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_069 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to GEN-2011-014 (515686) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_070 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_071 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_072 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_074 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #2 b.2. TOLK 6 (525531) 230.0 kV to ROOSEVELT 6 (524909) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_075 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_076 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.2. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_077 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-151TAP (762216) 345.0 kV to O.K.U.-7 (511456) 345.0 kV Transmission Circuit #1 b.2. G17-151TAP (762216) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_078 | Single Phase Fault with Stuck Breaker on WWDBORDT 345.00 (755000) 345 kV Bus a. Apply Fault at the WWDBORDT 345.00 (755000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDBORDT (755000) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. WWDBORDT (755000) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | No | Yes | Yes | Transient Post Fault Voltage exceeds 1.2 p.u. and stabilizes above 1.1 p.u. at BORDER 7 345.00 kV busbar | Operational Steady State Fixes (generator voltage setpoints/transformer tap changes/shunt adjustments)
05 Southwest | Winter | Base | P4_Fault_078 | Single Phase Fault with Stuck Breaker on WWDBORDT 345.00 (755000) 345 kV Bus a. Apply Fault at the WWDBORDT 345.00 (755000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDBORDT (755000) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 b.2. WWDBORDT (755000) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | No | Yes | Yes | Transient Post Fault Voltage exceeds 1.2 p.u. and stabilizes above 1.1 p.u. at BORDER 7 345.00 kV busbar | Operational Steady State Fixes (generator voltage setpoints/transformer tap changes/shunt adjustments)
05 Southwest | Winter | Transfer | P4_Fault_079 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_080 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 b.2. TUCO_INT 3 (525828) 115.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_081 | Single Phase Fault with Stuck Breaker on JONES 6230.00 (526337) 230 kV Bus a. Apply Fault at the JONES 6230.00 (526337) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES 6 (526337) 230.0 kV to LUBBCK_STH 6 (526269) 230.0 kV Transmission Circuit #1 b.2. JONES 6 (526337) 230.0 kV to LUBBCK_STH 6 (526269) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_082 | Single Phase Fault with Stuck Breaker on SWISHER 6230.00 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 b.2. SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV to SWISHER_TR11 (525211) 13.2 kV Three Winding #1 b.4. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.5. SWISHER 6 (525213) 230.0 kV to Switched Shunt # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_083 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to ELK_CT1 (525850) 345.0 kV Transmission Circuit #1 b.3. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.4. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 b.5. TUCO_INT 7 (525832) 345.0 kV to GEN-2022-147 (769921) 345.0 kV Transmission Circuit #1 b.6. TUCO_INT 7 (525832) 345.0 kV to ELK_2 1 (525845) 18.0 kV Transformer #1 b.7. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.8. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_084 | Single Phase Fault with Stuck Breaker on TOLK 7345.00 (525549) 345 kV Bus a. Apply Fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 b.2. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 b.3. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 b.4. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.5. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.6. TOLK 6 (525531) 230.0 kV to GEN-2017-158 (762132) 230.0 kV Transmission Circuit #1 b.7. TOLK 6 (525531) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #1 b.8. TOLK 6 (525531) 230.0 kV to G17-218TAP (762174) 230.0 kV Transmission Circuit #2 b.9. TOLK 6 (525531) 230.0 kV to TOLK_1 1 (525561) 24.0 kV Transformer #1 b.10. TOLK 6 (525531) 230.0 kV to TOLK_2 1 (525562) 24.0 kV Transformer #1 b.11. TOLK 6 (525531) 230.0 kV to TOLK 7 (525549) 345.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #2 b.12. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_085 | Single Phase Fault with Stuck Breaker on G17-151TAP 345.00 (762216) 345 kV Bus a. Apply Fault at the G17-151TAP 345.00 (762216) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 b.2. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 b.3. G17-151TAP (762216) 345.0 kV to GEN-2017-151 (762217) 345.0 kV Transmission Circuit #1 b.4. G17-151TAP (762216) 345.0 kV to Switched Shunt # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_086 | Single Phase Fault with Stuck Breaker on WWDBORDT 345.00 (755000) 345 kV Bus a. Apply Fault at the WWDBORDT 345.00 (755000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.3. BORDER 7 (515458) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_087 | Single Phase Fault with Stuck Breaker on YOAKUM_345 345.00 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 345.00 (526936) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 7 (525832) 345.0 kV to YOAKUM_345 (526936) 345.0 kV Transmission Circuit #1 b.2. YOAKUM_345 (526936) 345.0 kV to HOBBS_INT 7 (527896) 345.0 kV Transmission Circuit #1 b.3. YOAKUM_345 (526936) 345.0 kV to YOAKUM 6 (526935) 230.0 kV to YOAKUM_TR1 (526937) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 Southwest | Winter | Transfer | P4_Fault_088 | Single Phase Fault with Stuck Breaker on TUCO_INT 6230.00 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6230.00 (525830) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR3 1 (525819) 13.2 kV Three Winding #2 b.2. TUCO_INT 6 (525830) 230.0 kV to TUCO_INT 3 (525828) 115.0 kV to TUCO_TR4 1 (525821) 13.2 kV Three Winding #1 b.3. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR1 1 (525824) 13.2 kV Three Winding #1 b.4. TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV to TUCO_TR2 1 (525825) 13.2 kV Three Winding #2 b.5. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.6. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 b.7. TUCO_INT 6 (525830) 230.0 kV to ANTELOPE_1 6 (525840) 230.0 kV Transmission Circuit #1 b.8. TUCO_INT 6 (525830) 230.0 kV to HALE_WNDCL16 (525957) 230.0 kV Transmission Circuit #1 b.9. TUCO_INT 6 (525830) 230.0 kV to CARLISLE 6 (526161) 230.0 kV Transmission Circuit #1 b.10. TUCO_INT 6 (525830) 230.0 kV to JONES 6 (526337) 230.0 kV Transmission Circuit #1 b.11. TUCO_SVC 1 (525820) 13.0 kV to TUCO_INT 6 (525830) 230.0 kV Transformer #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis Results
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2022-147 | 05 Southwest | 511422 | FLETCHR4 | 138 | 8.1642 | 8.1644 | 0.0002
GEN-2022-147 | 05 Southwest | 511423 | FLE TAP4 | 138 | 8.9175 | 8.9178 | 0.0003
GEN-2022-147 | 05 Southwest | 511431 | LWS S4 | 138 | 11.317 | 11.3179 | 0.0009
GEN-2022-147 | 05 Southwest | 511437 | COMANC-4 | 138 | 18.4317 | 18.4338 | 0.0021
GEN-2022-147 | 05 Southwest | 511439 | LWSTAP 4 | 138 | 11.7896 | 11.7905 | 0.0009
GEN-2022-147 | 05 Southwest | 511456 | O.K.U.-7 | 345 | 5.6746 | 5.682 | 0.0074
GEN-2022-147 | 05 Southwest | 511466 | L.E.S.-2 | 69 | 17.1377 | 17.1386 | 0.0009
GEN-2022-147 | 05 Southwest | 511467 | L.E.S.-4 | 138 | 24.6224 | 24.6268 | 0.0044
GEN-2022-147 | 05 Southwest | 511468 | L.E.S.-7 | 345 | 12.702 | 12.707 | 0.005
GEN-2022-147 | 05 Southwest | 511470 | LGORE-S2 | 69 | 7.2365 | 7.2367 | 0.0002
GEN-2022-147 | 05 Southwest | 511474 | SHERID4 | 138 | 12.5745 | 12.5755 | 0.001
GEN-2022-147 | 05 Southwest | 511486 | ELGINJT4 | 138 | 10.3592 | 10.3596 | 0.0004
GEN-2022-147 | 05 Southwest | 511490 | ELKCITY6 | 230 | 7.4559 | 7.4568 | 0.0009
GEN-2022-147 | 05 Southwest | 511494 | COMMTAP4 | 138 | 21.6698 | 21.673 | 0.0032
GEN-2022-147 | 05 Southwest | 511503 | LAW WC2 | 69 | 4.7366 | 4.7366 | 0
GEN-2022-147 | 05 Southwest | 511541 | SWEETWT6 | 230 | 8.9374 | 8.9389 | 0.0015
GEN-2022-147 | 05 Southwest | 511542 | BUFFCK6 | 230 | 6.56 | 6.5608 | 0.0008
GEN-2022-147 | 05 Southwest | 511544 | DEMPSEY6 | 230 | 5.284 | 5.2845 | 0.0005
GEN-2022-147 | 05 Southwest | 511547 | ROARK6 | 230 | 5.2077 | 5.2082 | 0.0005
GEN-2022-147 | 05 Southwest | 511553 | CHISHOLM7 | 345 | 10.4651 | 10.4712 | 0.0061
GEN-2022-147 | 05 Southwest | 511557 | CHISHOLM6 | 230 | 11.6794 | 11.6828 | 0.0034
GEN-2022-147 | 05 Southwest | 511565 | OKLAUN HVDC7 | 345 | 5.6579 | 5.6652 | 0.0073
GEN-2022-147 | 05 Southwest | 511568 | TERRYRD7 | 345 | 9.0623 | 9.0638 | 0.0015
GEN-2022-147 | 05 Southwest | 511571 | RUSHSPR7 | 345 | 5.5714 | 5.572 | 0.0006
GEN-2022-147 | 05 Southwest | 511979 | RSHSPR1_MPT1 | 345 | 5.419 | 5.4195 | 0.0005
GEN-2022-147 | 05 Southwest | 514785 | WOODWRD4 | 138 | 6.7326 | 6.7327 | 0.0001
GEN-2022-147 | 05 Southwest | 514796 | IODINE-4 | 138 | 7.5883 | 7.5883 | 0
GEN-2022-147 | 05 Southwest | 515363 | CENT 4 | 138 | 2.7709 | 2.7709 | 0
GEN-2022-147 | 05 Southwest | 515375 | WWRDEHV7 | 345 | 18.9653 | 18.967 | 0.0017
GEN-2022-147 | 05 Southwest | 515376 | WWRDEHV4 | 138 | 21.3834 | 21.3842 | 0.0008
GEN-2022-147 | 05 Southwest | 515394 | KEENAN 4 | 138 | 8.7599 | 8.76 | 0.0001
GEN-2022-147 | 05 Southwest | 515398 | OUSPRT 4 | 138 | 9.3327 | 9.3328 | 0.0001
GEN-2022-147 | 05 Southwest | 515407 | TATONGA7 | 345 | 17.3681 | 17.3689 | 0.0008
GEN-2022-147 | 05 Southwest | 515448 | CRSRDSW7 | 345 | 12.2315 | 12.2319 | 0.0004
GEN-2022-147 | 05 Southwest | 515458 | BORDER 7 | 345 | 7.626 | 7.6325 | 0.0065
GEN-2022-147 | 05 Southwest | 515497 | MATHWSN7 | 345 | 31.1463 | 31.1476 | 0.0013
GEN-2022-147 | 05 Southwest | 515582 | SLNGWND7 | 345 | 8.6516 | 8.6518 | 0.0002
GEN-2022-147 | 05 Southwest | 515585 | MAMTHPW7 | 345 | 13.8249 | 13.8253 | 0.0004
GEN-2022-147 | 05 Southwest | 515599 | G07621119-20 | 345 | 11.8701 | 11.8707 | 0.0006
GEN-2022-147 | 05 Southwest | 515677 | BADGER 7 | 345 | 14.1096 | 14.1101 | 0.0005
GEN-2022-147 | 05 Southwest | 515686 | GEN-2011-014 | 345 | 12.7545 | 12.7549 | 0.0004
GEN-2022-147 | 05 Southwest | 515800 | GRACMNT7 | 345 | 17.1873 | 17.1912 | 0.0039
GEN-2022-147 | 05 Southwest | 515825 | GRTWSRN7 | 345 | 8.685 | 8.6853 | 0.0003
GEN-2022-147 | 05 Southwest | 515852 | DGRASSE7 | 345 | 14.3411 | 14.3416 | 0.0005
GEN-2022-147 | 05 Southwest | 515853 | DGRASSE4 | 138 | 14.8077 | 14.8078 | 0.0001
GEN-2022-147 | 05 Southwest | 515951 | PERSIMN7 | 345 | 10.4059 | 10.4064 | 0.0005
GEN-2022-147 | 05 Southwest | 515961 | GUTHRIE7 | 345 | 11.8941 | 11.8948 | 0.0007
GEN-2022-147 | 05 Southwest | 522800 | MU-TULIA 3 | 115 | 5.4445 | 5.4456 | 0.0011
GEN-2022-147 | 05 Southwest | 522805 | MU-FLOYDADA2 | 69 | 2.3158 | 2.3161 | 0.0003
GEN-2022-147 | 05 Southwest | 522892 | MU-BROWNFLD2 | 69 | 2.8763 | 2.8765 | 0.0002
GEN-2022-147 | 05 Southwest | 523309 | MOORE_CNTY 6 | 230 | 7.1968 | 7.197 | 0.0002
GEN-2022-147 | 05 Southwest | 523551 | HUTCHISON 6 | 230 | 7.4755 | 7.4757 | 0.0002
GEN-2022-147 | 05 Southwest | 523771 | GRAPEVINE 6 | 230 | 6.0295 | 6.0298 | 0.0003
GEN-2022-147 | 05 Southwest | 523869 | CHAN+TASCOS6 | 230 | 4.4428 | 4.4429 | 0.0001
GEN-2022-147 | 05 Southwest | 523959 | POTTER_CO 6 | 230 | 21.0182 | 21.0214 | 0.0032
GEN-2022-147 | 05 Southwest | 523961 | POTTER_CO 7 | 345 | 7.6921 | 7.6925 | 0.0004
GEN-2022-147 | 05 Southwest | 523977 | HARRNG_WST 6 | 230 | 26.7476 | 26.7518 | 0.0042
GEN-2022-147 | 05 Southwest | 523978 | HARRNG_MID 6 | 230 | 26.7476 | 26.7518 | 0.0042
GEN-2022-147 | 05 Southwest | 523979 | HARRNG_EST 6 | 230 | 26.7476 | 26.7518 | 0.0042
GEN-2022-147 | 05 Southwest | 524010 | ROLLHILLS 6 | 230 | 19.9306 | 19.9331 | 0.0025
GEN-2022-147 | 05 Southwest | 524016 | ASARCO 3 | 115 | 26.6619 | 26.6636 | 0.0017
GEN-2022-147 | 05 Southwest | 524043 | NICHOLS 3 | 115 | 30.602 | 30.6044 | 0.0024
GEN-2022-147 | 05 Southwest | 524044 | NICHOLS 6 | 230 | 25.9716 | 25.9755 | 0.0039
GEN-2022-147 | 05 Southwest | 524267 | BUSHLAND 6 | 230 | 10.0907 | 10.0917 | 0.001
GEN-2022-147 | 05 Southwest | 524276 | WILDOR_WND 6 | 230 | 5.1921 | 5.1923 | 0.0002
GEN-2022-147 | 05 Southwest | 524290 | WILDOR2_JUS6 | 230 | 6.9216 | 6.9221 | 0.0005
GEN-2022-147 | 05 Southwest | 524296 | SPNSPUR_WND7 | 345 | 4.2585 | 4.2586 | 0.0001
GEN-2022-147 | 05 Southwest | 524299 | SPNSPUR_COL7 | 345 | 4.2585 | 4.2586 | 0.0001
GEN-2022-147 | 05 Southwest | 524331 | PULLMAN 3 | 115 | 7.5078 | 7.5081 | 0.0003
GEN-2022-147 | 05 Southwest | 524338 | SOUTHEAST 3 | 115 | 11.6455 | 11.6463 | 0.0008
GEN-2022-147 | 05 Southwest | 524364 | RANDALL 3 | 115 | 21.6129 | 21.6154 | 0.0025
GEN-2022-147 | 05 Southwest | 524365 | RANDALL 6 | 230 | 14.8487 | 14.8509 | 0.0022
GEN-2022-147 | 05 Southwest | 524377 | FARMERS 3 | 115 | 15.8339 | 15.8351 | 0.0012
GEN-2022-147 | 05 Southwest | 524397 | ARROWHEAD 3 | 115 | 14.1041 | 14.105 | 0.0009
GEN-2022-147 | 05 Southwest | 524404 | OWENSCORN 3 | 115 | 15.4593 | 15.4605 | 0.0012
GEN-2022-147 | 05 Southwest | 524414 | AMA_SOUTH 3 | 115 | 17.3306 | 17.3321 | 0.0015
GEN-2022-147 | 05 Southwest | 524415 | AMA_SOUTH 6 | 230 | 13.9469 | 13.9494 | 0.0025
GEN-2022-147 | 05 Southwest | 524472 | LOPEZ 3 | 115 | 2.4697 | 2.4697 | 0
GEN-2022-147 | 05 Southwest | 524477 | CAMPBELL_ST3 | 115 | 2.4616 | 2.4616 | 0
GEN-2022-147 | 05 Southwest | 524486 | CAPROCK 3 | 115 | 2.8847 | 2.8848 | 0.0001
GEN-2022-147 | 05 Southwest | 524502 | NORTON 3 | 115 | 3.2302 | 3.2302 | 0
GEN-2022-147 | 05 Southwest | 524509 | FE-TUCMCARI3 | 115 | 2.6162 | 2.6163 | 0.0001
GEN-2022-147 | 05 Southwest | 524544 | SPRING_DRW 3 | 115 | 6.6664 | 6.6666 | 0.0002
GEN-2022-147 | 05 Southwest | 524679 | DIMMIT_S_TP2 | 69 | 3.0831 | 3.0832 | 0.0001
GEN-2022-147 | 05 Southwest | 524680 | DIMIT_SOUTH2 | 69 | 3.0272 | 3.0273 | 0.0001
GEN-2022-147 | 05 Southwest | 524681 | DIMMIT_EAST2 | 69 | 2.9518 | 2.9518 | 0
GEN-2022-147 | 05 Southwest | 524688 | DS-#3 2 | 69 | 3.129 | 3.1291 | 0.0001
GEN-2022-147 | 05 Southwest | 524694 | DS-#22 3 | 115 | 4.905 | 4.9054 | 0.0004
GEN-2022-147 | 05 Southwest | 524721 | DS-#15&#19+2 | 69 | 3.7599 | 3.76 | 0.0001
GEN-2022-147 | 05 Southwest | 524728 | DS-CASTRO 2 | 69 | 4.5294 | 4.5296 | 0.0002
GEN-2022-147 | 05 Southwest | 524745 | CASTRO_CNTY2 | 69 | 9.4043 | 9.4051 | 0.0008
GEN-2022-147 | 05 Southwest | 524746 | CASTRO_CNTY3 | 115 | 10.6751 | 10.6768 | 0.0017
GEN-2022-147 | 05 Southwest | 524757 | BETHEL_COL13 | 115 | 9.1956 | 9.1967 | 0.0011
GEN-2022-147 | 05 Southwest | 524768 | PLSNT_HILL 3 | 115 | 10.3854 | 10.3866 | 0.0012
GEN-2022-147 | 05 Southwest | 524770 | PLSNT_HILL 6 | 230 | 6.3849 | 6.3858 | 0.0009
GEN-2022-147 | 05 Southwest | 524783 | W_CLOVIS 2 | 69 | 2.5325 | 2.5325 | 0
GEN-2022-147 | 05 Southwest | 524821 | CURRY 2 | 69 | 4.5567 | 4.5568 | 0.0001
GEN-2022-147 | 05 Southwest | 524822 | CURRY 3 | 115 | 11.0144 | 11.0159 | 0.0015
GEN-2022-147 | 05 Southwest | 524846 | FARWELL 2 | 69 | 2.2196 | 2.2196 | 0
GEN-2022-147 | 05 Southwest | 524874 | OASIS 3 | 115 | 9.9627 | 9.9638 | 0.0011
GEN-2022-147 | 05 Southwest | 524875 | OASIS 6 | 230 | 7.6445 | 7.6459 | 0.0014
GEN-2022-147 | 05 Southwest | 524885 | SN_JUAN_TAP6 | 230 | 4.9483 | 4.9487 | 0.0004
GEN-2022-147 | 05 Southwest | 524889 | SN_JUAN_WND6 | 230 | 4.7423 | 4.7426 | 0.0003
GEN-2022-147 | 05 Southwest | 524908 | ROOSEVELT 3 | 115 | 10.9243 | 10.9258 | 0.0015
GEN-2022-147 | 05 Southwest | 524909 | ROOSEVELT 6 | 230 | 9.1879 | 9.19 | 0.0021
GEN-2022-147 | 05 Southwest | 524923 | PORTALES 2 | 69 | 7.7244 | 7.7248 | 0.0004
GEN-2022-147 | 05 Southwest | 524924 | PORTALES 3 | 115 | 7.5774 | 7.5781 | 0.0007
GEN-2022-147 | 05 Southwest | 524929 | RO-PORT_MTR2 | 69 | 7.7244 | 7.7248 | 0.0004
GEN-2022-147 | 05 Southwest | 524934 | ZODIAC 2 | 69 | 5.7037 | 5.704 | 0.0003
GEN-2022-147 | 05 Southwest | 524935 | KILGORE 3 | 115 | 6.2201 | 6.2205 | 0.0004
GEN-2022-147 | 05 Southwest | 524941 | PORTALES#1 2 | 69 | 5.9124 | 5.9126 | 0.0002
GEN-2022-147 | 05 Southwest | 524948 | PORTALES#2 2 | 69 | 5.013 | 5.0132 | 0.0002
GEN-2022-147 | 05 Southwest | 524962 | S_PORTALES 2 | 69 | 4.4578 | 4.458 | 0.0002
GEN-2022-147 | 05 Southwest | 524963 | S_PORTALES 3 | 115 | 5.8508 | 5.8512 | 0.0004
GEN-2022-147 | 05 Southwest | 524969 | PORT_EFDC 2 | 69 | 4.1615 | 4.1616 | 0.0001
GEN-2022-147 | 05 Southwest | 524976 | MARKET_ST 2 | 69 | 4.2203 | 4.2204 | 0.0001
GEN-2022-147 | 05 Southwest | 524977 | GREYHOUND 3 | 115 | 5.7679 | 5.7683 | 0.0004
GEN-2022-147 | 05 Southwest | 525018 | MULESHVALLY3 | 115 | 4.9979 | 4.9984 | 0.0005
GEN-2022-147 | 05 Southwest | 525019 | MULSHVLY_TP3 | 115 | 5.3135 | 5.314 | 0.0005
GEN-2022-147 | 05 Southwest | 525056 | BC-EARTH 3 | 115 | 8.1816 | 8.1829 | 0.0013
GEN-2022-147 | 05 Southwest | 525116 | DS-#12 2 | 69 | 2.505 | 2.5051 | 0.0001
GEN-2022-147 | 05 Southwest | 525119 | BC-SUNYSIDE2 | 69 | 1.3832 | 1.3832 | 0
GEN-2022-147 | 05 Southwest | 525122 | HART_INDUST2 | 69 | 2.0488 | 2.0489 | 0.0001
GEN-2022-147 | 05 Southwest | 525124 | HART_INDUST3 | 115 | 7.7526 | 7.7546 | 0.002
GEN-2022-147 | 05 Southwest | 525129 | LC-HART 2 | 69 | 2.6734 | 2.6736 | 0.0002
GEN-2022-147 | 05 Southwest | 525132 | LC-N_OLTON 2 | 69 | 3.2033 | 3.2035 | 0.0002
GEN-2022-147 | 05 Southwest | 525179 | TULIA_TP 3 | 115 | 6.7565 | 6.7582 | 0.0017
GEN-2022-147 | 05 Southwest | 525191 | KRESS_INT 2 | 69 | 4.7137 | 4.7144 | 0.0007
GEN-2022-147 | 05 Southwest | 525192 | KRESS_INT 3 | 115 | 12.4081 | 12.4157 | 0.0076
GEN-2022-147 | 05 Southwest | 525203 | SW-KRESS 2 | 69 | 4.7137 | 4.7144 | 0.0007
GEN-2022-147 | 05 Southwest | 525212 | SWISHER 3 | 115 | 11.9708 | 11.9782 | 0.0074
GEN-2022-147 | 05 Southwest | 525213 | SWISHER 6 | 230 | 10.7209 | 10.735 | 0.0141
GEN-2022-147 | 05 Southwest | 525224 | KRESS_RURL 2 | 69 | 2.6515 | 2.6517 | 0.0002
GEN-2022-147 | 05 Southwest | 525225 | KRESS_RURAL3 | 115 | 6.2581 | 6.2602 | 0.0021
GEN-2022-147 | 05 Southwest | 525226 | KRS_RURL_TP3 | 115 | 6.7494 | 6.7519 | 0.0025
GEN-2022-147 | 05 Southwest | 525233 | BRISCOE 2 | 69 | 0.8585 | 0.8586 | 0.0001
GEN-2022-147 | 05 Southwest | 525240 | LH-SLVRTON+2 | 69 | 0.9768 | 0.9768 | 0
GEN-2022-147 | 05 Southwest | 525249 | LH-PLW&FNY+2 | 69 | 1.682 | 1.6821 | 0.0001
GEN-2022-147 | 05 Southwest | 525256 | SW_9748 2 | 69 | 3.2763 | 3.2767 | 0.0004
GEN-2022-147 | 05 Southwest | 525263 | W_PLAINVEW 2 | 69 | 3.1649 | 3.1653 | 0.0004
GEN-2022-147 | 05 Southwest | 525271 | KISER 2 | 69 | 3.6792 | 3.6797 | 0.0005
GEN-2022-147 | 05 Southwest | 525272 | KISER 3 | 115 | 5.5526 | 5.5545 | 0.0019
GEN-2022-147 | 05 Southwest | 525279 | WSTRIDGE_TP3 | 69 | 4.4596 | 4.4603 | 0.0007
GEN-2022-147 | 05 Southwest | 525284 | WESTRIDGE 2 | 69 | 3.1751 | 3.1755 | 0.0004
GEN-2022-147 | 05 Southwest | 525291 | PLAINVW_TP 2 | 69 | 6.7653 | 6.7671 | 0.0018
GEN-2022-147 | 05 Southwest | 525298 | S_PLAINVEW 2 | 69 | 2.7077 | 2.708 | 0.0003
GEN-2022-147 | 05 Southwest | 525307 | E_PLAINVEW 2 | 69 | 2.6085 | 2.6088 | 0.0003
GEN-2022-147 | 05 Southwest | 525316 | LH-PROVDNCE2 | 69 | 3.6019 | 3.6024 | 0.0005
GEN-2022-147 | 05 Southwest | 525325 | COX 2 | 69 | 3.6019 | 3.6024 | 0.0005
GEN-2022-147 | 05 Southwest | 525326 | COX 3 | 115 | 6.6573 | 6.6603 | 0.003
GEN-2022-147 | 05 Southwest | 525338 | SW_3710 2 | 69 | 2.694 | 2.6942 | 0.0002
GEN-2022-147 | 05 Southwest | 525339 | AIKEN_RURL 2 | 69 | 2.9214 | 2.9218 | 0.0004
GEN-2022-147 | 05 Southwest | 525351 | LH-AIKEN 2 | 69 | 2.2872 | 2.2875 | 0.0003
GEN-2022-147 | 05 Southwest | 525358 | LOCKNEY 2 | 69 | 2.2796 | 2.2799 | 0.0003
GEN-2022-147 | 05 Southwest | 525365 | LH-CDARHLL+2 | 69 | 1.928 | 1.9281 | 0.0001
GEN-2022-147 | 05 Southwest | 525372 | LH-LONESTAR2 | 69 | 1.5268 | 1.5269 | 0.0001
GEN-2022-147 | 05 Southwest | 525373 | LH-LNSTR_TP2 | 69 | 1.5793 | 1.5794 | 0.0001
GEN-2022-147 | 05 Southwest | 525379 | LH-SPLAINS 2 | 69 | 1.2615 | 1.2616 | 0.0001
GEN-2022-147 | 05 Southwest | 525390 | SPRINGLAKE 2 | 69 | 2.1775 | 2.1776 | 0.0001
GEN-2022-147 | 05 Southwest | 525393 | ROCKYFORD 3 | 115 | 8.4606 | 8.4625 | 0.0019
GEN-2022-147 | 05 Southwest | 525397 | OLTON 2 | 69 | 4.3374 | 4.3378 | 0.0004
GEN-2022-147 | 05 Southwest | 525404 | LC-OLTON 2 | 69 | 4.6488 | 4.6493 | 0.0005
GEN-2022-147 | 05 Southwest | 525413 | LAMTON 2 | 69 | 5.3507 | 5.3514 | 0.0007
GEN-2022-147 | 05 Southwest | 525414 | LAMTON 3 | 115 | 7.72 | 7.7223 | 0.0023
GEN-2022-147 | 05 Southwest | 525425 | CORNER 2 | 69 | 3.8009 | 3.8015 | 0.0006
GEN-2022-147 | 05 Southwest | 525432 | SP-HALFWAY+2 | 69 | 6.1232 | 6.1247 | 0.0015
GEN-2022-147 | 05 Southwest | 525440 | LC-S_OLTON+3 | 115 | 7.1705 | 7.1723 | 0.0018
GEN-2022-147 | 05 Southwest | 525446 | RKYFORD_TP 3 | 115 | 9.3524 | 9.3547 | 0.0023
GEN-2022-147 | 05 Southwest | 525453 | HALE_CNTY 2 | 69 | 7.205 | 7.207 | 0.002
GEN-2022-147 | 05 Southwest | 525454 | HALE_CNTY 3 | 115 | 10.4978 | 10.5048 | 0.007
GEN-2022-147 | 05 Southwest | 525460 | NEWHART 3 | 115 | 15.3913 | 15.3989 | 0.0076
GEN-2022-147 | 05 Southwest | 525461 | NEWHART 6 | 230 | 11.0599 | 11.0679 | 0.008
GEN-2022-147 | 05 Southwest | 525480 | PLANT_X 3 | 115 | 15.1786 | 15.1839 | 0.0053
GEN-2022-147 | 05 Southwest | 525481 | PLANT_X 6 | 230 | 23.2323 | 23.2502 | 0.0179
GEN-2022-147 | 05 Southwest | 525531 | TOLK 6 | 230 | 28.5298 | 28.5554 | 0.0256
GEN-2022-147 | 05 Southwest | 525549 | TOLK 7 | 345 | 11.5825 | 11.5884 | 0.0059
GEN-2022-147 | 05 Southwest | 525584 | BLUECLDCOL 6 | 230 | 10.4372 | 10.4408 | 0.0036
GEN-2022-147 | 05 Southwest | 525585 | BLUECLDPOI 6 | 230 | 11.0094 | 11.0134 | 0.004
GEN-2022-147 | 05 Southwest | 525586 | NEEDMORE 6 | 230 | 11.0094 | 11.0134 | 0.004
GEN-2022-147 | 05 Southwest | 525592 | SUDANRURAL 2 | 69 | 1.8939 | 1.894 | 0.0001
GEN-2022-147 | 05 Southwest | 525599 | LC-SANDHLL+2 | 69 | 2.1953 | 2.1953 | 0
GEN-2022-147 | 05 Southwest | 525606 | AMHERST 2 | 69 | 2.4463 | 2.4463 | 0
GEN-2022-147 | 05 Southwest | 525613 | W_LITTLFLD 2 | 69 | 3.0982 | 3.0983 | 0.0001
GEN-2022-147 | 05 Southwest | 525620 | LTFLD_S&CTY2 | 69 | 4.3447 | 4.345 | 0.0003
GEN-2022-147 | 05 Southwest | 525635 | LAMB_CNTY 2 | 69 | 6.1203 | 6.1208 | 0.0005
GEN-2022-147 | 05 Southwest | 525636 | LAMB_CNTY 3 | 115 | 8.6129 | 8.6144 | 0.0015
GEN-2022-147 | 05 Southwest | 525637 | LAMB_CNTY 6 | 230 | 5.5348 | 5.5359 | 0.0011
GEN-2022-147 | 05 Southwest | 525650 | LC-LTTLFLD+2 | 69 | 5.1267 | 5.127 | 0.0003
GEN-2022-147 | 05 Southwest | 525657 | W_ANTON_TP 2 | 69 | 4.2773 | 4.2775 | 0.0002
GEN-2022-147 | 05 Southwest | 525664 | LC-SPD&HART2 | 69 | 2.772 | 2.7721 | 0.0001
GEN-2022-147 | 05 Southwest | 525671 | BAINER 2 | 69 | 3.6546 | 3.6547 | 0.0001
GEN-2022-147 | 05 Southwest | 525678 | W_ANTON 2 | 69 | 2.4697 | 2.4698 | 0.0001
GEN-2022-147 | 05 Southwest | 525687 | LC-LUMSCHAP2 | 69 | 4.7979 | 4.7982 | 0.0003
GEN-2022-147 | 05 Southwest | 525694 | HOBGOOD 2 | 69 | 3.585 | 3.5851 | 0.0001
GEN-2022-147 | 05 Southwest | 525697 | PUMP/YH_TP 2 | 69 | 3.3197 | 3.3199 | 0.0002
GEN-2022-147 | 05 Southwest | 525701 | PHLLPPMP#2 2 | 69 | 1.8096 | 1.8097 | 0.0001
GEN-2022-147 | 05 Southwest | 525703 | YELLOWHOUSE2 | 69 | 2.1823 | 2.1824 | 0.0001
GEN-2022-147 | 05 Southwest | 525708 | MIDAMERI#2 2 | 69 | 2.5573 | 2.5574 | 0.0001
GEN-2022-147 | 05 Southwest | 525717 | WHITHARRAL 2 | 69 | 2.4857 | 2.4857 | 0
GEN-2022-147 | 05 Southwest | 525723 | CNTYLINE_TP2 | 69 | 2.3126 | 2.3132 | 0.0006
GEN-2022-147 | 05 Southwest | 525724 | COUNTYLINE 2 | 69 | 2.0252 | 2.0256 | 0.0004
GEN-2022-147 | 05 Southwest | 525731 | SP-ABERNTHY2 | 69 | 3.162 | 3.163 | 0.001
GEN-2022-147 | 05 Southwest | 525738 | HALECENTER 2 | 69 | 2.5802 | 2.5809 | 0.0007
GEN-2022-147 | 05 Southwest | 525745 | LH-HALECTR 2 | 69 | 2.5512 | 2.5518 | 0.0006
GEN-2022-147 | 05 Southwest | 525763 | CALLAHAN 3 | 115 | 6.1059 | 6.1089 | 0.003
GEN-2022-147 | 05 Southwest | 525779 | FLOYD_CNTY 2 | 69 | 5.872 | 5.8738 | 0.0018
GEN-2022-147 | 05 Southwest | 525780 | FLOYD_CNTY 3 | 115 | 7.0316 | 7.0359 | 0.0043
GEN-2022-147 | 05 Southwest | 525790 | FLOYDADA_TP2 | 69 | 2.686 | 2.6864 | 0.0004
GEN-2022-147 | 05 Southwest | 525797 | S_FLOYDADA 2 | 69 | 2.6718 | 2.6721 | 0.0003
GEN-2022-147 | 05 Southwest | 525801 | LRNZ_MPT 3 | 115 | 6.1421 | 6.1446 | 0.0025
GEN-2022-147 | 05 Southwest | 525803 | BLANCO 3 | 115 | 6.1431 | 6.1456 | 0.0025
GEN-2022-147 | 05 Southwest | 525804 | LH-FLYDADA+2 | 69 | 2.6556 | 2.656 | 0.0004
GEN-2022-147 | 05 Southwest | 525811 | LH-HARMONY 2 | 69 | 4.6562 | 4.6573 | 0.0011
GEN-2022-147 | 05 Southwest | 525816 | TUCO_INT2 2 | 69 | 4.8913 | 4.8937 | 0.0024
GEN-2022-147 | 05 Southwest | 525826 | TUCO_INT 2 | 69 | 8.2644 | 8.2712 | 0.0068
GEN-2022-147 | 05 Southwest | 525828 | TUCO_INT 3 | 115 | 20.4927 | 20.5634 | 0.0707
GEN-2022-147 | 05 Southwest | 525830 | TUCO_INT 6 | 230 | 22.9104 | 23.1829 | 0.2725
GEN-2022-147 | 05 Southwest | 525832 | TUCO_INT 7 | 345 | 13.2084 | 13.5343 | 0.3259
GEN-2022-147 | 05 Southwest | 525840 | ANTELOPE_1 6 | 230 | 22.7162 | 22.9837 | 0.2675
GEN-2022-147 | 05 Southwest | 525850 | ELK_CT1 | 345 | 13.0768 | 13.396 | 0.3192
GEN-2022-147 | 05 Southwest | 525853 | LH-WIL&ELN+2 | 69 | 2.6679 | 2.6686 | 0.0007
GEN-2022-147 | 05 Southwest | 525860 | SP-BECTON +2 | 69 | 2.3676 | 2.3682 | 0.0006
GEN-2022-147 | 05 Southwest | 525867 | ALLMON 2 | 69 | 2.3017 | 2.3019 | 0.0002
GEN-2022-147 | 05 Southwest | 525874 | LH-PETERBRG2 | 69 | 2.3044 | 2.3046 | 0.0002
GEN-2022-147 | 05 Southwest | 525885 | SP-NEWDEAL 2 | 69 | 3.4747 | 3.4759 | 0.0012
GEN-2022-147 | 05 Southwest | 525891 | WHITEHEAD 2 | 69 | 2.6802 | 2.681 | 0.0008
GEN-2022-147 | 05 Southwest | 525892 | MONROE 2 | 69 | 2.7811 | 2.7819 | 0.0008
GEN-2022-147 | 05 Southwest | 525899 | SP-SHALLWTR2 | 69 | 2.2058 | 2.2063 | 0.0005
GEN-2022-147 | 05 Southwest | 525906 | SP-ACUFF +2 | 69 | 2.0739 | 2.0741 | 0.0002
GEN-2022-147 | 05 Southwest | 525915 | SP-CROSBY 2 | 69 | 4.8908 | 4.8917 | 0.0009
GEN-2022-147 | 05 Southwest | 525925 | CROSBY 2 | 69 | 5.4788 | 5.4799 | 0.0011
GEN-2022-147 | 05 Southwest | 525926 | CROSBY 3 | 115 | 5.4533 | 5.4553 | 0.002
GEN-2022-147 | 05 Southwest | 525936 | LH-CROSBY +2 | 69 | 3.6845 | 3.685 | 0.0005
GEN-2022-147 | 05 Southwest | 525943 | HENDRICKS 2 | 69 | 3.649 | 3.6495 | 0.0005
GEN-2022-147 | 05 Southwest | 525957 | HALE_WNDCL16 | 230 | 12.3168 | 12.3757 | 0.0589
GEN-2022-147 | 05 Southwest | 525979 | LC-HODGE 2 | 69 | 1.5753 | 1.5753 | 0
GEN-2022-147 | 05 Southwest | 525986 | ELLWOOD 2 | 69 | 1.3457 | 1.3457 | 0
GEN-2022-147 | 05 Southwest | 525995 | LC-HODGE_TP2 | 69 | 2.724 | 2.7241 | 0.0001
GEN-2022-147 | 05 Southwest | 526002 | LC-WHITHRRL2 | 69 | 2.9994 | 2.9996 | 0.0002
GEN-2022-147 | 05 Southwest | 526009 | LC-LEVLND#22 | 69 | 4.4555 | 4.4559 | 0.0004
GEN-2022-147 | 05 Southwest | 526019 | HOCKLEY 2 | 69 | 5.3343 | 5.3348 | 0.0005
GEN-2022-147 | 05 Southwest | 526020 | HOCKLEY 3 | 115 | 5.6378 | 5.6387 | 0.0009
GEN-2022-147 | 05 Southwest | 526030 | LC-PETTIT +2 | 69 | 1.9724 | 1.9724 | 0
GEN-2022-147 | 05 Southwest | 526042 | COBLE 2 | 69 | 2.3684 | 2.3684 | 0
GEN-2022-147 | 05 Southwest | 526048 | LVLNDCTY_TP2 | 69 | 4.4555 | 4.4559 | 0.0004
GEN-2022-147 | 05 Southwest | 526049 | LVLAND_CITY2 | 69 | 4.0575 | 4.0578 | 0.0003
GEN-2022-147 | 05 Southwest | 526056 | E_LEVELLAND2 | 69 | 1.7504 | 1.7504 | 0
GEN-2022-147 | 05 Southwest | 526073 | STANTON_N 2 | 69 | 1.7481 | 1.7484 | 0.0003
GEN-2022-147 | 05 Southwest | 526075 | STANTON_E 2 | 69 | 3.3876 | 3.3881 | 0.0005
GEN-2022-147 | 05 Southwest | 526076 | STANTON_W 3 | 115 | 9.3499 | 9.3601 | 0.0102
GEN-2022-147 | 05 Southwest | 526086 | SW_6786_N 2 | 69 | 5.2251 | 5.2264 | 0.0013
GEN-2022-147 | 05 Southwest | 526087 | SW_6786_S 2 | 69 | 5.2251 | 5.2264 | 0.0013
GEN-2022-147 | 05 Southwest | 526102 | SP-HETTLER 2 | 69 | 3.3367 | 3.3372 | 0.0005
GEN-2022-147 | 05 Southwest | 526109 | SP-ERSKINE 3 | 115 | 11.482 | 11.4957 | 0.0137
GEN-2022-147 | 05 Southwest | 526116 | SP-IDALOU +2 | 69 | 2.3437 | 2.3439 | 0.0002
GEN-2022-147 | 05 Southwest | 526123 | VICKERS 2 | 69 | 2.188 | 2.1882 | 0.0002
GEN-2022-147 | 05 Southwest | 526130 | SP-CARLISLE2 | 69 | 2.2067 | 2.207 | 0.0003
GEN-2022-147 | 05 Southwest | 526146 | INDIANA 3 | 115 | 9.7436 | 9.7543 | 0.0107
GEN-2022-147 | 05 Southwest | 526159 | CARLISLE 2 | 69 | 2.6836 | 2.684 | 0.0004
GEN-2022-147 | 05 Southwest | 526160 | CARLISLE 3 | 115 | 13.343 | 13.3607 | 0.0177
GEN-2022-147 | 05 Southwest | 526161 | CARLISLE 6 | 230 | 10.8202 | 10.8487 | 0.0285
GEN-2022-147 | 05 Southwest | 526162 | LP-DOUD_TP 3 | 115 | 11.8312 | 11.8443 | 0.0131
GEN-2022-147 | 05 Southwest | 526176 | LP-DOUD 3 | 115 | 9.2586 | 9.2666 | 0.008
GEN-2022-147 | 05 Southwest | 526184 | SW_6878 2 | 69 | 2.2601 | 2.2604 | 0.0003
GEN-2022-147 | 05 Southwest | 526192 | MURPHY 3 | 115 | 10.8556 | 10.8667 | 0.0111
GEN-2022-147 | 05 Southwest | 526195 | QUINCY 3 | 115 | 10.1326 | 10.142 | 0.0094
GEN-2022-147 | 05 Southwest | 526196 | SP-MILWAUKEE | 115 | 7.8153 | 7.8209 | 0.0056
GEN-2022-147 | 05 Southwest | 526198 | SP-UPLAND | 115 | 5.9606 | 5.9638 | 0.0032
GEN-2022-147 | 05 Southwest | 526205 | IVORY 2 | 69 | 4.101 | 4.1017 | 0.0007
GEN-2022-147 | 05 Southwest | 526213 | ALLEN 3 | 115 | 10.9067 | 10.9162 | 0.0095
GEN-2022-147 | 05 Southwest | 526221 | BATTON_N 2 | 69 | 1.8599 | 1.8601 | 0.0002
GEN-2022-147 | 05 Southwest | 526228 | BATTON_S 2 | 69 | 2.838 | 2.8383 | 0.0003
GEN-2022-147 | 05 Southwest | 526236 | LP-WHEELOCK3 | 115 | 8.8052 | 8.8115 | 0.0063
GEN-2022-147 | 05 Southwest | 526249 | ACCO 2 | 69 | 3.338 | 3.3384 | 0.0004
GEN-2022-147 | 05 Southwest | 526256 | IVORY_TP 2 | 69 | 4.097 | 4.0977 | 0.0007
GEN-2022-147 | 05 Southwest | 526267 | LUBBCK_STH 2 | 69 | 4.536 | 4.5369 | 0.0009
GEN-2022-147 | 05 Southwest | 526268 | LUBBCK_STH 3 | 115 | 18.8045 | 18.83 | 0.0255
GEN-2022-147 | 05 Southwest | 526269 | LUBBCK_STH 6 | 230 | 16.2186 | 16.2522 | 0.0336
GEN-2022-147 | 05 Southwest | 526284 | PLANTERS 2 | 69 | 6.0266 | 6.0283 | 0.0017
GEN-2022-147 | 05 Southwest | 526297 | LUBBCK_EST 2 | 69 | 8.3492 | 8.3526 | 0.0034
GEN-2022-147 | 05 Southwest | 526298 | LUBBCK_EST 3 | 115 | 15.4619 | 15.4811 | 0.0192
GEN-2022-147 | 05 Southwest | 526299 | LUBBCK_EST 6 | 230 | 11.9172 | 11.935 | 0.0178
GEN-2022-147 | 05 Southwest | 526310 | CLUTTER 2 | 69 | 5.6767 | 5.6782 | 0.0015
GEN-2022-147 | 05 Southwest | 526337 | JONES 6 | 230 | 18.1797 | 18.2192 | 0.0395
GEN-2022-147 | 05 Southwest | 526409 | SLAUGHTER 2 | 69 | 2.337 | 2.3371 | 0.0001
GEN-2022-147 | 05 Southwest | 526416 | SLAUGTER_TP2 | 69 | 3.3056 | 3.3058 | 0.0002
GEN-2022-147 | 05 Southwest | 526434 | SUNDOWN 3 | 115 | 11.1831 | 11.1871 | 0.004
GEN-2022-147 | 05 Southwest | 526435 | SUNDOWN 6 | 230 | 11.2944 | 11.3049 | 0.0105
GEN-2022-147 | 05 Southwest | 526460 | AMOCO_SS 6 | 230 | 9.9892 | 9.997 | 0.0078
GEN-2022-147 | 05 Southwest | 526475 | YUMA_INT 3 | 115 | 11.18 | 11.191 | 0.011
GEN-2022-147 | 05 Southwest | 526481 | SP-WOLF_TP 3 | 115 | 11.3489 | 11.3604 | 0.0115
GEN-2022-147 | 05 Southwest | 526483 | SP-WOLFORTH3 | 115 | 8.8627 | 8.8697 | 0.007
GEN-2022-147 | 05 Southwest | 526499 | LG-MEADOW 2 | 69 | 3.9045 | 3.9048 | 0.0003
GEN-2022-147 | 05 Southwest | 526506 | LG-DOCWEBR 2 | 69 | 5.2086 | 5.2092 | 0.0006
GEN-2022-147 | 05 Southwest | 526513 | LG-TWO_DRAW2 | 69 | 2.9484 | 2.9487 | 0.0003
GEN-2022-147 | 05 Southwest | 526524 | WOLFFORTH 3 | 115 | 11.7693 | 11.7798 | 0.0105
GEN-2022-147 | 05 Southwest | 526525 | WOLFFORTH 6 | 230 | 13.1617 | 13.189 | 0.0273
GEN-2022-147 | 05 Southwest | 526562 | SLATON 2 | 69 | 2.5948 | 2.5951 | 0.0003
GEN-2022-147 | 05 Southwest | 526569 | SP-SLATON 2 | 69 | 1.2739 | 1.274 | 0.0001
GEN-2022-147 | 05 Southwest | 526576 | SOUTHLAND 2 | 69 | 1.4561 | 1.4561 | 0
GEN-2022-147 | 05 Southwest | 526583 | LG-HAKBERRY2 | 69 | 1.717 | 1.7171 | 0.0001
GEN-2022-147 | 05 Southwest | 526592 | DIEKEMPER 2 | 69 | 2.9607 | 2.9611 | 0.0004
GEN-2022-147 | 05 Southwest | 526602 | WOODROW 3 | 115 | 9.6743 | 9.6808 | 0.0065
GEN-2022-147 | 05 Southwest | 526615 | YANCY_TP 2 | 69 | 1.3755 | 1.3755 | 0
GEN-2022-147 | 05 Southwest | 526622 | GARZA 2 | 69 | 3.2673 | 3.2677 | 0.0004
GEN-2022-147 | 05 Southwest | 526631 | LAKEVIEW 2 | 69 | 1.5815 | 1.5815 | 0
GEN-2022-147 | 05 Southwest | 526638 | LG-NEWMOORE2 | 69 | 1.9429 | 1.9431 | 0.0002
GEN-2022-147 | 05 Southwest | 526645 | LG-NH&WILN+2 | 69 | 3.3875 | 3.3879 | 0.0004
GEN-2022-147 | 05 Southwest | 526655 | LYNN_CNTY 2 | 69 | 4.823 | 4.8239 | 0.0009
GEN-2022-147 | 05 Southwest | 526656 | LYNN_CNTY 3 | 115 | 6.3024 | 6.3049 | 0.0025
GEN-2022-147 | 05 Southwest | 526666 | LG-CENTRAL 2 | 69 | 2.1286 | 2.1288 | 0.0002
GEN-2022-147 | 05 Southwest | 526676 | GRASSLAND 3 | 115 | 7.3197 | 7.323 | 0.0033
GEN-2022-147 | 05 Southwest | 526677 | GRASSLAND 6 | 230 | 6.4914 | 6.4964 | 0.005
GEN-2022-147 | 05 Southwest | 526679 | CIRRUS_WND 6 | 230 | 5.1054 | 5.1085 | 0.0031
GEN-2022-147 | 05 Southwest | 526693 | GRAHAM 2 | 69 | 3.5347 | 3.5351 | 0.0004
GEN-2022-147 | 05 Southwest | 526694 | GRAHAM 3 | 115 | 2.9765 | 2.977 | 0.0005
GEN-2022-147 | 05 Southwest | 526703 | YANCY_SUB 2 | 69 | 1.2562 | 1.2562 | 0
GEN-2022-147 | 05 Southwest | 526711 | LG-DIXON 2 | 69 | 2.6302 | 2.6304 | 0.0002
GEN-2022-147 | 05 Southwest | 526719 | BG-YANCY_TP2 | 69 | 1.354 | 1.3541 | 0.0001
GEN-2022-147 | 05 Southwest | 526726 | LG-DRAW 2 | 69 | 2.6558 | 2.6561 | 0.0003
GEN-2022-147 | 05 Southwest | 526735 | TERRY_CNTY 2 | 69 | 7.3534 | 7.3545 | 0.0011
GEN-2022-147 | 05 Southwest | 526736 | TERRY_CNTY 3 | 115 | 11.075 | 11.0789 | 0.0039
GEN-2022-147 | 05 Southwest | 526747 | LG-BROWNFLD2 | 69 | 3.7514 | 3.7516 | 0.0002
GEN-2022-147 | 05 Southwest | 526754 | BROWNFIELD 2 | 69 | 3.2098 | 3.21 | 0.0002
GEN-2022-147 | 05 Southwest | 526761 | BROWNFLD_TP2 | 69 | 2.9729 | 2.9731 | 0.0002
GEN-2022-147 | 05 Southwest | 526770 | OZARK_MAHO 2 | 69 | 1.8801 | 1.8802 | 0.0001
GEN-2022-147 | 05 Southwest | 526777 | GOODPASTURE2 | 69 | 2.5286 | 2.5287 | 0.0001
GEN-2022-147 | 05 Southwest | 526784 | AMOCOWASSON6 | 230 | 14.6483 | 14.656 | 0.0077
GEN-2022-147 | 05 Southwest | 526792 | PRENTICE 3 | 115 | 6.2782 | 6.2793 | 0.0011
GEN-2022-147 | 05 Southwest | 526799 | JST_CORNER 2 | 69 | 1.7235 | 1.7237 | 0.0002
GEN-2022-147 | 05 Southwest | 526800 | BG-GARZA 2 | 69 | 0.9895 | 0.9895 | 0
GEN-2022-147 | 05 Southwest | 526807 | BG-JUSTBRG 2 | 69 | 0.8105 | 0.8106 | 0.0001
GEN-2022-147 | 05 Southwest | 526814 | BG-FLUVANNA2 | 69 | 1.0378 | 1.0379 | 0.0001
GEN-2022-147 | 05 Southwest | 526821 | BG-JSTBG_TP2 | 69 | 1.3278 | 1.3279 | 0.0001
GEN-2022-147 | 05 Southwest | 526928 | PLAINS_INT 3 | 115 | 10.3386 | 10.3409 | 0.0023
GEN-2022-147 | 05 Southwest | 526934 | YOAKUM 3 | 115 | 19.4895 | 19.4979 | 0.0084
GEN-2022-147 | 05 Southwest | 526935 | YOAKUM 6 | 230 | 18.9473 | 18.9657 | 0.0184
GEN-2022-147 | 05 Southwest | 526936 | YOAKUM_345 | 345 | 10.025 | 10.0451 | 0.0201
GEN-2022-147 | 05 Southwest | 526944 | LG-PLAINS 3 | 115 | 8.1877 | 8.1892 | 0.0015
GEN-2022-147 | 05 Southwest | 526953 | TOKIO 2 | 69 | 1.6815 | 1.6815 | 0
GEN-2022-147 | 05 Southwest | 526959 | LG-TOKIO 2 | 69 | 1.6745 | 1.6746 | 0.0001
GEN-2022-147 | 05 Southwest | 526965 | KINNEY 2 | 69 | 2.5576 | 2.5577 | 0.0001
GEN-2022-147 | 05 Southwest | 526971 | TOKIO_TP 2 | 69 | 3.874 | 3.8741 | 0.0001
GEN-2022-147 | 05 Southwest | 526979 | LG-JS_SMITH2 | 69 | 2.208 | 2.2081 | 0.0001
GEN-2022-147 | 05 Southwest | 526985 | WELLMAN 2 | 69 | 3.0303 | 3.0304 | 0.0001
GEN-2022-147 | 05 Southwest | 526993 | LG-WELLMAN 2 | 69 | 3.2538 | 3.2539 | 0.0001
GEN-2022-147 | 05 Southwest | 527009 | BRU_SUB 6 | 230 | 15.0449 | 15.0547 | 0.0098
GEN-2022-147 | 05 Southwest | 527010 | OXYBRU 6 | 230 | 14.9162 | 14.9258 | 0.0096
GEN-2022-147 | 05 Southwest | 527011 | XTO_MAHONEY6 | 230 | 14.6877 | 14.6965 | 0.0088
GEN-2022-147 | 05 Southwest | 527018 | BENNETT 3 | 115 | 14.1574 | 14.1605 | 0.0031
GEN-2022-147 | 05 Southwest | 527021 | CORTEZ 3 | 115 | 8.3793 | 8.3802 | 0.0009
GEN-2022-147 | 05 Southwest | 527022 | APACHE_ROB 3 | 115 | 9.7824 | 9.7836 | 0.0012
GEN-2022-147 | 05 Southwest | 527024 | ALLRED_SUB 3 | 115 | 11.0282 | 11.0298 | 0.0016
GEN-2022-147 | 05 Southwest | 527027 | INK_BASIN 3 | 115 | 13.3881 | 13.3904 | 0.0023
GEN-2022-147 | 05 Southwest | 527028 | INK_BASIN 6 | 230 | 11.3716 | 11.3761 | 0.0045
GEN-2022-147 | 05 Southwest | 527030 | ALRDCRTZ_TP3 | 115 | 12.5338 | 12.5359 | 0.0021
GEN-2022-147 | 05 Southwest | 527041 | ARCO_TP 3 | 115 | 14.0605 | 14.0636 | 0.0031
GEN-2022-147 | 05 Southwest | 527047 | OXY_WILRD1 3 | 115 | 11.2449 | 11.2469 | 0.002
GEN-2022-147 | 05 Southwest | 527062 | SHELL_CO2 3 | 115 | 17.1158 | 17.1199 | 0.0041
GEN-2022-147 | 05 Southwest | 527130 | DENVER_N 3 | 115 | 22.9114 | 22.918 | 0.0066
GEN-2022-147 | 05 Southwest | 527136 | DENVER_S 3 | 115 | 22.9114 | 22.918 | 0.0066
GEN-2022-147 | 05 Southwest | 527146 | MUSTANG 3 | 115 | 24.5053 | 24.5124 | 0.0071
GEN-2022-147 | 05 Southwest | 527149 | MUSTANG 6 | 230 | 16.2162 | 16.2247 | 0.0085
GEN-2022-147 | 05 Southwest | 527151 | GS-MUSTANG 6 | 230 | 16.2162 | 16.2247 | 0.0085
GEN-2022-147 | 05 Southwest | 527194 | LG-PLSHILL 3 | 115 | 8.2514 | 8.2526 | 0.0012
GEN-2022-147 | 05 Southwest | 527201 | SEAGRAVES 2 | 69 | 5.7872 | 5.7875 | 0.0003
GEN-2022-147 | 05 Southwest | 527202 | SEAGRAVES 3 | 115 | 9.473 | 9.4745 | 0.0015
GEN-2022-147 | 05 Southwest | 527217 | MOSS 2 | 69 | 5.6793 | 5.6797 | 0.0004
GEN-2022-147 | 05 Southwest | 527223 | LG-MC&SMNL+2 | 69 | 2.7399 | 2.74 | 0.0001
GEN-2022-147 | 05 Southwest | 527238 | ROZ 3 | 115 | 11.5375 | 11.5392 | 0.0017
GEN-2022-147 | 05 Southwest | 527242 | AMERADA 3 | 115 | 11.6929 | 11.6947 | 0.0018
GEN-2022-147 | 05 Southwest | 527275 | SEMINOLE 3 | 115 | 14.8599 | 14.8628 | 0.0029
GEN-2022-147 | 05 Southwest | 527276 | SEMINOLE 6 | 230 | 8.1589 | 8.1609 | 0.002
GEN-2022-147 | 05 Southwest | 527598 | SAGA_NDCOL 7 | 345 | 8.8449 | 8.8475 | 0.0026
GEN-2022-147 | 05 Southwest | 527599 | SAGA_SDCOL 7 | 345 | 10.1699 | 10.1734 | 0.0035
GEN-2022-147 | 05 Southwest | 527600 | SAGA_SMEAS 7 | 345 | 10.1699 | 10.1734 | 0.0035
GEN-2022-147 | 05 Southwest | 527601 | SAGA_NCOL 7 | 345 | 8.8449 | 8.8475 | 0.0026
GEN-2022-147 | 05 Southwest | 527610 | SAGA_SCOL 7 | 345 | 10.1699 | 10.1734 | 0.0035
GEN-2022-147 | 05 Southwest | 527654 | RSVLT_CC_W 7 | 345 | 8.8166 | 8.8192 | 0.0026
GEN-2022-147 | 05 Southwest | 527655 | RSVLT_CC_E 7 | 345 | 9.9639 | 9.9674 | 0.0035
GEN-2022-147 | 05 Southwest | 527656 | CROSSROADS 7 | 345 | 11.3506 | 11.3552 | 0.0046
GEN-2022-147 | 05 Southwest | 527666 | RSVLT_COL1 7 | 345 | 8.8166 | 8.8192 | 0.0026
GEN-2022-147 | 05 Southwest | 527667 | RSVLT_COL2 7 | 345 | 8.8166 | 8.8192 | 0.0026
GEN-2022-147 | 05 Southwest | 527799 | EDDY_NORTH 6 | 230 | 9.5726 | 9.5748 | 0.0022
GEN-2022-147 | 05 Southwest | 527802 | EDDY_CNTY 7 | 345 | 7.4665 | 7.4689 | 0.0024
GEN-2022-147 | 05 Southwest | 527864 | CUNNINHAM 3 | 115 | 28.5556 | 28.5599 | 0.0043
GEN-2022-147 | 05 Southwest | 527865 | CUNNIGHM_N 6 | 230 | 17.9281 | 17.9333 | 0.0052
GEN-2022-147 | 05 Southwest | 527867 | CUNNIGHM_S 6 | 230 | 17.9281 | 17.9333 | 0.0052
GEN-2022-147 | 05 Southwest | 527891 | HOBBS_INT 3 | 115 | 32.4839 | 32.4896 | 0.0057
GEN-2022-147 | 05 Southwest | 527894 | HOBBS_INT 6 | 230 | 19.8352 | 19.8425 | 0.0073
GEN-2022-147 | 05 Southwest | 527896 | HOBBS_INT 7 | 345 | 12.1126 | 12.1215 | 0.0089
GEN-2022-147 | 05 Southwest | 527962 | POTASH_JCT 3 | 115 | 17.6768 | 17.6809 | 0.0041
GEN-2022-147 | 05 Southwest | 527965 | KIOWA 7 | 345 | 8.9723 | 8.9762 | 0.0039
GEN-2022-147 | 05 Southwest | 527966 | KIOWA 3 | 115 | 17.65 | 17.6542 | 0.0042
GEN-2022-147 | 05 Southwest | 528013 | PHANTOM 3 | 115 | 13.5366 | 13.5396 | 0.003
GEN-2022-147 | 05 Southwest | 528015 | PHANTOM 7 | 345 | 5.8402 | 5.8419 | 0.0017
GEN-2022-147 | 05 Southwest | 528018 | RED_BLUFF 3 | 115 | 10.5894 | 10.5911 | 0.0017
GEN-2022-147 | 05 Southwest | 528024 | RR_SVC_HV 3 | 115 | 14.2388 | 14.242 | 0.0032
GEN-2022-147 | 05 Southwest | 528025 | RDRUNNER 3 | 115 | 14.2388 | 14.242 | 0.0032
GEN-2022-147 | 05 Southwest | 528027 | RDRUNNER 7 | 345 | 8.8437 | 8.8479 | 0.0042
GEN-2022-147 | 05 Southwest | 528040 | BATTLE_AXE 3 | 115 | 3.3595 | 3.3597 | 0.0002
GEN-2022-147 | 05 Southwest | 528182 | NORTH_LOVNG3 | 115 | 12.8494 | 12.852 | 0.0026
GEN-2022-147 | 05 Southwest | 528185 | N_LOVING 7 | 345 | 6.7183 | 6.7205 | 0.0022
GEN-2022-147 | 05 Southwest | 528195 | AGAVE_PDURO3 | 115 | 8.3598 | 8.3609 | 0.0011
GEN-2022-147 | 05 Southwest | 528223 | CHINA_DRAW 7 | 345 | 5.9888 | 5.9906 | 0.0018
GEN-2022-147 | 05 Southwest | 528230 | AGAVE_RHILL3 | 115 | 12.7841 | 12.7867 | 0.0026
GEN-2022-147 | 05 Southwest | 528231 | AGAVE_RHIL23 | 115 | 12.037 | 12.0393 | 0.0023
GEN-2022-147 | 05 Southwest | 528232 | OCHOA 3 | 115 | 12.094 | 12.0963 | 0.0023
GEN-2022-147 | 05 Southwest | 528239 | CUSTERMTN 3 | 115 | 7.9796 | 7.9803 | 0.0007
GEN-2022-147 | 05 Southwest | 528240 | PONDEROSA 3 | 115 | 4.2202 | 4.2204 | 0.0002
GEN-2022-147 | 05 Southwest | 528325 | LE-WAITS 3 | 115 | 9.2722 | 9.2731 | 0.0009
GEN-2022-147 | 05 Southwest | 528333 | LE-WEST_SUB3 | 115 | 9.4012 | 9.4018 | 0.0006
GEN-2022-147 | 05 Southwest | 528353 | MADDOXG23 3 | 115 | 27.4191 | 27.423 | 0.0039
GEN-2022-147 | 05 Southwest | 528355 | MADDOX 3 | 115 | 27.4191 | 27.423 | 0.0039
GEN-2022-147 | 05 Southwest | 528433 | BENSING 3 | 115 | 8.378 | 8.3784 | 0.0004
GEN-2022-147 | 05 Southwest | 528435 | MILLEN 3 | 115 | 12.0244 | 12.0253 | 0.0009
GEN-2022-147 | 05 Southwest | 528602 | ANDREWS 3 | 115 | 10.1799 | 10.1808 | 0.0009
GEN-2022-147 | 05 Southwest | 528604 | ANDREWS 6 | 230 | 6.3047 | 6.3054 | 0.0007
GEN-2022-147 | 05 Southwest | 528617 | LE-WAITS 2 | 69 | 3.7066 | 3.7067 | 0.0001
GEN-2022-147 | 05 Southwest | 528626 | LE-PLNSINT 2 | 69 | 3.8049 | 3.8051 | 0.0002
GEN-2022-147 | 05 Southwest | 528669 | LE-STKLDRTP2 | 69 | 2.0911 | 2.0912 | 0.0001
GEN-2022-147 | 05 Southwest | 528670 | LE-STAKHLDR2 | 69 | 2.0381 | 2.0382 | 0.0001
GEN-2022-147 | 05 Southwest | 528709 | LE-PLNSGOAB2 | 69 | 2.9334 | 2.9335 | 0.0001
GEN-2022-147 | 05 Southwest | 528714 | LE-FORT_SW 2 | 69 | 3.484 | 3.4841 | 0.0001
GEN-2022-147 | 05 Southwest | 528718 | LE-NEWTEX 2 | 69 | 2.7438 | 2.7438 | 0
GEN-2022-147 | 05 Southwest | 528722 | LE-LEWIS 2 | 69 | 1.8853 | 1.8853 | 0
GEN-2022-147 | 05 Southwest | 528725 | LE-PRICE 2 | 69 | 1.8923 | 1.8924 | 0.0001
GEN-2022-147 | 05 Southwest | 528735 | LE-PLAINSUB2 | 69 | 2.7931 | 2.7932 | 0.0001
GEN-2022-147 | 05 Southwest | 528740 | LE-PLANS_SW2 | 69 | 2.795 | 2.7951 | 0.0001
GEN-2022-147 | 05 Southwest | 528747 | LE-ALLRED 2 | 69 | 2.6661 | 2.6662 | 0.0001
GEN-2022-147 | 05 Southwest | 528754 | LE-HIGGBTHM2 | 69 | 2.0981 | 2.0982 | 0.0001
GEN-2022-147 | 05 Southwest | 528759 | LE-TP51 2 | 69 | 2.4183 | 2.4184 | 0.0001
GEN-2022-147 | 05 Southwest | 528763 | LE-TP91 2 | 69 | 1.8014 | 1.8014 | 0
GEN-2022-147 | 05 Southwest | 528780 | LE-NITROTEC2 | 69 | 2.1164 | 2.1164 | 0
GEN-2022-147 | 05 Southwest | 528784 | LE-DARBY 2 | 69 | 1.3145 | 1.3145 | 0
GEN-2022-147 | 05 Southwest | 539801 | THISTLE7 | 345 | 16.1361 | 16.1363 | 0.0002
GEN-2022-147 | 05 Southwest | 560071 | G16-003-TAP | 345 | 14.8173 | 14.8181 | 0.0008
GEN-2022-147 | 05 Southwest | 560078 | G16-037-TAP | 345 | 8.9528 | 8.9554 | 0.0026
GEN-2022-147 | 05 Southwest | 560756 | CEILO-TAP-N | 69 | 0.809 | 0.809 | 0
GEN-2022-147 | 05 Southwest | 563259 | GEN-2015-092 | 345 | 5.406 | 5.4065 | 0.0005
GEN-2022-147 | 05 Southwest | 563269 | GEN-2015-093 | 345 | 9.7556 | 9.7569 | 0.0013
GEN-2022-147 | 05 Southwest | 585190 | GEN-2015-082 | 345 | 7.3129 | 7.313 | 0.0001
GEN-2022-147 | 05 Southwest | 585300 | GEN-2015-095 | 138 | 14.6186 | 14.6187 | 0.0001
GEN-2022-147 | 05 Southwest | 585410 | GREAT_WESTRN | 345 | 8.7021 | 8.7024 | 0.0003
GEN-2022-147 | 05 Southwest | 585420 | COWBOY_RIDGE | 345 | 6.7362 | 6.7364 | 0.0002
GEN-2022-147 | 05 Southwest | 585430 | PRSIMN_CRK1 | 345 | 10.501 | 10.5015 | 0.0005
GEN-2022-147 | 05 Southwest | 585440 | PRSIMN_CRK2 | 345 | 9.6649 | 9.6653 | 0.0004
GEN-2022-147 | 05 Southwest | 587020 | GEN-2016-003 | 345 | 14.8173 | 14.8181 | 0.0008
GEN-2022-147 | 05 Southwest | 587230 | GEN-2016-037 | 345 | 7.6707 | 7.6726 | 0.0019
GEN-2022-147 | 05 Southwest | 587740 | GEN-2016-091 | 345 | 9.9166 | 9.9183 | 0.0017
GEN-2022-147 | 05 Southwest | 587744 | G16-091-TAP | 345 | 14.0357 | 14.0391 | 0.0034
GEN-2022-147 | 05 Southwest | 587770 | GEN-2016-095 | 345 | 10.2488 | 10.2506 | 0.0018
GEN-2022-147 | 05 Southwest | 587990 | GEN-2016-121 | 115 | 13.1746 | 13.1774 | 0.0028
GEN-2022-147 | 05 Southwest | 588460 | A16-008SUB | 115 | 13.3881 | 13.3904 | 0.0023
GEN-2022-147 | 05 Southwest | 588560 | GEN-2017-011 | 345 | 12.0982 | 12.0988 | 0.0006
GEN-2022-147 | 05 Southwest | 588630 | GEN-2017-018 | 345 | 16.1361 | 16.1363 | 0.0002
GEN-2022-147 | 05 Southwest | 588760 | GEN-2017-033 | 345 | 4.1852 | 4.189 | 0.0038
GEN-2022-147 | 05 Southwest | 599955 | PNM-DC6 | 230 | 9.1879 | 9.19 | 0.0021
GEN-2022-147 | 05 Southwest | 599960 | EPTNP-D6 | 230 | 9.5726 | 9.5748 | 0.0022
GEN-2022-147 | 05 Southwest | 755000 | WWDBORDT | 345 | 10.4525 | 10.4587 | 0.0062
GEN-2022-147 | 05 Southwest | 760494 | GEN-2017-146 | 230 | 7.6646 | 7.6658 | 0.0012
GEN-2022-147 | 05 Southwest | 760498 | G17-146-TAP | 230 | 7.9578 | 7.9591 | 0.0013
GEN-2022-147 | 05 Southwest | 760938 | G17-171-TAP | 345 | 10.1359 | 10.1384 | 0.0025
GEN-2022-147 | 05 Southwest | 760939 | GEN-2017-171 | 345 | 10.1359 | 10.1384 | 0.0025
GEN-2022-147 | 05 Southwest | 761355 | GEN-2017-239 | 230 | 13.3164 | 13.3235 | 0.0071
GEN-2022-147 | 05 Southwest | 761439 | GEN-2017-176 | 230 | 11.0599 | 11.0679 | 0.008
GEN-2022-147 | 05 Southwest | 761460 | GEN-2017-116 | 230 | 6.0082 | 6.0091 | 0.0009
GEN-2022-147 | 05 Southwest | 761467 | G17-116-TAP | 230 | 6.0082 | 6.0091 | 0.0009
GEN-2022-147 | 05 Southwest | 761523 | GEN-2017-217 | 230 | 21.7481 | 21.7638 | 0.0157
GEN-2022-147 | 05 Southwest | 762111 | GEN-2017-102 | 345 | 9.6978 | 9.7012 | 0.0034
GEN-2022-147 | 05 Southwest | 762132 | GEN-2017-158 | 230 | 12.9438 | 12.9488 | 0.005
GEN-2022-147 | 05 Southwest | 762174 | G17-218TAP | 230 | 24.3577 | 24.3769 | 0.0192
GEN-2022-147 | 05 Southwest | 762175 | GEN-2017-218 | 230 | 24.2702 | 24.2893 | 0.0191
GEN-2022-147 | 05 Southwest | 762216 | G17-151TAP | 345 | 8.0278 | 8.1178 | 0.09
GEN-2022-147 | 05 Southwest | 762217 | GEN-2017-151 | 345 | 5.9911 | 6.039 | 0.0479
GEN-2022-147 | 05 Southwest | 769921 | GEN-2022-147 | 345 | 13.2084 | 13.5343 | 0.3259
GEN-2022-147 | 05 Southwest | 900001 | TRAVERSE3 | 345 | 5.4514 | 5.4515 | 0.0001
GEN-2022-147 | 05 Southwest | 900002 | TRAVERSE-2 | 345 | 4.0862 | 4.0862 | 0
GEN-2022-147 | 05 Southwest | 900003 | TRAVERSE1 | 345 | 3.7987 | 3.7987 | 0
GEN-2022-147 | 05 Southwest | 900004 | TRW2-TRW3 | 345 | 4.7434 | 4.7435 | 0.0001