## Executive Summary
Executive Summary: GEN-2022-098 Limited Operation System Impact Study
Interconnection Customer (GEN-2022-098) has requested a Limited Operation System Impact Study under the Southwest Power Pool Open Access Transmission Tariff (OATT).
Results of this study determine whether there will be sufficient stability and reliability margin on the Transmission System with anticipated topology to accommodate Interconnection Requests for each Generating Facility at the Interconnection Customer’s requested In-Service Date.
This study evaluates Network Upgrades and Generating Facility exclusions (Scenarios Tab) at the time of service to determine the amount of Interconnection Capacity available to the interconnection customers listed under specific system conditions.
Once a GIA amendment to incorporate Limited Operation is effective, SPP and Transmission Owner will permit Interconnection Customer to operate the Generating Facilities under Limited Operation in accordance with the SPP study results.
Limited Operation
In accordance with Section 8.4.3 of the GIP, Availability of Limited Operation, SPP determines in the DISIS whether the full amount of interconnection capacity requested by the Interconnection Customers is available by the requested Commercial Operation Date (COD). SPP quantifies, within the “Requests” tab of the DISIS report, the amount of interconnection capacity available to Interconnection Customers prior to the in-service date of identified Network Upgrades.
In accordance with GIA Article 5.9, Limited Operation, Interconnection Customers may request SPP to perform studies to determine the Limited Operation of each Generating Facility prior to the completion of the identified mitigation for the observed system constraint(s).
Limited Operation conditions and amounts permitted as determined in this study are detailed in the Scenarios Tab.
Study Limitations
Limited Operation Interconnection Service Available between April 1 - May 31 : 200 MW
Limited Operation Interconnection Service Available between June 1 - Sept 30 : 200 MW
Limited Operation Interconnection Service Available between Oct 1 - Nov 30 : 200 MW
Limited Operation Interconnection Service Available between Dec 1 - March 31 : 200 MW
In the event that an Interconnection Request, with queue priority equal to or higher than an Interconnection Request, which was excluded as a study scenario achieves a status of Commercial Operation prior to the in-service date of all required Network Upgrades, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
In the event that a Network Upgrade which was included as a study scenario is not placed in-service prior to the Commercial Operation of Interconnection Requests, the results of this study revise to 0 MW of available Interconnection Service until a restudy is completed to identify a revised amount for this system condition.
SPP study results do not guarantee operation for all periods of time. Although studies analyzed many of the most probable contingencies, they are not an all‐inclusive list and cannot account for every operational situation. It is likely that the customer(s) may be required to reduce their generation output to 0 MW, also known as curtailment, under certain system conditions to allow system operators to maintain the reliability of the transmission network.
DISIS Manual Version 4.4
https://www.spp.org/media/2400/gi-manual-business-practice_7250_20251017.pdf
Models Used in Study
Power Flow Analysis: DISIS-2022-001 (2022 ITP Series)* * modified to exclude network upgrades assigned through DISIS-1701,DISIS-1702 and DISIS-1801, DISIS-1802/1901, DISIS-2020-001, and DISIS-2021-001.
Summer: 2024 (24SP), 2027 (27SP)
Winter: 2027 (27WP)
Stability Analysis: DISIS-2022-001 (2020 MDWG) * modified to exclude network upgrades assigned through DISIS-1701,DISIS-1702 and DISIS-1801, DISIS-1802/1901, DISIS-2020-001, and DISIS-2021-001.
Summer: 2025 (25SP)
Winter: 2025 (25WP)
Short Circuit Analysis: DISIS-2022-001 (2020 MDWG) * modified to exclude network upgrades assigned through DISIS-1701,DISIS-1702 and DISIS-1801, DISIS-1802/1901, DISIS-2020-001, and DISIS-2021-001.
Summer: 2025 (25SP)
Author: SPP Generator Interconnection Department
Published: 9/15/2026

## Revision History
Revision History
Date | Author | Change Description
2026-09-15 | SPP | Initial Draft

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 | June 1 - Sept 30 | Oct 1 - Nov 30 | Dec 1 - March 31 | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | 0 | 0 | 0 | 200 | -5.2217 | ER/NR | OGE | Bison 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [5 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [5 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal: CTG | 250 | [5 empty] | ER | BEPC | Judson Substation 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [5 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [5 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [5 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [5 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [5 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [5 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [5 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | IA PENDING
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [5 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | IA PENDING
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [5 empty] | ER/NR | KCPL | Nashua-Smithville 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [5 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | IA PENDING
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Hybrid: Solar and Storage | 80 | [5 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [5 empty] | ER/NR | KCPL | Liberty West 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [5 empty] | ER | KCPL | Shoal Creek 161 kV Substation | IA PENDING
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [5 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [5 empty] | ER | WERE | Burns 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [5 empty] | ER | WERE | Gill - Viola 138 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [5 empty] | ER/NR | OGE | Woodward 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [5 empty] | ER/NR | OGE | Woodward 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [5 empty] | ER/NR | OGE | Woodward 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [5 empty] | ER | AEP | Longwood to Scottville 138 kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [5 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | IA PENDING
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.82 | [5 empty] | ER/NR | AEP | Talawanda to Canadian River 138 kV Line Tap | IA PENDING
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.08 | [5 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Hybrid: Solar and Storage | 150 | [5 empty] | ER/NR | AEP | Wilkes 345 kV Substation | FACILITY STUDY STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [5 empty] | ER/NR | OGE | Battlefield BESS 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [5 empty] | ER | WFEC | Colbert 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [5 empty] | ER | AEP | Pirkey 345kV Substation | IA PENDING
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [5 empty] | ER | OGE | Caney Creek 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [5 empty] | ER | AEP | Weatherford Jct. to Hinton 138 kV line | IA PENDING
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [5 empty] | ER | WFEC | Canadian Switch 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [5 empty] | ER | OGE | Horseshoe Lake 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [5 empty] | ER | GRDA | Silver City 138 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [5 empty] | ER/NR | AEP | Northeastern - Delaware 345 kV transmission line | IA PENDING
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [5 empty] | ER/NR | WFEC | El Reno SW 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [5 empty] | ER/NR | OGE | Maud 138 kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal: CTG | 203 | [5 empty] | ER | SPS | Tuco 345kV | IA FULLY EXECUTED/ON SCHEDULE
J2088 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 400 | [5 empty] | ER/NR | XEL | WEST MEMPHIS EHV - KEO EHV 500 kV (854.0) | Done: Phase 3
J1849 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | EES | Cypress 230 kV | Done: Phase 3
J1855 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 500 | [5 empty] | ER/NR | EES-EAI | MALLORY 161 | Done: Phase 3
J1856 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 140 | [5 empty] | ER/NR | EES-EAI | SHOFFNER - NEWPORT | Done: Phase 3
J1858 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 440 | [5 empty] | ER/NR | EES-EAI | Sandy Bayou | Done: Phase 3
J1872 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [5 empty] | ER/NR | EES-EAI | El Dorado 500kV Substation | Done: Phase 3
J1873 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [5 empty] | ER/NR | EES-EAI | El Dorado 500kV Substation | Done: Phase 3
J1890 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 270 | [5 empty] | ER/NR | EES | HARTBURG - AEP LAYFIELD 500.0kV | Done: Phase 3
J1891 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 200 | [5 empty] | ER/NR | EES-EMI | 230 kV McAdams Substation | Done: Phase 3
J1897 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 500 | [5 empty] | ER/NR | EES-EAI | DELL EHV - SAN SOUCI 500.0kV | Done: Phase 3
J1899 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 500 | [5 empty] | ER/NR | EES-EAI | DELL EHV - SAN SOUCI 500.0kV | Done: Phase 3
J1946 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 350 | [5 empty] | ER/NR | SMEPA | 230 kV Missionary Substation | Done: Phase 3
J2010 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 75 | [5 empty] | ER/NR | EES-EAI | STUTTGART RICUSKEY - WOODWARD 230 SUB 230.0kV | Done: Phase 3
J2047 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 199 | [5 empty] | ER | EES-EMI | Robinsonville 230 kV | Done: Phase 3
J2071 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 198 | [5 empty] | ER/NR | EES | RYE CO - CYPRESS 138.0kV | Done: Phase 3
J2075 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | EES | China (Bus# 334204) to Sheco Batiste Creek (Bus# 334240) | Done: Phase 3
J2089 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | EES-EAI | Line tap DELL to Manilla AECC 161 kV | Done: Phase 3
J2091 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Battery/Storage | 250 | [5 empty] | ER/NR | EES-EMI | TWINKLETOWN 230 KV | Done: Phase 3
J2127 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 172.5 | [5 empty] | ER/NR | SMEPA | Silver Creek 115kV | Done: Phase 3
J2133 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 100 | [5 empty] | ER/NR | EES-EAI | Garner 115 kV Substation | Done: Phase 3
J2143 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [5 empty] | ER/NR | EES-EAI | Lake Village Bagby 115 KV | Done: Phase 3
J2153 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 134 | [5 empty] | ER/NR | EES-EAI | Ashley Switchyard | Done: Phase 3
J2165 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 145 | [5 empty] | ER | EES | JACINTO - SHECO BATISTE CREEK 230.0kV | Done: Phase 3
J2173 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 396 | [5 empty] | ER/NR | EES-EMI | BOLTON | Done: Phase 3
J2180 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [5 empty] | ER/NR | CLEC | Fisher | Done: Phase 3
J2181 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | EES-EAI | 161 kV line tap of DELL EAST to Blytheville | Done: Phase 3
J2190 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 500 | [5 empty] | ER/NR | EES-EAI | DELL EHV - SAN SOUCI 500.0kV | Done: Phase 3
J2228 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | EES | Red Gum | Done: Phase 3
J2237 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 185 | [5 empty] | ER/NR | EES-EAI | Brinkley East - Aubrey 230 kV Line | Done: Phase 3
J2261 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 625 | [5 empty] | ER/NR | EES-EAI | INDEPENDENCE-ISES - POWERLINE ROAD 500.0kV | Done: Phase 3
J2262 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 625 | [5 empty] | ER/NR | EES-EAI | INDEPENDENCE-ISES - POWERLINE ROAD 500.0kV | Done: Phase 3
J2287 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 122 | [5 empty] | ER | EES-EMI | DELTA SES SWITCHYARD 115kV | Done: Phase 3
J2292 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 50 | [5 empty] | ER/NR | LAGN | GOOS FERRY | Done: Phase 3
J2294 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 250 | [5 empty] | ER/NR | EES-EAI | Dell to Nucor 161 kV | Done: Phase 3
J2298 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | EES-EAI | Gainesville Switching Station | Done: Phase 3
J2314 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 150 | [5 empty] | ER/NR | EES | PETRY WOODS SS | Done: Phase 3
J2317 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Solar | 202.5 | [5 empty] | ER/NR | EES | BASTROP (CAHOON) - STERLINGTON 115 SWYD 115.0kV | Done: Phase 3
J1846 | 01 NORTH | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 200 | [5 empty] | ER/NR | XEL | PANTHER | Active: Phase 2
J1898 | 01 NORTH | 23.5 | DIS-22-PQ | Battery/Storage | 200 | [5 empty] | ER/NR | XEL | Byron 161 kV | Active: Phase 2
J2027 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 150 | [5 empty] | ER/NR | GRE | CHUB LAKE - 304JB21/22 - HAMPTON - 8S50/51 345.0kV | Active: Phase 2
J2053 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 151.47 | [5 empty] | ER/NR | XEL | Cedar Mountain - Lyon County 345.0kV | Active: Phase 2
J2087 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 125 | [5 empty] | ER/NR | XEL | FRANKLIN | Active: Phase 2
J2097 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 100 | [5 empty] | ER/NR | MP | Tri-County 230 kV Substation | Active: Phase 2
J2104 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 230 | [5 empty] | ER/NR | XEL | Cedar Mountain - Lyon County 345.0kV | Active: Phase 2
J2157 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 100 | [5 empty] | ER/NR | MP | Tri-County 230 kV Substation | Active: Phase 2
J2219 | 01 NORTH | 23.5 | DIS-22-PQ | Hybrid: Battery and Solar | 180 | [5 empty] | ER/NR | DPC | ROCHESTER - WABACO 161.0kV | Active: Phase 2
J2227 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 80.1 | [5 empty] | ER/NR | DPC | Independence - Bridge Creek 69.0kV | Active: Phase 2
J2250 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 200 | [5 empty] | ER | OTP | Ellendale 345 | Active: Phase 2
J2276 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 39.5 | [5 empty] | ER/NR | OTP | ALEXANDRIA | Active: Phase 2
J2309 | 01 NORTH | 23.5 | DIS-22-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Chanarambie - ELLSBOROUGH (GRE) 115.0kV | Active: Phase 2
J1889 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Solar | 60 | [5 empty] | ER/NR | ALTW | Mount Vernon | Active: Phase 2
J2031 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Wind | 100 | [5 empty] | ER/NR | ALTW | Toledo | Active: Phase 2
J2078 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Solar | 200 | [5 empty] | ER/NR | ALTW | Fernald | Active: Phase 2
J2120 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Battery/Storage | 100 | [5 empty] | ER/NR | ALTW | Fairfax | Active: Phase 2
J2268 | 02 NEBRASKA | 23.5 | DIS-22-PQ | Solar | 370 | [5 empty] | ER/NR | ALTW | Duane Arnold | Active: Phase 2
J1867 | 04 SOUTHEAST | 23.5 | DIS-22-PQ | Wind | 200 | [5 empty] | ER/NR | ALTW | Quinn | Active: Phase 2
MPC04500 | 01 NORTH | 23.5 | DIS-22-PQ | Wind | 250 | [5 empty] | ER/NR | OTP
J1519 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 180 | [5 empty] | ER/NR | AMMO | St. Francois to Lutesville 345 kV | Done: GIA
J1649 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 60 | [5 empty] | ER/NR | BREC | Shell - McCracken County 69.0kV | Done: GIA
J1836 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | Solar | 275 | [5 empty] | ER/NR | AMMO | Montgomery- Callaway- 7 | Done: GIA
GIA-116 | 04 SOUTHEAST | 22.5 | DIS-21-1-PQ | Thermal | 26 | [5 empty] | ER/NR | AECI
GIA-117 | 04 SOUTHEAST | 22.5 | DIS-21-1-PQ | Thermal | 46 | [5 empty] | ER/NR | AECI
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [5 empty] | ER | NPPD | Olive Creek 115 kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [5 empty] | ER | LES | Rokeby 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [5 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [5 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [5 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [5 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [5 empty] | ER/NR | LES | Wagener 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [5 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [5 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [5 empty] | ER | SPS | Carpenter 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [5 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [5 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [5 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [5 empty] | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [5 empty] | ER | WERE | Viola 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [5 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [5 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [5 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Hybrid: Solar and Storage | 95 | [5 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [5 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [5 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [5 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [5 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [5 empty] | ER/NR | OKGE | 138kV Brown Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [5 empty] | ER | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [5 empty] | ER/NR | OKGE | Sooner 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [5 empty] | ER | WERE | Wild Plains 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [5 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [5 empty] | ER | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [5 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [5 empty] | ER/NR | AEPW | Welsh 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [5 empty] | ER/NR | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [5 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [5 empty] | ER | OKGE | Pecan Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [5 empty] | ER | OKGE | Pecan Creek 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 155 | [5 empty] | ER/NR | AEPW | Craig JCT 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 100 | [5 empty] | ER/NR | AEPW | Carnegie South 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [5 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 50 | [5 empty] | ER/NR | SPS |  | DISIS STAGE
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 40 | [5 empty] | ER/NR | SPS |  | DISIS STAGE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid: Solar and Storage | 400 | [5 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA PENDING
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal: Gas | 45 | [5 empty] | ER/NR | BEPC | Lonesome Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Hybrid: Solar and Storage | 74.5 | [5 empty] | ER/NR | WAPA | Fairview 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-002 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 81 | [5 empty] | ER | OPPD | 6846 Substation 69 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 320 | [5 empty] | ER/NR | NPPD | Axtell 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid: Solar and Storage | 215 | [5 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [5 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 255 | [5 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [5 empty] | ER | OPPD | Substation 1363; 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: CT | 272.7 | [5 empty] | ER | OPPD | Substation 3740; 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [5 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [5 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal: Reciprocating Engine | 56.52 | [5 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [5 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [5 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [5 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 35 | [5 empty] | ER | KCPL |  | DISIS STAGE
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 35 | [5 empty] | ER | KCPL |  | DISIS STAGE
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Diesel and Gas | 58 | [5 empty] | ER/NR | WERE | East Substation 69 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 650 | [5 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 250 | [5 empty] | ER | SPS | Corporation Carpenter 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 20 | [5 empty] | ER/NR | SUNC | Russell 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [5 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [5 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: Gas | 29 | [5 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal: CT | 64 | [5 empty] | ER/NR | EDE | 4544 Stateline CC 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 150 | [5 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid: Solar and Storage | 225 | [5 empty] | ER/NR | EDE | Riverton-Neosho 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [5 empty] | ER/NR | EDE | La Russell 161 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [5 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 140 | [5 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 113 | [5 empty] | ER/NR | AEP | Snyder â€“ Altus Jct. 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid: Solar and Storage | 201.6 | [5 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [5 empty] | ER/NR | AEPW | Lydia 345 kV Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [5 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [5 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [5 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [5 empty] | ER | SPS | Lubbock East Substation 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal: Combined Cycle | 1003 | [5 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [5 empty] | ER | SPS | Tuco to Yoakum 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.15 | [5 empty] | ER/NR | BEPC-SPP | Siouxland 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | [5 empty] | ER/NR | BEPC-SPP | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | [5 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 78 | [5 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | [5 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | [5 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal: Gas Turbine | 15.56 | [5 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 252 | [5 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | [5 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [5 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [5 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [5 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [5 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [5 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [5 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 100 | [5 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | [5 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 180 | [5 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | [5 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | Battery/Storage | 207 | [5 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | [5 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
MPC04300 | 01 NORTH | 20.5 | DIS-18-2-PQ | Wind | 400 | [5 empty] | ER/NR | OTP
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 460 | [5 empty] | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 75 | [5 empty] | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | Gas | 460 | [5 empty] | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | Gas | 460 | [5 empty] | ER/NR | AECI
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | Wind | 255 | [5 empty] | ER | BEPC-SPP | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | Wind | 72 | [5 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 231 | [5 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | [5 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | [5 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | Battery/Storage | 95 | [5 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | Wind | 200.22 | [5 empty] | ER/NR | WERE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | [5 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [5 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [5 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | [5 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | Wind | 215 | [5 empty] | ER | AEPW | Pittsburg 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | [5 empty] | ER | AEPW | Longwood 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Hybrid: Solar and Storage | 250 | [5 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 196 | [5 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 300 | [5 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 290 | [5 empty] | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | Done: GIA
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 380 | [5 empty] | ER/NR | AMMO | Spencer Creek 345 kV Substation | Done: GIA
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [5 empty] | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | Done: GIA
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [5 empty] | ER/NR | AMMO | Zachary Substation 345 kV Bus | Done: GIA
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 68.4 | [5 empty] | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | Done: GIA
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [5 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138 kV line | Done: GIA
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [5 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | Done: GIA
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hydro | 60 | [5 empty] | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | Done: GIA
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 185 | [5 empty] | ER/NR | AMIL | Ashley 138 kV Substation | Done: GIA
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 165 | [5 empty] | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | Done: GIA
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | AMMO | Pike - Troy 161kV Line | Done: GIA
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 95 | [5 empty] | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | Done: GIA
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | AMIL | Commodore-Jordan 345kV Line | Done: GIA
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | Done: GIA
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 500 | [5 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Done: GIA
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 1000 | [5 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Done: GIA
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | AMMO | Spencer Creek 345kV Substation | Done: GIA
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 300 | [5 empty] | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | Done: GIA
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | [5 empty] | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | Done: GIA
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | Done: GIA
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | Done: GIA
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 149 | [5 empty] | ER/NR | AMMO | Miner - Kelso 161kV Line | Done: GIA
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 180 | [5 empty] | ER/NR | EES-EAI | Marion - Marked Tree 161kV Line Tap | Done: GIA
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER | EES | Poco - Menard 138kV Line Tao | Done: GIA
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 450 | [5 empty] | ER/NR | EES-EAI | West Memphis - Keo 500 kV Line Tap | Done: GIA
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [5 empty] | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV Line Tap | Done: GIA
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | EES-EAI | Driver 230 kV Substation | Done: GIA
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [5 empty] | ER | CLEC | Centennial - West Bay 138kV Line | Done: GIA
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 155 | [5 empty] | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | Done: GIA
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER | EES | Rilla 115 kV Substation | Done: GIA
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done: GIA
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 | [5 empty] | ER/NR | EES-EAI | Crossett - Monticello East 115kV Line | Done: GIA
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 | [5 empty] | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | Done: GIA
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 0 | [5 empty] | ER/NR | EES-EAI | Cash - Newport AB161kV Line | Done: GIA
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 250 | [5 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Done: GIA
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER | CLEC | Cooper - Penton Road 230kV Line | Done: GIA
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | Done: GIA
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER | EES | Oak Ridge 115 kV Substation | Done: GIA
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 180 | [5 empty] | ER/NR | EES-EAI | AECC Dry Creek 161kV Switchyard Station | Done: GIA
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 105 | [5 empty] | ER | EES | Rich (SHECO) - Livingston 138 kV Line Tap | Done: GIA
J1514 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | EES-EAI | Driver 203kV Substation | Done: GIA
J1558 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | EES-EAI | MORELAND | Done: GIA
J1559 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | Done: GIA
J1562 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | EES-EAI | BLYTHEVILLE I-55 - AECC BLYTHEVILLE NORTH 161.0kV | Done: GIA
J1577 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | EES-EAI | HARDIN WEST SS - SHERIDAN 115.0kV | Done: GIA
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 325 | [5 empty] | ER/NR | EES | Goos Ferry | Done: GIA
J1602 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery/Storage | 25 | [5 empty] | ER/NR | EES | Rilla 115kV substation (Same as J1239) | Done: GIA
J1612 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | Done: GIA
J1669 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [5 empty] | ER | EES | LAKE CHARLES BULK | Done: GIA
J1670 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | Done: GIA
J1671 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER | EES | Rocky Creek to Lewis Creek 230kV | Done: GIA
J1672 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | EES-EMI | Tinnin Road 230kV | Done: GIA
J1673 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | CLEC | Fisher - Marthaville 230.0kV | Done: GIA
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 300 | [5 empty] | ER/NR | EES-EAI | KEO EHV | Done: GIA
J1747 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | EES-EMI | J830 POI | Done: GIA
J1748 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | EES-EMI | Twinkletown 230 kV | Done: GIA
J1760 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 205 | [5 empty] | ER/NR | EES | Timberland 230kV | Done: GIA
J1816 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [5 empty] | ER/NR | EES-EAI | FISHER - CHERRY VALLEY 161.0kV | Done: GIA
J1820 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | EES-EAI | WEST MEMPHIS EHV - KEO EHV 500.0kV | Done: GIA
J1827 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 90 | [5 empty] | ER/NR | EES | bastrop tap point | Done: GIA
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Gas | 126 | [5 empty] | ER/NR | EES | Sabine 138/230 kV Substation | Done: GIA
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 135 | [5 empty] | NR | EES-EAI | FORREST CITY N SS - WYNNE SOUTH 161.0kV | Done: GIA
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [5 empty] | ER/NR | MDU | Wishek Junction 230 kV Substation | Done: GIA
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Battery/Storage | 20 | [5 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | Done: GIA
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | XEL | Adams 345 kV Substation | Done: GIA
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Three Lakes 115 kV Substation | Done: GIA
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Byron 345kV Substation | Done: GIA
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 | [5 empty] | ER | ALTW | Magnolia 161 kV Substation | Done: GIA
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER | XEL | Grant 115 kV Substation | Done: GIA
J1181 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 200 | [5 empty] | ER/NR | ALTW | Hazleton - Mitchell county 345 kV line | Done: GIA
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | GRE | Wing River- Riverton 230kV line | Done: GIA
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | XEL | Grant 115 kV Substation | Done: GIA
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | DPC | Apple River 161 kV Substation | Done: GIA
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Benton County 115kV Substation | Done: GIA
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Mayhew Lake 115kV Substation | Done: GIA
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [5 empty] | ER | OTP | Astoria 345 kV Substation (J493/J510) | Done: GIA
J1503 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | ALTW | Huntley | Done: GIA
J1504 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | ALTW | Huntley | Done: GIA
J1534 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Byron | Done: GIA
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [5 empty] | ER/NR | ALTW | Rutland | Done: GIA
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hybrid: Battery and Solar | 150 | [5 empty] | ER/NR | XEL | Huntley to Blue Earth 161kV | Done: GIA
J1575 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 70 | [5 empty] | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | Done: GIA
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | XEL | NOBLES COUNTY | Done: GIA
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | XEL | BISON | Done: GIA
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | XEL | SHERBURNE CO | Done: GIA
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 120 | [5 empty] | ER/NR | XEL | Langdon 115 kV Sub | Done: GIA
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 125 | [5 empty] | ER/NR | XEL | Split Rock - Pipestone 115.0kV | Done: GIA
J1657 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | XEL | Pine Lake to Apple River 161 kV | Done: GIA
J1730 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 300 | [5 empty] | ER/NR | XEL | Eau Claire to AS King 345 kV | Done: GIA
J1769 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 80 | [5 empty] | ER/NR | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | Done: GIA
J1808 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 148 | [5 empty] | ER/NR | DPC | Barron 161 kV | Done: GIA
J1826 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hydro | 4 | [5 empty] | ER/NR | XEL | Cannon Falls Transmission 69 kV | Done: GIA
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | [5 empty] | ER/NR | XEL | Adams 345kV Substation | Done: GIA
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 | [5 empty] | ER/NR | ALTW | Doud Tap 161 kV Substation | Done: GIA
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | ALTW | Creston East 69 kV Substation | Done: GIA
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 | [5 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | Done: GIA
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 | [5 empty] | ER | ALTW | Ledyard - Colby 345kV Line Tap | Done: GIA
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [5 empty] | ER/NR | MEC | Kossuth - O'Brien 345 kV Line Tap | Done: GIA
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 | [5 empty] | ER/NR | ALTW | 161kV bus at Karma substation | Done: GIA
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Gas | 95 | [5 empty] | ER/NR | ALTW | Oakridge 69 kV Substation | Done: GIA
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 169.4 | [5 empty] | ER/NR | ALTW | Traer 161-kV Substation | Done: GIA
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 | [5 empty] | ER/NR | ALTW | Duane Arnold 345kV Substation | Done: GIA
J1520 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 135 | [5 empty] | ER/NR | ALTW | Other_ | Done: GIA
J1529 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | Done: GIA
J1530 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | Done: GIA
J1532 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [5 empty] | ER/NR | MEC | Clarinda-Coburg 69 kV | Done: GIA
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [5 empty] | ER/NR | MEC | REMSEN TOWNSHIP | Done: GIA
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 | [5 empty] | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | Done: GIA
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 170 | [5 empty] | ER | OTP
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 130 | [5 empty] | ER | OTP |  | DISIS STAGE
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [5 empty] | ER/NR | OTP |  | DISIS STAGE
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 151.2 | [5 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 300 | [5 empty] | ER/NR | OTP
GEN-2018-010 | 01 NORTH | 20 | DIS-18-1 | Battery/Storage | 74.1 | [5 empty] | ER/NR | BEPC-SPP | Neset 230kV Substation | TERMINATED
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [5 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [5 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [5 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [5 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [5 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | TERMINATED
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [5 empty] | ER | KCPL | Tap Appleton - Rockbille 34.5kV | DISIS STAGE
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [5 empty] | ER | KCPL | Tap Metz-Dederick Junction 34.5kV | DISIS STAGE
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [5 empty] | ER | KCPL | Tap Salisbury - Glasgow 34.5kV | DISIS STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [5 empty] | ER | KCPL | Tap Wal-Mart-Rock Creek 34.5kV | DISIS STAGE
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [5 empty] | ER | KCPL | Tap Rock Creek-Lane 34.5kV | DISIS STAGE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [5 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [5 empty] | ER | KCPL | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 310 | [5 empty] | ER | WERE | Neosho 345kV Substation | TERMINATED
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [5 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [5 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [5 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [5 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [5 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [5 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [5 empty] | ER | AEPW | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [5 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [5 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [5 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [5 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [5 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [5 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [5 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [5 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | [5 empty] | ER | XEL | Buffalo 115kV Substation | Done: GIA
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | [5 empty] | ER | OTP | Big Stone South 230kV Substation | Done: GIA
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | [5 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line | Done: GIA
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | [5 empty] | ER | DPC | Rice - Beaver Creek 161kV line tap | Done: GIA
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 101.28 | [5 empty] | ER | XEL | Pine Lake - Apple River 161 kV Line | Done: GIA
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | [5 empty] | ER | ALTW | Ledyard 345kV Substation | Done: GIA
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 | [5 empty] | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | Done: GIA
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [5 empty] | ER/NR | ALTW | Murray Junction 69 kV substation | IA PENDING
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | [5 empty] | ER/NR | AECI | McCredie 345 kV
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | [5 empty] | ER/NR | AECI | Thomas Hill 69 kV
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | [5 empty] | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | [5 empty] | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | [5 empty] | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 | [5 empty] | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 270 | [5 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [5 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [5 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [5 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [5 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [5 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [5 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [5 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [5 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [5 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [5 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [5 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 | [5 empty] | ER | KCPL | Holt County 345 kV | TERMINATED
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [5 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [5 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [5 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [5 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [5 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [5 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [5 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [5 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [5 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 201.6 | [5 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [5 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [5 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [5 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [5 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [5 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [5 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [5 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [5 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [5 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [5 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [5 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [5 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [5 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [5 empty] | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [5 empty] | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [5 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [5 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [5 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [5 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [5 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [5 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [5 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J718 | 01 NORTH | 17.5 | DIS-17-1-PQ | Solar | 45 | [5 empty] | ER/NR | DPC | Cherry Grove 69kV Substation | Done: GIA
J748 | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 200 | [5 empty] | ER/NR | MEC | Highland - Raun 345kV Line Tap | Done: GIA
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | [5 empty] | ER | WAPA | NELSON 7
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [5 empty] | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [5 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [5 empty] | ER | BEPC-SPP | Neset 230 kV Substation | TERMINATED
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [5 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [5 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [5 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [5 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [5 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [5 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [5 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [5 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [5 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [5 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [5 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [5 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [5 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [5 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [5 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [5 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [5 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [5 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [5 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [5 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [5 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [5 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [5 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
J569 | 01 NORTH | 16.5 | DIS-16-2-PQ | Wind | 100 | [5 empty] | ER/NR | XEL
J476 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | Wind | 246 | [5 empty] | ER/NR | AMMO
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [5 empty] | ER | WAPA | Campbell County 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [5 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [5 empty] | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [5 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [5 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [5 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [5 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [5 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [5 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [5 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 147.5 | [5 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [5 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [5 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [5 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [5 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [5 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [5 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [5 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [5 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [5 empty] | ER | SPS | Powell Corner 115kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [5 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Thermal: Gas Turbine | 17 | [5 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [5 empty] | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [5 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [5 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [5 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Thermal: Steam Turbine | 29 | [5 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [5 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 | [5 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [5 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [5 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [5 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [5 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [5 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 64.6 | [5 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [5 empty] | ER | SPS | Palo Buro 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [5 empty] | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [5 empty] | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [5 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 | [5 empty] | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [5 empty] | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [5 empty] | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 16 | [5 empty] | ER/NR | BEPC-SPP
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [5 empty] | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [5 empty] | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 | [5 empty] | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [5 empty] | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 34 | [5 empty] | ER/NR | BEPC-SPP
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [5 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery/Storage | 10.3 | [5 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [5 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [5 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [5 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 219.96 | [5 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [5 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [5 empty] | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | [5 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [5 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [5 empty] | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [5 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | [5 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [5 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | [5 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | [5 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [5 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | [5 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 3.96 | [5 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [5 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [5 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.53 | [5 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [5 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Solar | 73.6 | [5 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [5 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Solar | 50.6 | [5 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [5 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [5 empty] | ER | SPS
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [5 empty] | ER | SPS
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | [5 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | [5 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [5 empty] | ER | SPS | FEC 69kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Thermal | 22.5 | [5 empty] | ER | SUNC
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [5 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | [5 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [5 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [5 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | [5 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [5 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 165.6 | [5 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [5 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | [5 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [5 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [5 empty] | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [5 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | [5 empty] | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | Wind | 20 | [5 empty] | ER | NPPD | Tekamah & Oakland 115kV
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [5 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | [5 empty] | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [5 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [5 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal: Gas | 550 | [5 empty] | ER | AEP | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 SOUTHWEST | 8 | PQ | Wind | 240 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [5 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 299.2 | [5 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | [5 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 24SP | ERIS 27SP | ERIS 27L | ERIS 27WP | NRIS 24SP | NRIS 27SP | NRIS 27L | NRIS 27WP | Stability SP | Stability WP
GEN-2022-098 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 200 | 0 | Instability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 200 | 0 | 200
GEN-2022-098 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 200 | 0 | Instability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 200 | 0 | 200
GEN-2022-098 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 200 | 200 | None | None | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200
GEN-2022-098 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 200 | 200 | None | None | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200
GEN-2022-098 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 200 | 0 | Instability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 200 | N/A | N/A | N/A | 200 | N/A | N/A | 0 | N/A
GEN-2022-098 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 200 | 0 | Instability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 0 | N/A
GEN-2022-098 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Instability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 200 | 0 | 200
GEN-2022-098 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Instability | Line - Beckham County - Potter -345 kV New Line (2024 ITP) | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 200 | 0 | 200

## Upgrade Removal Summary
NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Source Study | Included/Excluded? | Estimated In-Service Date / Lead Time (months)
210483 | 72019 | Multi - Park Community - Sunshine 138 kV | Calumet - Concho 138 kV Ckt 1 Voltage Conversion | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. | DPA-2017-August-767-774-776 | Excluded | 2025-12-30
210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Excluded | 2026-06-01
210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Excluded | 2026-06-30
210483 | 72023 | Multi - Park Community - Sunshine 138 kV | El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | DPA-2017-August-767-774-776 | Excluded | 2026-07-31
210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Excluded | 2026-09-30
210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Excluded | 2027-02-28
210489 | 82112 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. | DPA-2017-December-815 | Excluded | 2026-04-28
210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Excluded | 2027-02-28
210545 | 112395 | Device - Gypsum 69 kV Capacitor Bank | Gypsum 69 kV Capacitor Bank | Install a new 12 MVAR capacitor bank at Gypsum 69 kV substation. | 2019 ITP | Excluded | 2026-03-31
210545 | 112435 | Line - East Kingfisher - Kingfisher 138kV | East Kingfisher - Kingfisher 138 kV Rebuild | Rebuild 2.03 miles of 138 kV line from Kingfisher to East Kingfisher and upgrade any necessary terminal equipment at East Kingfisher and/or Kingfisher to increase the summer emergency rating to 187 MVA | 2019 ITP | Excluded | 2026-05-31
210586 | 112443 | Line - Russett - South Brown 138 kV | Russett - South Brown 138 kV Ckt 1 Rebuild | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 2020 ITP | Excluded | 2027-10-31
210544 | 112460 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sand Springs - Sheffield Steel 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA | 2019 ITP | Excluded | 2026-02-26
210575 | 122730 | Line - South Shreveport - Wallace Lake 138 kV #2 | South Shreveport - Wallace Lake 138 kV Ckt 1 Rebuild #2 | Rebuild 11.18 miles of 138 kV line from South Shreveport to Wallace Lake and upgrade any necessary terminal equipment to achieve a summer emergency to 347 MVA | 2020 ITP | Excluded | 2025-12-29
220773 | 122756 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Substation Rebuild and Line Re-termination | Rebuild Anadarko SPA 138 kV substation to support a new second and third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA. Re-terminate all existing lines into the new station. | 2023 ITP | Excluded | 2028-05-31
210617 | 143254 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Lexington - Lil Axe 138 kV | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV | DPA-2020-May-1203 | Excluded | 2025-12-31
210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Excluded | 2026-09-30
220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Excluded | 2026-12-31
220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Excluded | 2026-12-31
220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Excluded | 2026-12-31
220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Excluded | 2026-12-31
220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Excluded | 2026-12-31
220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Excluded | 2026-12-31
220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Excluded | 2027-12-31
220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Excluded | 2027-12-31
220773 | 158638 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 2 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV to support a second 138 kV line from Anadarko to Gracemont. | 2023 ITP | Excluded | 2028-05-31
220880 | 159382 | Line - N Reed Spring 161 kV - S Reed Spring 161 kV Rebuild | N Reed Spring - S Reed Spring 161 kV Ckt 1 Rebuild | Rebuild 1.5 mile Ckt 1 line from N Reed Spring 161 kV substation to S Reed Spring 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2024 ITP | Excluded | 2029-11-01
220812 | 170066 | Line - Beckham County - Potter -345 kV New Line | Beckham County 345 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Beckham County 345 kV substation to support the line from Beckham County 345 kV substation to Potter 345 kV substation with a summer emergency rating of 1792 MVA. | 2024 ITP | Excluded | 2029-11-12
220812 | 170168 | Device - Maud Tap 138 kV Terminal Equipment | Maud Tap 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Maud Tap 138 kV substation for the line from Maud Tap 138 kV substation to Earlsboro 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Excluded | 2026-05-31
220804 | 170384 | XFR - Tulsa North 345/138 kV | Tulsa North 345/138 kV Transformer Ckt 2 (138 kV) | Install new 345/138 transformer at Tulsa North 138 kV substation | 2024 ITP | Excluded | 2029-03-01
220804 | 170385 | XFR - Tulsa North 345/138 kV | Tulsa North 345/138 kV Transformer Ckt 2 (345 kV) | Install 345 kV terminal equipment to support 345/138 transformer at Tulsa North 345 kV substation with a summer emergency rating of 675 MVA. | 2024 ITP | Excluded | 2029-03-01
220804 | 170389 | Line - Cherokee Data Center East 138 kV - Tulsa North 138 kV Rebuild | Cherokee Data Center East - Tulsa North 138 kV Ckt 1 Rebuild | Rebuild 4.6-mile Ckt 1 line from Tulsa North 138 kV substation to Cherokee Data Center East 138 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 300 MVA. | 2024 ITP | Excluded | 2027-10-01
220804 | 170390 | Line - Cherokee Data Center East 138 kV - Tulsa North 138 kV Rebuild | Cherokee Data Center East 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Cherokee Data Center East 138 kV substation to support the line from Cherokee Data Center East 138 kV substation to Tulsa North 138 kV substation with a summer emergency rating of 300 MVA. | 2024 ITP | Excluded | 2027-10-01
220804 | 170405 | Line - Cherokee Data Center East 138 kV - Tulsa North 138 kV Rebuild | Tulsa North 138 kV Ckt 1 Terminal Upgrade #3 | Install any necessary terminal equipment at Tulsa North 138 kV substation to support the line from Tulsa North 138 kV substation to Cherokee Data Center East 138 kV substation with a summer emergency rating of 300 MVA. | 2024 ITP | Excluded | 2027-10-01
210611 | 112307 | Sub - Oklaunion 345 kV Capacitive Reactive Power Support | Oklaunion 345 kV Capacitive Reactive Power Support | Install +200Mvar Capacitor Bank(s) at the Oklaunion 345kV substation. | DISIS-2016-002 | Exclude | 2026-05-15
220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1-345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation. | DISIS-2016-002 | Exclude | 2026-12-31
TBD | TBD | Adora - Adora Tap 69 kV Rebuild Line | Adora - Adora Tap 69 kV Rebuild Line | Rebuild the Adora to Adora Tap 138 kV 1.4 mile line to a standard rating of 95 MVA | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Neosho S - Noel SW 161 kV Rebuild Line | Neosho S - Noel SW 161 kV Rebuild Line | Rebuild the Neosho S to Noel SW 161 kV 23.13 mile line to a standard rating of 557 MVA | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Grove 161/138 kV Upgrade Transformer | Grove 161/138 kV Upgrade Transformer | Upgrade 161/138 kV Ckt 1 Transformer at Substation Grove | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | TONNEC345 345/161 kV Upgrade Transformer | TONNEC345 345/161 kV Upgrade Transformer | Upgrade 345/161 kV Ckt 1 Transformer at Substation Tonnec | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Brown - Sbrown 138 kV Build Line | Brown - Sbrown 138 kV Build Line | Build a second 138 kV line from Brown to Sbrown with a standard rating of 286 MVA. | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Upgrade SPA Brown Substation | Upgrade SPA Brown Substation | Upgrade SPA Brown to add line 2 (Planning Level Estimates) | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Upgrade Brown Substation | Upgrade Brown Substation | Upgrade Brown Substation to Ring Bus Configuration | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Brown Substation Expansion | Brown Substation Expansion | Move COLBRTP4 138 kV from SBROWN4 to BROWN4. Add new 138 kV second circuit from BROWN4 to SBROWN4. Upgrade BROWN Substation to a breaker-and-a-half configuration. | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Rebuild NOELSW4 to ROSEVLY4 138 kV line 1 | Rebuild NOELSW4 to ROSEVLY4 138 kV line 1 | Rebuild the NOELSW4 to ROSEVALY4 138 kV line CKT1 (8.15 miles) to a minimum rating of 200 MVA | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Rebuild SOUTHRD4 to ROMNOSE4 138 kV line 1 | Rebuild SOUTHRD4 to ROMNOSE4 138 kV line 1 | Rebuild the SOUTHRD4 to ROMNOSE4 138 kV line CKT1 (17.28 miles) to a standard rating of 478 MVA | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Rebuild DEQUEEN2 to DEQUEEN 2 69 kV line 1 | Rebuild DEQUEEN2 to DEQUEEN 2 69 kV line 1 | Rebuild the DEQUEEN2 to DEQUEEN 2 69 kV line CKT1 (3.25 miles) to a minimum rating of 51 MVA | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Upgrade Terminal Equipment at ROSEHIL and G15052_T | Replace Switches at ROSEHIL and G15052_T to achieve a minimum rating of 1806 MVA | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Rebuild SW5th4 to CLASSEN4 138 kV line 1 | Rebuild SW5th4 to CLASSEN4 138 kV line 1 | Rebuild the SW5TH4 to CLASSEN4 138 kV line CKT1 (3.43 miles) to a standard rating of 478 MVA | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Reconfigure Little City to Brown 138 kV Line | Reconfigure Little City to Brown 138 kV Line | Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation | DISIS-2021-001 | Exclude | 36 Months
TBD | TBD | Catoosa to Catsag 138 kV Equipment Upgrade | Catoosa to Catsag 138 kV Equipment Upgrade | Upgrade terminal equipment at Catoosa for Catoosa to Catsag 138 kV line | DISIS-2020-001 | Exclude | 36 Months
TBD | TBD | Replace Snyder 138-69 kV Transformer | Replace Snyder 138-69 kV Transformer | Replace Snyder 138-69 kV Transformer to a minimum of 90 MVA | DISIS-2020-001 | Exclude | 36 Months
TBD | TBD | Sweetwater to Demarcation 230 kV Line Rebuild | Sweetwater to Demarcation 230 kV Line Rebuild | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | DISIS-2018-002 & DISIS-2019-001 | Exclude | 36 Months
TBD | TBD | Wheeler to Demarcation 230 kV Line Rebuild | Wheeler to Demarcation 230 kV Line Rebuild | Rebuild the Wheeler to Demarcation 230 kV 13.92 mile Line to a minimum rating of 583 MVA | DISIS-2018-002 & DISIS-2019-001 | Exclude | 36 Months
TBD | 170510 | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1 | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1 | Rebuild the AEPW portion of the SWEETWT6 to WHEELER6 230 kV line CKT1 (5 miles) to a minimum rating of 459 MVA | DISIS-2018-002 / DISIS-2019-001 | Exclude | 36 Months
TBD | TBD | Delaware Tap to 36th&Lewis 138 kV Rebuild (DISIS-2018-001) | Delaware Tap to 36th&Lewis 138 kV Rebuild (DISIS-2018-001) | Rebuild the existing Delaware Tap to 36th&Lewis 138 kV 0.97 mile line with a minimum summer emergency rating of 305 MVA | DISIS-2018-001 | Exclude | 36 Months
TBD | TBD | N North Boston to GEN-2018-003-TAP 138 kV Rebuild (DISIS-2018-001) | N North Boston to GEN-2018-003-TAP 138 kV Rebuild (DISIS-2018-001) | Rebuild the existing N North Boston to GEN-2018-003-TAP 138 kV 1.73 mile line with a minimum summer emergency rating and winter emergency rating of 173/199 MVA | DISIS-2018-001 | Exclude | 36 Months
TBD | 158556 | Delaware Tap to T.S.E. 138 kV Rebuild (DISIS-2018-001) | Delaware Tap to T.S.E. 138 kV Rebuild (DISIS-2018-001) | Rebuild the existing Delaware Tap to T.S.E. 138 kV 2.09 mile line with a minimum summer emergency rating of 295 MVA | DISIS-2018-001 | Exclude | 36 Months
TBD | 159070 | Build Tolk to Potter County 345 kV Circuit 1 | Build Tolk to Potter County 345 kV Circuit 1 | Build approximately 115 miles of 345 kV from Tolk - Potter County with minimum normal/emergency rating of 1195 MVA | DISIS-2017-002 | Exclude | 36 Months
TBD | 156487 | Rocky Point Terminal Equipment Upgrade (DISIS-2017-002) | Rocky Point Terminal Equipment Upgrade (DISIS-2017-002) | Upgrade terminal equipment at Rocky Point for the Rocky Point to Sunnyside 138 kV line to achieve minimum summer/emergency rating of 270 MVA | DISIS-2017-002 | Exclude | 36 Months
TBD | TBD | Broken Arrow North Street Tap to Oneta 138 kV Rebuild (DISIS-2017-002) | Broken Arrow North Street Tap to Oneta 138 kV Rebuild (DISIS-2017-002) | Rebuild the existing Broken Arrow North Street Tap to Oneta 138kV 4.31 mile line to achieve a minimum summer/emergency rating of 335 MVA | DISIS-2017-002 | Exclude | 36 Months
TBD | TBD | Northwest Texarkana to Wilkes 345kV New Line Build (DISIS-2017-002) | Northwest Texarkana to Wilkes 345kV New Line Build (DISIS-2017-002) | Build a new 60 mile 345 kV line from Northwest Texarkana to Wilkes. | DISIS-2017-002 | Exclude | 36 Months
TBD | 156487 | Rocky Point Terminal Equipment Upgrade (DISIS-2017-002) | Rocky Point Terminal Equipment Upgrade (DISIS-2017-002) | Upgrade terminal equipment at Rocky Point for the Rocky Point to Sunnside 138 kV line to achieve minimum summer/emergency rating of 205 MVA (DISIS-2017-002) | DISIS-2017-002 | Exclude | 36 Months

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
04ALL | GEN-2022-098 LOSIS | ERIS | Non-Converged | None | 24SP, 27SP, 27WP | None | [7 empty] | None
04ALL | GEN-2022-098 LOSIS | ERIS | Thermal | None | 24SP, 27SP, 27WP | None | [7 empty] | None
04ALL | GEN-2022-098 LOSIS | ERIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00NR | GEN-2022-098 LOSIS | NRIS | Non-Converged | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00NR | GEN-2022-098 LOSIS | NRIS | Thermal | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 24SP, 27SP, 27WP | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | 776 | 776 | 117.05 | 119.31 |  |  |  | DIS2201_P2-Restudy_G00_NRIS_UPDATE_LONGWD 7_WILKES 7_345kV_CKT1_MODEL_CORRECTION
00NR | GEN-2022-098 LOSIS | NRIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
04ALL | GEN-2022-098 LOSIS | ERIS | Stability | Instability and non-dampening oscillations | 25S | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | [7 empty] | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04ALL | GEN-2022-098 LOSIS | ERIS | Stability | None | 25W | None | [7 empty] | None

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | GEN-2022-098 LOSIS | 00NR | 1 | 24SP | GEN-2022-098 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.0767 | 117.06 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | DIS2201_P2-Restudy_G00_NRIS_UPDATE_LONGWD 7_WILKES 7_345kV_CKT1_MODEL_CORRECTION
Thermal | GEN-2022-098 LOSIS | 00NR | 1 | 24SP | GEN-2022-098 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.0767 | 117.06 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | DIS2201_P2-Restudy_G00_NRIS_UPDATE_LONGWD 7_WILKES 7_345kV_CKT1_MODEL_CORRECTION
Thermal | GEN-2022-098 LOSIS | 00NR | 1 | 27SP | GEN-2022-098 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.07689 | 111.42 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | DIS2201_P2-Restudy_G00_NRIS_UPDATE_LONGWD 7_WILKES 7_345kV_CKT1_MODEL_CORRECTION
Thermal | GEN-2022-098 LOSIS | 00NR | 1 | 27SP | GEN-2022-098 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.07689 | 111.42 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | DIS2201_P2-Restudy_G00_NRIS_UPDATE_LONGWD 7_WILKES 7_345kV_CKT1_MODEL_CORRECTION
Thermal | GEN-2022-098 LOSIS | 00NR | 1 | 27WP | GEN-2022-098 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.07264 | 119.31 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: | TDF Impact | DIS2201_P2-Restudy_G00_NRIS_UPDATE_LONGWD 7_WILKES 7_345kV_CKT1_MODEL_CORRECTION
Thermal | GEN-2022-098 LOSIS | 00NR | 1 | 27WP | GEN-2022-098 | TO->FROM | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 776 | 776 | 0.07264 | 119.31 | P23:345:AEPW:WELSH CB 11990 NBTB:::: | TDF Impact | DIS2201_P2-Restudy_G00_NRIS_UPDATE_LONGWD 7_WILKES 7_345kV_CKT1_MODEL_CORRECTION
Non-Converged | GEN-2022-098 LOSIS | 04ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2022-098 LOSIS | 04ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2022-098 LOSIS | 04ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2022-098 LOSIS | 00NR | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2022-098 LOSIS | 00NR | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | GEN-2022-098 LOSIS | 00NR | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2022-098 LOSIS | 04ALL | 1 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2022-098 LOSIS | 04ALL | 1 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | GEN-2022-098 LOSIS | 04ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | GEN-2022-098 LOSIS | 04ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2022-098 LOSIS | 04ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2022-098 LOSIS | 04ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | GEN-2022-098 LOSIS | 00NR | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2022-098 LOSIS | 00NR | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | GEN-2022-098 LOSIS | 00NR | 2 | 27WP | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Voltage breakdown and angular instability following fault clearance causing the simulation to crash. The issue is also observed in the base case and is not impacted by the CQ units. Low post-fault voltage at GEN-2018-015 345 kV. | System adjustments at GEN-2018-015 resolved the low-voltage issue. Remove reclosing and reduce clearing time to 3 cycles. The clearing time is not impacted by the CQ units.
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on TUCO_INT 7 345.0 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 345.0 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Voltage breakdown and angular instability following fault clearance causing the simulation to crash. The PTDF of the CQ request is 5.4%. The issue is also observed in the base case and limiting the request to 0 MW does not resolve the issue. | Line - Beckham County - Potter -345 kV New Line (2024 ITP)
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on G17-151TAP 345.0 (762216) 345 kV Bus a. Apply fault at the G17-151TAP 345.0 (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP (762216) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on S BROWN4 138.00 (505602) 138 kV Bus a. Apply Fault at the S BROWN4 138.00 (505602) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUPELO 4 (505600) 138.0 kV to S BROWN4 (505602) 138.0 kV Transmission Circuit #1 b.2. S BROWN4 (505602) 138.0 kV to DENISON4 (505604) 138.0 kV Transmission Circuit #1 b.3. S BROWN4 (505602) 138.0 kV to BROWN 4 (515157) 138.0 kV Transmission Circuit #1 b.4. S BROWN4 (505602) 138.0 kV to BROWN 4 (515157) 138.0 kV Transmission Circuit #2 b.5. S BROWN4 (505602) 138.0 kV to COLBRTP4 (515159) 138.0 kV Transmission Circuit #1 b.6. S BROWN4 (505602) 138.0 kV to KIERSEY4 (520963) 138.0 kV Transmission Circuit #1 b.7. S BROWN4 (505602) 138.0 kV to RUSSETT4 (521044) 138.0 kV Transmission Circuit #1 b.8. S BROWN4 (505602) 138.0 kV to G22-104-TAP (769060) 138.0 kV Transmission Circuit #1 b.9. RUSSET-4 (515120) 138.0 kV to RUSSETT4 (521044) 138.0 kV Transmission Circuit #1 b.10. COLBRT-4 (515193) 138.0 kV to COLBERT4 (520860) 138.0 kV Transmission Circuit #1 b.11. FROGVIL4 (520918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GOLDENSW4 138.00 (521194) 138 kV Bus a. Apply Fault at the GOLDENSW4 138.00 (521194) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKN BW4 (505614) 138.0 kV to HOCHTWN4 (520943) 138.0 kV Transmission Circuit #1 b.2. CRAIGJT4 (510890) 138.0 kV to MTRIVER4 (521004) 138.0 kV Transmission Circuit #1 b.3. BROKNBW4 (520834) 138.0 kV to GOLDENSW4 (521194) 138.0 kV Transmission Circuit #1 b.4. HUGO PP4 (520948) 138.0 kV to VALLANT4 (521079) 138.0 kV Transmission Circuit #1 b.5. GOLDENSW4 (521194) 138.0 kV to DOMINJCT4 (521195) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HUGO PP4 138.00 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 138.00 (520948) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S BROWN4 (505602) 138.0 kV to G22-104-TAP (769060) 138.0 kV Transmission Circuit #1 b.2. ATOKA--4 (510887) 138.0 kV to LANE 4 (520968) 138.0 kV Transmission Circuit #1 b.3. SAWYER4 (520411) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 b.4. FROGVIL4 (520918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillatory response observed in the active power outputs of G22-143GEN1 unit. Rotor Angle Damping Requirements met. The issue was also observed in the base case, and the CQ unit was not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on GOLDENSW4 138.00 (521194) 138 kV Bus a. Apply Fault at the GOLDENSW4 138.00 (521194) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKNBW4 (520834) 138.0 kV to GOLDENSW4 (521194) 138.0 kV Transmission Circuit #1 b.2. HUGO PP4 (520948) 138.0 kV to HUGO1 (520947) 23.4 kV Two Winding #1 b.3. HUGO PP4 (520948) 138.0 kV to VALLANT4 (521079) 138.0 kV Transmission Circuit #1 b.4. GOLDENSW4 (521194) 138.0 kV to DOMINJCT4 (521195) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on IDABEL-4 138.00 (510886) 138 kV Bus a. Apply Fault at the IDABEL-4 138.00 (510886) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDABEL-4 (510886) 138.0 kV to B.BOWTP4 (510888) 138.0 kV Transmission Circuit #1 b.2. IDABEL-4 (510886) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HUGO---4 138.00 (510901) 138 kV Bus a. Apply Fault at the HUGO---4 138.00 (510901) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGO---4 (510901) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 b.2. HUGO4-1 (510859) 13.8 kV to HUGO---2 (510893) 69.0 kV to HUGO---4 (510901) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on WELSH3-1 18.000 (509406) 18 kV Bus a. Apply Fault at the WELSH3-1 18.000 (509406) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to LYDIA 7 (508298) 345.0 kV Transmission Circuit #1 b.2. LYDIA 7 (508298) 345.0 kV to WELSH 7 (508359) 345.0 kV Transmission Circuit #1 b.3. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.4. WELSH3-1 (509406) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on NWTXARK7 345.00 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 345.00 (508072) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to LYDIA 7 (508298) 345.0 kV Transmission Circuit #1 b.2. LYDIA 7 (508298) 345.0 kV to WELSH 7 (508359) 345.0 kV Transmission Circuit #1 b.3. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.4. NWTXARK4 (508071) 138.0 kV to NWTXARK7 (508072) 345.0 kV to NWTEX2-1 (508101) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NWTXARK7 345.00 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 345.00 (508072) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to LYDIA 7 (508298) 345.0 kV Transmission Circuit #1 b.2. LYDIA 7 (508298) 345.0 kV to WELSH 7 (508359) 345.0 kV Transmission Circuit #1 b.3. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.4. NWTXARK4 (508071) 138.0 kV to NWTXARK7 (508072) 345.0 kV to NWTEX1-1 (508100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT7 (510911) 345.0 kV to VALIANT4 (510918) 138.0 kV to VALN2-1 (510938) 13.8 kV Three Winding #2 b.2. VALIANT7 (510911) 345.0 kV to VALIANT4 (510918) 138.0 kV to VALN3-1 (510939) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-020-TAP (764520) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.2. VALIANT4 (510918) 138.0 kV to VALIANT7 (510911) 345.0 kV to VALN3-1 (510939) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.2. VALIANT7 (510911) 345.0 kV to VALIANT4 (510918) 138.0 kV to VALN2-1 (510938) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-020-TAP (764520) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.2. VALIANT7 (510911) 345.0 kV to HUGO 7 (521157) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LYDIA 7 345.00 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 345.00 (508298) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to LYDIA 7 (508298) 345.0 kV Transmission Circuit #1 b.2. LYDIA 7 (508298) 345.0 kV to WELSH 7 (508359) 345.0 kV Transmission Circuit #1 b.3. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.4. VALIANT7 (510911) 345.0 kV to HUGO 7 (521157) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LYDIA 7 345.00 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 345.00 (508298) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to LYDIA 7 (508298) 345.0 kV Transmission Circuit #1 b.2. LYDIA 7 (508298) 345.0 kV to WELSH 7 (508359) 345.0 kV Transmission Circuit #1 b.3. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.4. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.2. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.2. PITTSB-7 (510907) 345.0 kV to JOHNCO 7 (514809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to KIOWA 7 (510925) 345.0 kV Transmission Circuit #1 b.2. PITTSB-7 (510907) 345.0 kV to JOHNCO 7 (514809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to KIOWA 7 (510925) 345.0 kV Transmission Circuit #1 b.2. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on VALIANT4 138.00 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 138.00 (510918) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDABEL-4 (510886) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 b.2. VALIANT2 (510910) 69.0 kV to VALIANT4 (510918) 138.0 kV to VALN1-1 (510937) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on VALIANT4 138.00 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 138.00 (510918) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGO---4 (510901) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 b.2. VALIANT2 (510910) 69.0 kV to VALIANT4 (510918) 138.0 kV to VALN1-1 (510937) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low post-fault voltage at HUGO---4 138 kV. After the Contingency, there would be no reactive support near the HUGO substation to maintain the voltage. The same observation was made in the base case, and the CQ units were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on VALIANT4 138.00 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 138.00 (510918) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. V-WEYCO4 (510866) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 b.2. HUGO---4 (510901) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. V-WEYCO4 (510866) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 b.2. VALIANT7 (510911) 345.0 kV to VALIANT4 (510918) 138.0 kV to VALN3-1 (510939) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT4 (510918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 b.2. VALIANT7 (510911) 345.0 kV to VALIANT4 (510918) 138.0 kV to VALN3-1 (510939) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-171-TAP (760938) 345.0 kV to TERRYRD7 (511568) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to G20-074-TAP (764115) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on UNIROY 4 138.00 (515137) 138 kV Bus a. Apply Fault at the UNIROY 4 138.00 (515137) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to UNIROY 4 (515137) 138.0 kV Transmission Circuit #1 b.2. UNIROY 4 (515137) 138.0 kV to ARDWEST4 (515372) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on ROCKYPT2 69.000 (515163) 69 kV Bus a. Apply Fault at the ROCKYPT2 69.000 (515163) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROCKYPT2 (515163) 69.0 kV to SCMMRCT2 (515420) 69.0 kV Transmission Circuit #1 b.2. ROCKYPT2 (515163) 69.0 kV to ROCKYPT4 (515164) 138.0 kV to ROCKYPT1 (515754) 13.2 kV Three Winding #1 b.5. ROCKYPT2 (515163) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on C-RIVER7 345.00 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 345.00 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit #1 b.2. C-RIVER4 (510946) 138.0 kV to C-RIVER7 (515422) 345.0 kV to C-RIVER1 (510947) 13.8 kV Three Winding #1 b.3. C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV to C-RIVER4 (510946) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on C-RIVER7 345.00 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 345.00 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIREWHL-TAP (588839) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit #1 b.2. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CARTRCO4 138.00 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 138.00 (515561) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RATLIFF4 (515129) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.2. POOLVIL4 (515130) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CARTRCO4 138.00 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 138.00 (515561) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RATLIFF4 (515129) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.2. CARTRCO4 (515561) 138.0 kV to ORIGINW4 (515563) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CARTRCO4 138.00 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 138.00 (515561) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.2. CARTRCO4 (515561) 138.0 kV to ORIGINW4 (515563) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on CARTRCO4 138.00 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 138.00 (515561) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POOLVIL4 (515130) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.2. SUNNYSD4 (515135) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to JOHNCO 7 (514809) 345.0 kV Transmission Circuit #1 b.2. JOHNCO 7 (514809) 345.0 kV to DMNDSPG7 (516006) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNCO 7 (514809) 345.0 kV to G21-016-TAP (765451) 345.0 kV Transmission Circuit #1 b.2. JOHNCO 7 (514809) 345.0 kV to DMNDSPG7 (516006) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RATLIFF4 138.00 (515129) 138 kV Bus a. Apply Fault at the RATLIFF4 138.00 (515129) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WLDHRST2 (515127) 69.0 kV to RATLIFF2 (515128) 69.0 kV Transmission Circuit #1 b.2. RATLIFF4 (515129) 138.0 kV to PRARPNT4 (515134) 138.0 kV Transmission Circuit #1 b.3. RATLIFF4 (515129) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.4. RATLIFF2 (515128) 69.0 kV to RATLIFF4 (515129) 138.0 kV to RATLIFF1 (515752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on ROCKYPT4 138.00 (515164) 138 kV Bus a. Apply Fault at the ROCKYPT4 138.00 (515164) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to ROCKYPT4 (515164) 138.0 kV Transmission Circuit #1 b.2. MRIETA 2 (515160) 138.0 kV to ROCKYPT4 (515164) 138.0 kV Transmission Circuit #1 b.3. ROCKYPT2 (515163) 69.0 kV to SCMMRCT2 (515420) 69.0 kV Transmission Circuit #1 b.4. ROCKYPT4 (515164) 138.0 kV to SPRNDAL4 (515172) 138.0 kV Transmission Circuit #1 b.5. ROCKYPT2 (515163) 69.0 kV to ROCKYPT4 (515164) 138.0 kV to ROCKYPT1 (515754) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. SEMINOL4 (515044) 138.0 kV to SEMINOL7 (515045) 345.0 kV to SEMINO21 (515757) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on SUNNYSD4 138.00 (515135) 138 kV Bus a. Apply Fault at the SUNNYSD4 138.00 (515135) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to UNIROY 4 (515137) 138.0 kV Transmission Circuit #1 b.2. SUNNYSD4 (515135) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on SUNNYSD4 138.00 (515135) 138 kV Bus a. Apply Fault at the SUNNYSD4 138.00 (515135) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to ROCKYPT4 (515164) 138.0 kV Transmission Circuit #1 b.2. SUNNYSD4 (515135) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SUNNYSD4 138.00 (515135) 138 kV Bus a. Apply Fault at the SUNNYSD4 138.00 (515135) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to LONEGRV4 (515144) 138.0 kV Transmission Circuit #1 b.2. SUNNYSD4 (515135) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.3. SUNNYSD4 (515135) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on NWTXARK7 345.00 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 345.00 (508072) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to NWTXARK4 (508071) 138.0 kV to NWTEX1-1 (508100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NWTXARK7 345.00 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 345.00 (508072) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to NWTXARK4 (508071) 138.0 kV to NWTEX1-1 (508100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on LYDIA 7 345.00 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 345.00 (508298) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LYDIA 7 345.00 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 345.00 (508298) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on LYDIA 7 345.00 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 345.00 (508298) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on IDABEL-4 138.00 (510886) 138 kV Bus a. Apply Fault at the IDABEL-4 138.00 (510886) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDABEL-4 (510886) 138.0 kV to B.BOWTP4 (510888) 138.0 kV Transmission Circuit #1 b.2. IDABEL-4 (510886) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT7 (510911) 345.0 kV to PITTSB-7 (510907) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT7 (510911) 345.0 kV to PITTSB-7 (510907) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT7 (510911) 345.0 kV to PITTSB-7 (510907) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT7 (510911) 345.0 kV to PITTSB-7 (510907) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on VALIANT4 138.00 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 138.00 (510918) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT4 (510918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on VALIANT4 138.00 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 138.00 (510918) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT4 (510918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNCO 7 (514809) 345.0 kV to JOHNCO 4 (514808) 138.0 kV to JOHNCO11 (514810) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNCO 7 (514809) 345.0 kV to JOHNCO 4 (514808) 138.0 kV to JOHNCO11 (514810) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNCO 7 (514809) 345.0 kV to JOHNCO 4 (514808) 138.0 kV to JOHNCO11 (514810) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNCO 7 (514809) 345.0 kV to JOHNCO 4 (514808) 138.0 kV to JOHNCO11 (514810) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on RATLIFF4 138.00 (515129) 138 kV Bus a. Apply Fault at the RATLIFF4 138.00 (515129) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RATLIFF4 (515129) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.2. RATLIFF4 (515129) 138.0 kV to PRARPNT4 (515134) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on POOLVIL4 138.00 (515130) 138 kV Bus a. Apply Fault at the POOLVIL4 138.00 (515130) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POOLVIL4 (515130) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.2. POOLVIL4 (515130) 138.0 kV to FOX 4 (515131) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on UNIROY 4 138.00 (515137) 138 kV Bus a. Apply Fault at the UNIROY 4 138.00 (515137) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIROY 4 (515137) 138.0 kV to SUNNYSD4 (515135) 138.0 kV Transmission Circuit #1 b.2. UNIROY 4 (515137) 138.0 kV to ARDWEST4 (515372) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on LONEGRV4 138.00 (515144) 138 kV Bus a. Apply Fault at the LONEGRV4 138.00 (515144) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONEGRV4 (515144) 138.0 kV to SUNNYSD4 (515135) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on LONEGRV4 138.00 (515144) 138 kV Bus a. Apply Fault at the LONEGRV4 138.00 (515144) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONEGRV4 (515144) 138.0 kV to SUNNYSD4 (515135) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on MRIETA 2 138.00 (515160) 138 kV Bus a. Apply Fault at the MRIETA 2 138.00 (515160) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MRIETA 2 (515160) 138.0 kV to ROCKYPT4 (515164) 138.0 kV Transmission Circuit #1 b.2. MRIETA 2 (515160) 138.0 kV to MARIETA4 (520988) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on ROCKYPT4 138.00 (515164) 138 kV Bus a. Apply Fault at the ROCKYPT4 138.00 (515164) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROCKYPT4 (515164) 138.0 kV to SUNNYSD4 (515135) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on ROCKYPT4 138.00 (515164) 138 kV Bus a. Apply Fault at the ROCKYPT4 138.00 (515164) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROCKYPT4 (515164) 138.0 kV to SUNNYSD4 (515135) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on CARTRCO4 138.00 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 138.00 (515561) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTRCO4 (515561) 138.0 kV to RATLIFF4 (515129) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on CARTRCO4 138.00 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 138.00 (515561) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTRCO4 (515561) 138.0 kV to RATLIFF4 (515129) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SAWYER4 138.00 (520411) 138 kV Bus a. Apply Fault at the SAWYER4 138.00 (520411) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAWYER4 (520411) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 b.2. SAWYER4 (520411) 138.0 kV to RATTAN 4 (521036) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on HUGO 7 345.00 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 345.00 (521157) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGOITC4 (520560) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 b.2. HUGOITC4 (520560) 138.0 kV to HUGO 7 (521157) 345.0 kV to HUGO TERTA (521189) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FROGVIL4 138.00 (520918) 138 kV Bus a. Apply Fault at the FROGVIL4 138.00 (520918) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FROGVIL4 (520918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 b.2. FROGVIL4 (520918) 138.0 kV to WSBNKTP4 (521098) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on HUGO PP4 138.00 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 138.00 (520948) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGO PP4 (520948) 138.0 kV to SAWYER4 (520411) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on HUGO PP4 138.00 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 138.00 (520948) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGO PP4 (520948) 138.0 kV to SAWYER4 (520411) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on HUGO 7 345.00 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 345.00 (521157) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGO 7 (521157) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on HUGO 7 345.00 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 345.00 (521157) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGO 7 (521157) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on G17-075-TAP 345.00 (560088) 345 kV Bus a. Apply Fault at the G17-075-TAP 345.00 (560088) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-075-TAP (560088) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on G17-075-TAP 345.00 (560088) 345 kV Bus a. Apply Fault at the G17-075-TAP 345.00 (560088) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-075-TAP (560088) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on GEN-2020-074345.00 (764105) 345 kV Bus a. Apply Fault at the GEN-2020-074345.00 (764105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-074 (764105) 345.0 kV to G20-074-TAP (764115) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-074 (764105) 345.0 kV to G20-074-XFM1 (764108) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on GEN-2021-016345.00 (765450) 345 kV Bus a. Apply Fault at the GEN-2021-016345.00 (765450) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-016 (765450) 345.0 kV to G21-016-TAP (765451) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-016 (765450) 345.0 kV to G21-016-XFM1 (765454) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on G17-075-TAP (560088) 345 kV Bus a. Apply Fault at the G17-075-TAP (560088) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-075-TAP (560088) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on HUGO 7 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 (521157) 345 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. HUGO 7 (521157) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. VALIANT7 (510911) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear Fault after 19 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear Fault after 20 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on G21-016-TAP (765451) 345 kV Bus a. Apply Fault at the G21-016-TAP (765451) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. G21-016-TAP (765451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on G20-074-TAP (764115) 345 kV Bus a. Apply Fault at the G20-074-TAP (764115) 345 kV Bus b. Clear Fault after 22 cycles and trip the following elements: b.1. G20-074-TAP (764115) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on JOHNCO 7 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear Fault after 23 cycles and trip the following elements: b.1. JOHNCO 7 (514809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear Fault after 24 cycles and trip the following elements: b.1. HUGO PP4 (520948) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear Fault after 25 cycles and trip the following elements: b.1. VALIANT4 (510918) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low post-fault voltage at HUGO---4 138 kV. After the Contingency, there would be no reactive support near the HUGO substation to maintain the voltage. The same observation was made in the base case, and the CQ units were not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on SUNNYSD4 (515135) 138 kV Bus a. Apply Fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear Fault after 26 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillatory response observed in the active power outputs of G22-143GEN1 unit. Rotor Angle Damping Requirements met. The issue was also observed in the base case, and the CQ unit was not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on CARTRCO4 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 (515561) 138 kV Bus b. Clear Fault after 27 cycles and trip the following elements: b.1. CARTRCO4 (515561) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on ROCKYPT4 (515164) 138 kV Bus a. Apply Fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. ROCKYPT4 (515164) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Breaker at From Bus #1 b.2. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Breaker at From Bus #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Breaker at To Bus #1 b.4. SUB M-161 (548814) 161.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Breaker at To Bus #1 b.2. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Breaker at From Bus #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Breaker at To Bus #1 b.4. SUB M-161 (548814) 161.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Breaker at To Bus #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Breaker at From Bus #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Breaker at To Bus #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Breaker at From Bus #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Breaker at From Bus #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Breaker at From Bus #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.3. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Breaker at From Bus #1 b.4. BLUMILS5 (543004) 161.0 kV to Trip Bus # b.5. BLUEMLS2 (543116) 69.0 kV to Trip Bus # b.6. BLUMILS_TER1 (543117) 12.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.3. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Breaker at To Bus #1 b.4. BLUMILS5 (543004) 161.0 kV to Trip Bus # b.5. BLUEMLS2 (543116) 69.0 kV to Trip Bus # b.6. BLUMILS_TER1 (543117) 12.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Breaker at To Bus #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Breaker at To Bus #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Breaker at To Bus #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Breaker at To Bus #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Trip Bus # b.4. RANDLPH5 (543027) 161.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on Hawthorn South (542973) 161 kV Bus a. Apply Fault at the Hawthorn South (542973) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on Hawthorn 161 kV (542973) 161 kV Bus a. Apply Fault at the Hawthorn 161 kV (542973) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@1 b.2. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@1 b.2. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on Northeast North (543666) 161 kV Bus a. Apply Fault at the Northeast North (543666) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NEASTN5 (543666) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to Trip Bus # b.4. NE CT14 (542971) 13.8 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NE CT17 (542983) 13.8 kV to Trip Bus # b.2. NE CT18 (542984) 13.8 kV to Trip Bus # b.3. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.4. NEASTS5 (542985) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 b.5. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 b.6. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillatory response observed in the active power outputs of GRECCTG_1 unit. Rotor Angle Damping Requirements met. The issue was also observed in the base case, and the CQ unit was not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEAUCRK5 (513570) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillatory response observed in the active power outputs of GRECCTG_1 unit. Rotor Angle Damping Requirements met. The issue was also observed in the base case, and the CQ unit was not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP5 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ADNA (345015) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on 8EL DORADO% 500.00 (337561) 500 kV Bus a. Apply Fault at the 8EL DORADO% 500.00 (337561) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. 8EL DORADO% (337561) 500.0 kV to 7EL DORADO (337562) 345.0 kV to 1EL DORADO2 (337565) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Two Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillatory response observed in the active power outputs of GRECCTG_1 unit. Rotor Angle Damping Requirements met. The issue was also observed in the base case, and the CQ unit was not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillatory response observed in the active power outputs of GRECCTG_1 unit. Rotor Angle Damping Requirements met. The issue was also observed in the base case, and the CQ unit was not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillatory response observed in the active power outputs of GRECCTG_1 unit. Rotor Angle Damping Requirements met. The issue was also observed in the base case, and the CQ unit was not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Oscillatory response observed in the active power outputs of GRECCTG_1 unit. Rotor Angle Damping Requirements met. The issue was also observed in the base case, and the CQ unit was not found to impact the issue. | No mitigation required.
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | G18-071-GEN1 trips on frequency protection settings. | Disabling frequency protection settings for G18-071-GEN1 prevents tripping. There are no stability constraints when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.2. FTSMITH7 (515302) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25S | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.3. # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_001 | 3 Phase fault on GOLDENSW4 138.00 (521194) 138 kV Bus a. Apply fault at the GOLDENSW4 138.00 (521194) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKNBW4 (520834) 138.0 kV to GOLDENSW4 (521194) 138.0 kV Transmission Circuit #1 b.2. HUGO PP4 (520948) 138.0 kV to VALLANT4 (521079) 138.0 kV Transmission Circuit #1 b.3. GOLDENSW4 (521194) 138.0 kV to DOMINJCT4 (521195) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_002 | 3 Phase fault on ATOKA--4 138.00 (510887) 138 kV Bus a. Apply fault at the ATOKA--4 138.00 (510887) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--4 (510887) 138.0 kV to LANE 4 (520968) 138.0 kV Transmission Circuit #1 b.2. SAWYER4 (520411) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_003 | 3 Phase fault on S BROWN4 138.00 (505602) 138 kV Bus a. Apply fault at the S BROWN4 138.00 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 (505602) 138.0 kV to G22-104-TAP (769060) 138.0 kV Transmission Circuit #1 b.2. FROGVIL4 (520918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_004 | 3 Phase fault on VALIANT4 138.00 (510918) 138 kV Bus a. Apply fault at the VALIANT4 138.00 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 (510918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_005 | 3 Phase fault on CANEYCK4 138.00 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 138.00 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 (515150) 138.0 kV to TEXOMAJ4 (521067) 138.0 kV Transmission Circuit #1 b.2. MRIETA 4 (520455) 138.0 kV to MARIETA4 (520988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_006 | 3 Phase fault on RUSSETT4 138.00 (521044) 138 kV Bus a. Apply fault at the RUSSETT4 138.00 (521044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 (505602) 138.0 kV to RUSSETT4 (521044) 138.0 kV Transmission Circuit #1 b.2. RUSSET-4 (515120) 138.0 kV to RUSSETT4 (521044) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_007 | 3 Phase fault on B.BOWTP4 138.00 (510888) 138 kV Bus a. Apply fault at the B.BOWTP4 138.00 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IDABEL-4 (510886) 138.0 kV to B.BOWTP4 (510888) 138.0 kV Transmission Circuit #1 b.2. B.BOWTP4 (510888) 138.0 kV to CRAIGJT4 (510890) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_008 | 3 Phase fault on HUGO---4 138.00 (510901) 138 kV Bus a. Apply fault at the HUGO---4 138.00 (510901) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO---4 (510901) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_009 | 3 Phase fault on IDABEL-4 138.00 (510886) 138 kV Bus a. Apply fault at the IDABEL-4 138.00 (510886) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IDABEL-4 (510886) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_010 | 3 Phase fault on V-WEYCO4 138.00 (510866) 138 kV Bus a. Apply fault at the V-WEYCO4 138.00 (510866) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. V-WEYCO4 (510866) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_011 | 3 Phase fault on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_012 | 3 Phase fault on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to JOHNCO 7 (514809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_013 | 3 Phase fault on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_014 | 3 Phase fault on VALIANT7 345.00 (510911) 345 kV Bus a. Apply fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 (510911) 345.0 kV to HUGO 7 (521157) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_015 | 3 Phase fault on LYDIA 7 345.00 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 345.00 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | G20-054-GEN1 trips on frequency protection settings. | Disabling frequency protection settings for G20-054-GEN1 prevents tripping. There are no stability constraints when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_016 | 3 Phase fault on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_017 | 3 Phase fault on KIPUMPT2 69.000 (510876) 69 kV Bus a. Apply fault at the KIPUMPT2 69.000 (510876) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KIPUMPT2 (510876) 69.0 kV to VALIANT2 (510910) 69.0 kV Transmission Circuit #1 b.2. KIPUMPT2 (510876) 69.0 kV to FTOWSON2 (510917) 69.0 kV Transmission Circuit #1 b.3. HUGO---2 (510893) 69.0 kV to SAWYER 2 (510920) 69.0 kV Transmission Circuit #1 b.4. FTOWSON2 (510917) 69.0 kV to SAWYER 2 (510920) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_018 | 3 Phase fault on WCITYTP2 69.000 (510870) 69 kV Bus a. Apply fault at the WCITYTP2 69.000 (510870) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GA PAC 2 (510868) 69.0 kV to WCITYTP2 (510870) 69.0 kV Transmission Circuit #1 b.2. WCITYTP2 (510870) 69.0 kV to VALIANT2 (510910) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_019 | 3 Phase fault on VALIANT7 345.00 (510911) 345 kV Bus a. Apply fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT4 (510918) 138.0 kV to VALIANT7 (510911) 345.0 kV to VALN3-1 (510939) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_020 | 3 Phase fault on VALIANT7 345.00 (510911) 345 kV Bus a. Apply fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT4 (510918) 138.0 kV to VALIANT7 (510911) 345.0 kV to VALN2-1 (510938) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_021 | 3 Phase fault on HUGO---4 138.00 (510901) 138 kV Bus a. Apply fault at the HUGO---4 138.00 (510901) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO---2 (510893) 69.0 kV to HUGO---4 (510901) 138.0 kV to HUGO4-1 (510859) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_022 | 3 Phase fault on VALIANT4 138.00 (510918) 138 kV Bus a. Apply fault at the VALIANT4 138.00 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT2 (510910) 69.0 kV to VALIANT4 (510918) 138.0 kV to VALN1-1 (510937) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_023 | 3 Phase fault on RATLIFF4 138.00 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 138.00 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 (515129) 138.0 kV to PRARPNT4 (515134) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_024 | 3 Phase fault on SXMLCKT4 138.00 (515122) 138 kV Bus a. Apply fault at the SXMLCKT4 138.00 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 (514808) 138.0 kV to SXMLCKT4 (515122) 138.0 kV Transmission Circuit #1 b.2. ARBUCKL4 (515117) 138.0 kV to MILLCKT4 (515121) 138.0 kV Transmission Circuit #1 b.3. MILLCKT4 (515121) 138.0 kV to SXMLCKT4 (515122) 138.0 kV Transmission Circuit #1 b.4. MILLCKT4 (515121) 138.0 kV to MILLCRK4 (515196) 138.0 kV Transmission Circuit #1 b.5. SXMLCKT4 (515122) 138.0 kV to HOWE 4 (521122) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_025 | 3 Phase fault on MADINDT4 138.00 (515149) 138 kV Bus a. Apply fault at the MADINDT4 138.00 (515149) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 (515120) 138.0 kV to GLASSES4 (515147) 138.0 kV Transmission Circuit #1 b.2. GLASSES4 (515147) 138.0 kV to MADINDT4 (515149) 138.0 kV Transmission Circuit #1 b.3. MADINDT4 (515149) 138.0 kV to CANEYCK4 (515150) 138.0 kV Transmission Circuit #1 b.4. MADINDT4 (515149) 138.0 kV to MADLIND4 (515158) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_026 | 3 Phase fault on SPRNDAL4 138.00 (515172) 138 kV Bus a. Apply fault at the SPRNDAL4 138.00 (515172) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 (515120) 138.0 kV to STIRLNG4 (515932) 138.0 kV Transmission Circuit #1 b.2. FNDTION4 (515162) 138.0 kV to SPRNDAL4 (515172) 138.0 kV Transmission Circuit #1 b.3. ROCKYPT4 (515164) 138.0 kV to SPRNDAL4 (515172) 138.0 kV Transmission Circuit #1 b.4. SPRNDAL4 (515172) 138.0 kV to DRPSPRG4 (515873) 138.0 kV Transmission Circuit #1 b.5. DRPSPRG4 (515873) 138.0 kV to STIRLNG4 (515932) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_027 | 3 Phase fault on POOLVIL4 138.00 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 138.00 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 (515130) 138.0 kV to FOX 4 (515131) 138.0 kV Transmission Circuit #1 b.2. POOLVIL4 (515130) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.3. FOX 4 (515131) 138.0 kV to DUNDEE 4 (515132) 138.0 kV Transmission Circuit #1 b.4. DUNDEE 4 (515132) 138.0 kV to HLTNTAP4 (515141) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_028 | 3 Phase fault on SUNNYSD4 138.00 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 138.00 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 (515135) 138.0 kV to UNIROY 4 (515137) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_029 | 3 Phase fault on CHEEKTP4 138.00 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 138.00 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 (515135) 138.0 kV to LONEGRV4 (515144) 138.0 kV Transmission Circuit #1 b.2. HLTNTAP4 (515141) 138.0 kV to DILLARD4 (515142) 138.0 kV Transmission Circuit #1 b.3. DILLARD4 (515142) 138.0 kV to WOLFCRK4 (515143) 138.0 kV Transmission Circuit #1 b.4. WOLFCRK4 (515143) 138.0 kV to CHEEKTP4 (515415) 138.0 kV Transmission Circuit #1 b.5. LONEGRV4 (515144) 138.0 kV to CHEEKTP4 (515415) 138.0 kV Transmission Circuit #1 b.6. CHEEKTP4 (515415) 138.0 kV to CHEEK_4 (521125) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_030 | 3 Phase fault on SUNNYSD4 138.00 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 138.00 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 (515135) 138.0 kV to ROCKYPT4 (515164) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_031 | 3 Phase fault on CARTER 4 138.00 (515138) 138 kV Bus a. Apply fault at the CARTER 4 138.00 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIROY 4 (515137) 138.0 kV to ARDWEST4 (515372) 138.0 kV Transmission Circuit #1 b.2. CARTER 4 (515138) 138.0 kV to CHIKSAW4 (515171) 138.0 kV Transmission Circuit #1 b.3. CARTER 4 (515138) 138.0 kV to ARDWEST4 (515372) 138.0 kV Transmission Circuit #1 b.4. CARTER 4 (515138) 138.0 kV to HONEYCK4 (515643) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_032 | 3 Phase fault on CANEYCK4 138.00 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 138.00 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 (515150) 138.0 kV to LTLCITY4 (515151) 138.0 kV Transmission Circuit #1 b.2. LTLCITY4 (515151) 138.0 kV to BROWNTP4 (515152) 138.0 kV Transmission Circuit #1 b.3. BROWNTP4 (515152) 138.0 kV to BODLE 4 (515155) 138.0 kV Transmission Circuit #1 b.4. BROWNTP4 (515152) 138.0 kV to STRRDTP4 (515944) 138.0 kV Transmission Circuit #1 b.5. COLEMNT4 (515153) 138.0 kV to EXPLRPL4 (515154) 138.0 kV Transmission Circuit #1 b.6. COLEMNT4 (515153) 138.0 kV to STRRDTP4 (515944) 138.0 kV Transmission Circuit #1 b.7. BROWN 4 (515157) 138.0 kV to STRRDTP4 (515944) 138.0 kV Transmission Circuit #1 b.8. CANEYCK4 (515150) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_033 | 3 Phase fault on LEBANTP4 138.00 (520972) 138 kV Bus a. Apply fault at the LEBANTP4 138.00 (520972) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 (515150) 138.0 kV to TEXOMAJ4 (521067) 138.0 kV Transmission Circuit #1 b.2. MRIETA 4 (520455) 138.0 kV to ENVILLE4 (520511) 138.0 kV Transmission Circuit #1 b.3. LEBANON4 (520488) 138.0 kV to LEBANTP4 (520972) 138.0 kV Transmission Circuit #1 b.4. ENVILLE4 (520511) 138.0 kV to LEBANTP4 (520972) 138.0 kV Transmission Circuit #1 b.5. LEBANTP4 (520972) 138.0 kV to TEXOMAJ4 (521067) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_034 | 3 Phase fault on ROCKYPT2 69.000 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 69.000 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 (515163) 69.0 kV to SCMMRCT2 (515420) 69.0 kV Transmission Circuit #1 b.2. ARDMORE2 (515166) 69.0 kV to SCMMRCT2 (515420) 69.0 kV Transmission Circuit #1 b.3. ROCKYPT2 (515163) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_035 | 3 Phase fault on JOHNCO 4 138.00 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 138.00 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 (514808) 138.0 kV to RUSSET-4 (515120) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_036 | 3 Phase fault on JOHNCO 4 138.00 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 138.00 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 (514808) 138.0 kV to CANEYCK4 (515150) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_037 | 3 Phase fault on RATLIFF4 138.00 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 138.00 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 (515129) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_038 | 3 Phase fault on SUNNYSD4 138.00 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 138.00 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 (515135) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_039 | 3 Phase fault on ROCKYPT4 138.00 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 138.00 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 (515163) 69.0 kV to ROCKYPT4 (515164) 138.0 kV to ROCKYPT1 (515754) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_040 | 3 Phase fault on SUNNYSD4 138.00 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 138.00 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 (515135) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_041 | 3 Phase fault on POOLVIL4 138.00 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 138.00 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 (515130) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_042 | 3 Phase fault on RUSSET-4 138.00 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 138.00 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 (515120) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_043 | 3 Phase fault on RATLIFF4 138.00 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 138.00 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 (515129) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_044 | 3 Phase fault on VALIANT7 345.00 (510911) 345 kV Bus a. Apply fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 (510911) 345.0 kV to G20-020-TAP (764520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_045 | 3 Phase fault on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | RSHSPR-1-B trips on voltage protection settings. | Disabling voltage protection settings for RSHSPR-1-B prevents tripping. There are no stability constraints when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_046 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_047 | 3 Phase fault on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 (511568) 345.0 kV to G20-074-TAP (764115) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | RSHSPR-1-B trips on voltage protection settings. | Disabling voltage protection settings for RSHSPR-1-B prevents tripping. There are no stability constraints when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_048 | 3 Phase fault on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 (514809) 345.0 kV to G21-016-TAP (765451) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_049 | 3 Phase fault on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_050 | 3 Phase fault on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 (515136) 345.0 kV to G20-074-TAP (764115) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_051 | 3 Phase fault on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 (515136) 345.0 kV to G20-074-TAP (764115) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_052 | 3 Phase fault on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 (515136) 345.0 kV to G21-016-TAP (765451) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_053 | 3 Phase fault on MRIETA 2 138.00 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 138.00 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 (515160) 138.0 kV to ROCKYPT4 (515164) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_054 | 3 Phase fault on MRIETA 2 138.00 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 138.00 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 (515160) 138.0 kV to MARIETA4 (520988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_055 | 3 Phase fault on SAWYER4 138.00 (520411) 138 kV Bus a. Apply fault at the SAWYER4 138.00 (520411) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAWYER4 (520411) 138.0 kV to RATTAN 4 (521036) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_056 | 3 Phase fault on GARVIN4 138.00 (520419) 138 kV Bus a. Apply fault at the GARVIN4 138.00 (520419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARVIN4 (520419) 138.0 kV to IDABEL 4 (520953) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_057 | 3 Phase fault on GARVIN4 138.00 (520419) 138 kV Bus a. Apply fault at the GARVIN4 138.00 (520419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARVIN4 (520419) 138.0 kV to VALLANT4 (521079) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_058 | 3 Phase fault on WSTBANK4 138.00 (520497) 138 kV Bus a. Apply fault at the WSTBANK4 138.00 (520497) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTBANK4 (520497) 138.0 kV to WSBNKTP4 (521098) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_059 | 3 Phase fault on HUGOITC4 138.00 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 138.00 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 (520560) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_060 | 3 Phase fault on DARWIN 4 138.00 (520874) 138 kV Bus a. Apply fault at the DARWIN 4 138.00 (520874) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARWIN 4 (520874) 138.0 kV to RATTAN 4 (521036) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_061 | 3 Phase fault on FROGVIL4 138.00 (520918) 138 kV Bus a. Apply fault at the FROGVIL4 138.00 (520918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROGVIL4 (520918) 138.0 kV to WSBNKTP4 (521098) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_062 | 3 Phase fault on UNGER 4 138.00 (521077) 138 kV Bus a. Apply fault at the UNGER 4 138.00 (521077) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNGER 4 (521077) 138.0 kV to WSBNKTP4 (521098) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_063 | 3 Phase fault on HUGO 7 345.00 (521157) 345 kV Bus a. Apply fault at the HUGO 7 345.00 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 (521157) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_064 | 3 Phase fault on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 4 (514808) 138.0 kV to JOHNCO 7 (514809) 345.0 kV to JOHNCO11 (514810) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_065 | 3 Phase fault on RATLIFF4 138.00 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 138.00 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF2 (515128) 69.0 kV to RATLIFF4 (515129) 138.0 kV to RATLIFF1 (515752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_066 | 3 Phase fault on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNNYSD1 (515762) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_067 | 3 Phase fault on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 (515136) 345.0 kV to SUNNYSD4 (515135) 138.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_068 | 3 Phase fault on HUGO 7 345.00 (521157) 345 kV Bus a. Apply fault at the HUGO 7 345.00 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 (521157) 345.0 kV to HUGOITC4 (520560) 138.0 kV to HUGO TERTA (521189) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_069 | 3 Phase fault on V-WEYCO4 138.00 (510866) 138 kV Bus a. Apply fault at the V-WEYCO4 138.00 (510866) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. V-WEYCO4 (510866) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_070 | 3 Phase fault on VALIANT2 69.000 (510910) 69 kV Bus a. Apply fault at the VALIANT2 69.000 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT2 (510910) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_071 | 3 Phase fault on WOLFCRK4 138.00 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 138.00 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 (515143) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_LOCAL_FAULT_072 | 3 Phase fault on LONEGRV4 138.00 (515144) 138 kV Bus a. Apply fault at the LONEGRV4 138.00 (515144) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONEGRV4 (515144) 138.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | CIRCUIT 1 FROM 602057 TO 667085 trips on apparent impedance protection settings. | Disabling protection settings for CIRCUIT 1 FROM 602057 TO 667085 prevents tripping. There are no stability constraints when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_001 | 3 Phase fault on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_002 | 3 Phase fault on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_003 | 3 Phase fault on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_004 | 3 Phase fault on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_005 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_006 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_007 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_008 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_009 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | CIRCUIT 1 FROM 602057 TO 667085 trips on apparent impedance protection settings. | Disabling protection settings for CIRCUIT 1 FROM 602057 TO 667085 prevents tripping. There are no stability constraints when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_010 | 3 Phase fault on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_011 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_012 | 3 Phase fault on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_013 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_014 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_015 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_016 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_017 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_018 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_019 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_020 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Voltage breakdown and angular instability following fault clearance causing the simulation to crash. The issue is also observed in the base case and is not impacted by the CQ units. | Remove reclosing and reduce clearing time to 5 cycles. The clearing time is not impacted by the CQ units.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_021 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_022 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_023 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_024 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_025 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_026 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to BECKHAM7 (516059) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_027 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_028 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Voltage breakdown and angular instability following fault clearance causing the simulation to crash. The issue is also observed in the base case and is not impacted by the CQ units. | Remove reclosing and reduce clearing time to 4 cycles per Transmission Owner indicated clearing time.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_029 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Voltage breakdown and angular instability following fault clearance causing the simulation to crash. The issue is also observed in the base case and is not impacted by the CQ units. | Remove reclosing and reduce clearing time to 4 cycles per Transmission Owner indicated clearing time.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_030 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_031 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_032 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_033 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_034 | 3 Phase fault on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_035 | 3 Phase fault on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_036 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_037 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to OKLAUN HVDC7 (511565) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | CIRCUIT 1 FROM 602057 TO 667085 trips on apparent impedance protection settings. | Disabling protection settings for CIRCUIT 1 FROM 602057 TO 667085 prevents tripping. There are no stability constraints when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_038 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_040 | 3 Phase fault on BORDER 7345.00 (515458) 345 kV Bus a. Apply fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 (515458) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_041 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_042 | 3 Phase fault on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Voltage breakdown and angular instability following fault clearance causing the simulation to crash. | Remove reclosing and reduce clearing time to 4.75 cycles per Transmission Owner indicated clearing time.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_043 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_044 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_045 | 3 Phase fault on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 (511456) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | CIRCUIT 1 FROM 602057 TO 667085 trips on apparent impedance protection settings. | Disabling protection settings for CIRCUIT 1 FROM 602057 TO 667085 prevents tripping. There are no stability constraints when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_046 | 3 Phase fault on TUCO_INT 7 345.0 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 345.0 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 (525832) 345.0 kV to G17-151TAP (762216) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Voltage breakdown and angular instability following fault clearance causing the simulation to crash. The issue is also observed in the base case and is not impacted by the CQ units. | Remove reclosing and reduce clearing time to 5 cycles. The clearing time is not impacted by the CQ units.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_047 | 3 Phase fault on G17-151TAP 345.0 (762216) 345 kV Bus a. Apply fault at the G17-151TAP 345.0 (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP (762216) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_048 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_049 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_050 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P1_REGIONAL_FAULT_051 | 3 Phase fault on BECKHAM7 345.00 (516059) 345 kV Bus a. Apply fault at the BECKHAM7 345.00 (516059) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BECKHAM7 (516059) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on S BROWN4 138.00 (505602) 138 kV Bus a. Apply Fault at the S BROWN4 138.00 (505602) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TUPELO 4 (505600) 138.0 kV to S BROWN4 (505602) 138.0 kV Transmission Circuit #1 b.2. S BROWN4 (505602) 138.0 kV to DENISON4 (505604) 138.0 kV Transmission Circuit #1 b.3. S BROWN4 (505602) 138.0 kV to BROWN 4 (515157) 138.0 kV Transmission Circuit #1 b.4. S BROWN4 (505602) 138.0 kV to BROWN 4 (515157) 138.0 kV Transmission Circuit #2 b.5. S BROWN4 (505602) 138.0 kV to COLBRTP4 (515159) 138.0 kV Transmission Circuit #1 b.6. S BROWN4 (505602) 138.0 kV to KIERSEY4 (520963) 138.0 kV Transmission Circuit #1 b.7. S BROWN4 (505602) 138.0 kV to RUSSETT4 (521044) 138.0 kV Transmission Circuit #1 b.8. S BROWN4 (505602) 138.0 kV to G22-104-TAP (769060) 138.0 kV Transmission Circuit #1 b.9. RUSSET-4 (515120) 138.0 kV to RUSSETT4 (521044) 138.0 kV Transmission Circuit #1 b.10. COLBRT-4 (515193) 138.0 kV to COLBERT4 (520860) 138.0 kV Transmission Circuit #1 b.11. FROGVIL4 (520918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on GOLDENSW4 138.00 (521194) 138 kV Bus a. Apply Fault at the GOLDENSW4 138.00 (521194) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKN BW4 (505614) 138.0 kV to HOCHTWN4 (520943) 138.0 kV Transmission Circuit #1 b.2. CRAIGJT4 (510890) 138.0 kV to MTRIVER4 (521004) 138.0 kV Transmission Circuit #1 b.3. BROKNBW4 (520834) 138.0 kV to GOLDENSW4 (521194) 138.0 kV Transmission Circuit #1 b.4. HUGO PP4 (520948) 138.0 kV to VALLANT4 (521079) 138.0 kV Transmission Circuit #1 b.5. GOLDENSW4 (521194) 138.0 kV to DOMINJCT4 (521195) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HUGO PP4 138.00 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 138.00 (520948) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S BROWN4 (505602) 138.0 kV to G22-104-TAP (769060) 138.0 kV Transmission Circuit #1 b.2. ATOKA--4 (510887) 138.0 kV to LANE 4 (520968) 138.0 kV Transmission Circuit #1 b.3. SAWYER4 (520411) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 b.4. FROGVIL4 (520918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on GOLDENSW4 138.00 (521194) 138 kV Bus a. Apply Fault at the GOLDENSW4 138.00 (521194) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKNBW4 (520834) 138.0 kV to GOLDENSW4 (521194) 138.0 kV Transmission Circuit #1 b.2. HUGO PP4 (520948) 138.0 kV to HUGO1 (520947) 23.4 kV Two Winding #1 b.3. HUGO PP4 (520948) 138.0 kV to VALLANT4 (521079) 138.0 kV Transmission Circuit #1 b.4. GOLDENSW4 (521194) 138.0 kV to DOMINJCT4 (521195) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on IDABEL-4 138.00 (510886) 138 kV Bus a. Apply Fault at the IDABEL-4 138.00 (510886) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDABEL-4 (510886) 138.0 kV to B.BOWTP4 (510888) 138.0 kV Transmission Circuit #1 b.2. IDABEL-4 (510886) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on HUGO---4 138.00 (510901) 138 kV Bus a. Apply Fault at the HUGO---4 138.00 (510901) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGO---4 (510901) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 b.2. HUGO4-1 (510859) 13.8 kV to HUGO---2 (510893) 69.0 kV to HUGO---4 (510901) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on WELSH3-1 18.000 (509406) 18 kV Bus a. Apply Fault at the WELSH3-1 18.000 (509406) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to LYDIA 7 (508298) 345.0 kV Transmission Circuit #1 b.2. LYDIA 7 (508298) 345.0 kV to WELSH 7 (508359) 345.0 kV Transmission Circuit #1 b.3. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.4. WELSH3-1 (509406) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on NWTXARK7 345.00 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 345.00 (508072) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to LYDIA 7 (508298) 345.0 kV Transmission Circuit #1 b.2. LYDIA 7 (508298) 345.0 kV to WELSH 7 (508359) 345.0 kV Transmission Circuit #1 b.3. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.4. NWTXARK4 (508071) 138.0 kV to NWTXARK7 (508072) 345.0 kV to NWTEX2-1 (508101) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NWTXARK7 345.00 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 345.00 (508072) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to LYDIA 7 (508298) 345.0 kV Transmission Circuit #1 b.2. LYDIA 7 (508298) 345.0 kV to WELSH 7 (508359) 345.0 kV Transmission Circuit #1 b.3. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.4. NWTXARK4 (508071) 138.0 kV to NWTXARK7 (508072) 345.0 kV to NWTEX1-1 (508100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT7 (510911) 345.0 kV to VALIANT4 (510918) 138.0 kV to VALN2-1 (510938) 13.8 kV Three Winding #2 b.2. VALIANT7 (510911) 345.0 kV to VALIANT4 (510918) 138.0 kV to VALN3-1 (510939) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-020-TAP (764520) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.2. VALIANT4 (510918) 138.0 kV to VALIANT7 (510911) 345.0 kV to VALN3-1 (510939) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.2. VALIANT7 (510911) 345.0 kV to VALIANT4 (510918) 138.0 kV to VALN2-1 (510938) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-020-TAP (764520) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.2. VALIANT7 (510911) 345.0 kV to HUGO 7 (521157) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LYDIA 7 345.00 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 345.00 (508298) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to LYDIA 7 (508298) 345.0 kV Transmission Circuit #1 b.2. LYDIA 7 (508298) 345.0 kV to WELSH 7 (508359) 345.0 kV Transmission Circuit #1 b.3. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.4. VALIANT7 (510911) 345.0 kV to HUGO 7 (521157) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on LYDIA 7 345.00 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 345.00 (508298) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to LYDIA 7 (508298) 345.0 kV Transmission Circuit #1 b.2. LYDIA 7 (508298) 345.0 kV to WELSH 7 (508359) 345.0 kV Transmission Circuit #1 b.3. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.4. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.2. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 b.2. PITTSB-7 (510907) 345.0 kV to JOHNCO 7 (514809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to KIOWA 7 (510925) 345.0 kV Transmission Circuit #1 b.2. PITTSB-7 (510907) 345.0 kV to JOHNCO 7 (514809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to KIOWA 7 (510925) 345.0 kV Transmission Circuit #1 b.2. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on VALIANT4 138.00 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 138.00 (510918) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDABEL-4 (510886) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 b.2. VALIANT2 (510910) 69.0 kV to VALIANT4 (510918) 138.0 kV to VALN1-1 (510937) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on VALIANT4 138.00 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 138.00 (510918) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGO---4 (510901) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 b.2. VALIANT2 (510910) 69.0 kV to VALIANT4 (510918) 138.0 kV to VALN1-1 (510937) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on VALIANT4 138.00 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 138.00 (510918) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. V-WEYCO4 (510866) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 b.2. HUGO---4 (510901) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. V-WEYCO4 (510866) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 b.2. VALIANT7 (510911) 345.0 kV to VALIANT4 (510918) 138.0 kV to VALN3-1 (510939) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT4 (510918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 b.2. VALIANT7 (510911) 345.0 kV to VALIANT4 (510918) 138.0 kV to VALN3-1 (510939) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-171-TAP (760938) 345.0 kV to TERRYRD7 (511568) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to G20-074-TAP (764115) 345.0 kV Transmission Circuit #1 b.2. TERRYRD7 (511568) 345.0 kV to RUSHSPR7 (511571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on UNIROY 4 138.00 (515137) 138 kV Bus a. Apply Fault at the UNIROY 4 138.00 (515137) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to UNIROY 4 (515137) 138.0 kV Transmission Circuit #1 b.2. UNIROY 4 (515137) 138.0 kV to ARDWEST4 (515372) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on ROCKYPT2 69.000 (515163) 69 kV Bus a. Apply Fault at the ROCKYPT2 69.000 (515163) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROCKYPT2 (515163) 69.0 kV to SCMMRCT2 (515420) 69.0 kV Transmission Circuit #1 b.2. ROCKYPT2 (515163) 69.0 kV to ROCKYPT4 (515164) 138.0 kV to ROCKYPT1 (515754) 13.2 kV Three Winding #1 b.5. ROCKYPT2 (515163) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on C-RIVER7 345.00 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 345.00 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit #1 b.2. C-RIVER4 (510946) 138.0 kV to C-RIVER7 (515422) 345.0 kV to C-RIVER1 (510947) 13.8 kV Three Winding #1 b.3. C-RIVER1 (510947) 13.8 kV to C-RIVER7 (515422) 345.0 kV to C-RIVER4 (510946) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on C-RIVER7 345.00 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 345.00 (515422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIREWHL-TAP (588839) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit #1 b.2. PITTSB-7 (510907) 345.0 kV to C-RIVER7 (515422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CARTRCO4 138.00 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 138.00 (515561) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RATLIFF4 (515129) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.2. POOLVIL4 (515130) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on CARTRCO4 138.00 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 138.00 (515561) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RATLIFF4 (515129) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.2. CARTRCO4 (515561) 138.0 kV to ORIGINW4 (515563) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CARTRCO4 138.00 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 138.00 (515561) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.2. CARTRCO4 (515561) 138.0 kV to ORIGINW4 (515563) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on CARTRCO4 138.00 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 138.00 (515561) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POOLVIL4 (515130) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.2. SUNNYSD4 (515135) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to JOHNCO 7 (514809) 345.0 kV Transmission Circuit #1 b.2. JOHNCO 7 (514809) 345.0 kV to DMNDSPG7 (516006) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNCO 7 (514809) 345.0 kV to G21-016-TAP (765451) 345.0 kV Transmission Circuit #1 b.2. JOHNCO 7 (514809) 345.0 kV to DMNDSPG7 (516006) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on RATLIFF4 138.00 (515129) 138 kV Bus a. Apply Fault at the RATLIFF4 138.00 (515129) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WLDHRST2 (515127) 69.0 kV to RATLIFF2 (515128) 69.0 kV Transmission Circuit #1 b.2. RATLIFF4 (515129) 138.0 kV to PRARPNT4 (515134) 138.0 kV Transmission Circuit #1 b.3. RATLIFF4 (515129) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.4. RATLIFF2 (515128) 69.0 kV to RATLIFF4 (515129) 138.0 kV to RATLIFF1 (515752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on ROCKYPT4 138.00 (515164) 138 kV Bus a. Apply Fault at the ROCKYPT4 138.00 (515164) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to ROCKYPT4 (515164) 138.0 kV Transmission Circuit #1 b.2. MRIETA 2 (515160) 138.0 kV to ROCKYPT4 (515164) 138.0 kV Transmission Circuit #1 b.3. ROCKYPT2 (515163) 69.0 kV to SCMMRCT2 (515420) 69.0 kV Transmission Circuit #1 b.4. ROCKYPT4 (515164) 138.0 kV to SPRNDAL4 (515172) 138.0 kV Transmission Circuit #1 b.5. ROCKYPT2 (515163) 69.0 kV to ROCKYPT4 (515164) 138.0 kV to ROCKYPT1 (515754) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SEMINOL7 345.00 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 345.00 (515045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to SEMINOL7 (515045) 345.0 kV Transmission Circuit #1 b.2. SEMINOL4 (515044) 138.0 kV to SEMINOL7 (515045) 345.0 kV to SEMINO21 (515757) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on SUNNYSD4 138.00 (515135) 138 kV Bus a. Apply Fault at the SUNNYSD4 138.00 (515135) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to UNIROY 4 (515137) 138.0 kV Transmission Circuit #1 b.2. SUNNYSD4 (515135) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on SUNNYSD4 138.00 (515135) 138 kV Bus a. Apply Fault at the SUNNYSD4 138.00 (515135) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to ROCKYPT4 (515164) 138.0 kV Transmission Circuit #1 b.2. SUNNYSD4 (515135) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on SUNNYSD4 138.00 (515135) 138 kV Bus a. Apply Fault at the SUNNYSD4 138.00 (515135) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to LONEGRV4 (515144) 138.0 kV Transmission Circuit #1 b.2. SUNNYSD4 (515135) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.3. SUNNYSD4 (515135) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on NWTXARK7 345.00 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 345.00 (508072) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to NWTXARK4 (508071) 138.0 kV to NWTEX1-1 (508100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on NWTXARK7 345.00 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 345.00 (508072) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWTXARK7 (508072) 345.0 kV to NWTXARK4 (508071) 138.0 kV to NWTEX1-1 (508100) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on LYDIA 7 345.00 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 345.00 (508298) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on LYDIA 7 345.00 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 345.00 (508298) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on LYDIA 7 345.00 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 345.00 (508298) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYDIA 7 (508298) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on IDABEL-4 138.00 (510886) 138 kV Bus a. Apply Fault at the IDABEL-4 138.00 (510886) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDABEL-4 (510886) 138.0 kV to B.BOWTP4 (510888) 138.0 kV Transmission Circuit #1 b.2. IDABEL-4 (510886) 138.0 kV to VALIANT4 (510918) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on PITTSB-7 345.00 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 345.00 (510907) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to VALIANT7 (510911) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT7 (510911) 345.0 kV to PITTSB-7 (510907) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT7 (510911) 345.0 kV to PITTSB-7 (510907) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT7 (510911) 345.0 kV to PITTSB-7 (510907) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on VALIANT7 345.00 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 345.00 (510911) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT7 (510911) 345.0 kV to PITTSB-7 (510907) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on VALIANT4 138.00 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 138.00 (510918) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT4 (510918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on VALIANT4 138.00 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 138.00 (510918) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALIANT4 (510918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on TERRYRD7 345.00 (511568) 345 kV Bus a. Apply Fault at the TERRYRD7 345.00 (511568) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRYRD7 (511568) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNCO 7 (514809) 345.0 kV to JOHNCO 4 (514808) 138.0 kV to JOHNCO11 (514810) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNCO 7 (514809) 345.0 kV to JOHNCO 4 (514808) 138.0 kV to JOHNCO11 (514810) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNCO 7 (514809) 345.0 kV to JOHNCO 4 (514808) 138.0 kV to JOHNCO11 (514810) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on JOHNCO 7 345.00 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 345.00 (514809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHNCO 7 (514809) 345.0 kV to JOHNCO 4 (514808) 138.0 kV to JOHNCO11 (514810) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on RATLIFF4 138.00 (515129) 138 kV Bus a. Apply Fault at the RATLIFF4 138.00 (515129) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RATLIFF4 (515129) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.2. RATLIFF4 (515129) 138.0 kV to PRARPNT4 (515134) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on POOLVIL4 138.00 (515130) 138 kV Bus a. Apply Fault at the POOLVIL4 138.00 (515130) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POOLVIL4 (515130) 138.0 kV to CARTRCO4 (515561) 138.0 kV Transmission Circuit #1 b.2. POOLVIL4 (515130) 138.0 kV to FOX 4 (515131) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to SUNNYSD7 (515136) 345.0 kV to SUNYSD 1 (515405) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on SUNNYSD7 345.00 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 345.00 (515136) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on UNIROY 4 138.00 (515137) 138 kV Bus a. Apply Fault at the UNIROY 4 138.00 (515137) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIROY 4 (515137) 138.0 kV to SUNNYSD4 (515135) 138.0 kV Transmission Circuit #1 b.2. UNIROY 4 (515137) 138.0 kV to ARDWEST4 (515372) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on LONEGRV4 138.00 (515144) 138 kV Bus a. Apply Fault at the LONEGRV4 138.00 (515144) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONEGRV4 (515144) 138.0 kV to SUNNYSD4 (515135) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on LONEGRV4 138.00 (515144) 138 kV Bus a. Apply Fault at the LONEGRV4 138.00 (515144) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONEGRV4 (515144) 138.0 kV to SUNNYSD4 (515135) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on MRIETA 2 138.00 (515160) 138 kV Bus a. Apply Fault at the MRIETA 2 138.00 (515160) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MRIETA 2 (515160) 138.0 kV to ROCKYPT4 (515164) 138.0 kV Transmission Circuit #1 b.2. MRIETA 2 (515160) 138.0 kV to MARIETA4 (520988) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on ROCKYPT4 138.00 (515164) 138 kV Bus a. Apply Fault at the ROCKYPT4 138.00 (515164) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROCKYPT4 (515164) 138.0 kV to SUNNYSD4 (515135) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on ROCKYPT4 138.00 (515164) 138 kV Bus a. Apply Fault at the ROCKYPT4 138.00 (515164) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROCKYPT4 (515164) 138.0 kV to SUNNYSD4 (515135) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on CARTRCO4 138.00 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 138.00 (515561) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTRCO4 (515561) 138.0 kV to RATLIFF4 (515129) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on CARTRCO4 138.00 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 138.00 (515561) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTRCO4 (515561) 138.0 kV to RATLIFF4 (515129) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SAWYER4 138.00 (520411) 138 kV Bus a. Apply Fault at the SAWYER4 138.00 (520411) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAWYER4 (520411) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 b.2. SAWYER4 (520411) 138.0 kV to RATTAN 4 (521036) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on HUGO 7 345.00 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 345.00 (521157) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGOITC4 (520560) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 b.2. HUGOITC4 (520560) 138.0 kV to HUGO 7 (521157) 345.0 kV to HUGO TERTA (521189) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FROGVIL4 138.00 (520918) 138 kV Bus a. Apply Fault at the FROGVIL4 138.00 (520918) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FROGVIL4 (520918) 138.0 kV to HUGO PP4 (520948) 138.0 kV Transmission Circuit #1 b.2. FROGVIL4 (520918) 138.0 kV to WSBNKTP4 (521098) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on HUGO PP4 138.00 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 138.00 (520948) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGO PP4 (520948) 138.0 kV to SAWYER4 (520411) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on HUGO PP4 138.00 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 138.00 (520948) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGO PP4 (520948) 138.0 kV to SAWYER4 (520411) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on HUGO 7 345.00 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 345.00 (521157) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGO 7 (521157) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on HUGO 7 345.00 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 345.00 (521157) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUGO 7 (521157) 345.0 kV to G17-075-TAP (560088) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on G17-075-TAP 345.00 (560088) 345 kV Bus a. Apply Fault at the G17-075-TAP 345.00 (560088) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-075-TAP (560088) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on G17-075-TAP 345.00 (560088) 345 kV Bus a. Apply Fault at the G17-075-TAP 345.00 (560088) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-075-TAP (560088) 345.0 kV to SUNNYSD7 (515136) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on GEN-2020-074345.00 (764105) 345 kV Bus a. Apply Fault at the GEN-2020-074345.00 (764105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-074 (764105) 345.0 kV to G20-074-TAP (764115) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-074 (764105) 345.0 kV to G20-074-XFM1 (764108) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on GEN-2021-016345.00 (765450) 345 kV Bus a. Apply Fault at the GEN-2021-016345.00 (765450) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2021-016 (765450) 345.0 kV to G21-016-TAP (765451) 345.0 kV Transmission Circuit #1 b.2. GEN-2021-016 (765450) 345.0 kV to G21-016-XFM1 (765454) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on G17-075-TAP (560088) 345 kV Bus a. Apply Fault at the G17-075-TAP (560088) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-075-TAP (560088) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on HUGO 7 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 (521157) 345 kV Bus b. Clear Fault after 17 cycles and trip the following elements: b.1. HUGO 7 (521157) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. VALIANT7 (510911) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear Fault after 19 cycles and trip the following elements: b.1. PITTSB-7 (510907) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear Fault after 20 cycles and trip the following elements: b.1. SUNNYSD7 (515136) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on G21-016-TAP (765451) 345 kV Bus a. Apply Fault at the G21-016-TAP (765451) 345 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. G21-016-TAP (765451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on G20-074-TAP (764115) 345 kV Bus a. Apply Fault at the G20-074-TAP (764115) 345 kV Bus b. Clear Fault after 22 cycles and trip the following elements: b.1. G20-074-TAP (764115) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on JOHNCO 7 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear Fault after 23 cycles and trip the following elements: b.1. JOHNCO 7 (514809) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear Fault after 24 cycles and trip the following elements: b.1. HUGO PP4 (520948) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear Fault after 25 cycles and trip the following elements: b.1. VALIANT4 (510918) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on SUNNYSD4 (515135) 138 kV Bus a. Apply Fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear Fault after 26 cycles and trip the following elements: b.1. SUNNYSD4 (515135) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on CARTRCO4 (515561) 138 kV Bus a. Apply Fault at the CARTRCO4 (515561) 138 kV Bus b. Clear Fault after 27 cycles and trip the following elements: b.1. CARTRCO4 (515561) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on ROCKYPT4 (515164) 138 kV Bus a. Apply Fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear Fault after 28 cycles and trip the following elements: b.1. ROCKYPT4 (515164) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Breaker at From Bus #1 b.2. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Breaker at From Bus #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Breaker at To Bus #1 b.4. SUB M-161 (548814) 161.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on SUB M-161 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 (548814) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. SUB M-161 (548814) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Breaker at To Bus #1 b.2. SUB M-161 (548814) 161.0 kV to SUB M (548815) 69.0 kV Breaker at From Bus #1 b.3. SUB M-161 (548814) 161.0 kV to HAWTHS5 (542973) 161.0 kV Breaker at To Bus #1 b.4. SUB M-161 (548814) 161.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Breaker at To Bus #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Breaker at From Bus #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Breaker at To Bus #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Breaker at From Bus #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Breaker at From Bus #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on BLUVLY-161 (548807) 161 kV Bus a. Apply Fault at the BLUVLY-161 (548807) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.2. BLUVLY-161 (548807) 161.0 kV to BLUVLY (548806) 69.0 kV Breaker at From Bus #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.3. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Breaker at From Bus #1 b.4. BLUMILS5 (543004) 161.0 kV to Trip Bus # b.5. BLUEMLS2 (543116) 69.0 kV to Trip Bus # b.6. BLUMILS_TER1 (543117) 12.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 5 cycles and trip the following elements: b.1. BLUVLY-161 (548807) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.2. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.3. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Breaker at To Bus #1 b.4. BLUMILS5 (543004) 161.0 kV to Trip Bus # b.5. BLUEMLS2 (543116) 69.0 kV to Trip Bus # b.6. BLUMILS_TER1 (543117) 12.5 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Breaker at To Bus #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Breaker at To Bus #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on ECKLES-161 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 (548808) 161 kV Bus b. Clear Fault after 18 cycles and trip the following elements: b.1. ECKLES-161 (548808) 161.0 kV to BLUMILS5 (543004) 161.0 kV Breaker at From Bus #1 b.2. ECKLES-161 (548808) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Breaker at To Bus #1 b.3. ECKLES-161 (548808) 161.0 kV to SIBLEYPL (541250) 161.0 kV Breaker at To Bus #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Trip Bus # b.4. RANDLPH5 (543027) 161.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on Hawthorn South (542973) 161 kV Bus a. Apply Fault at the Hawthorn South (542973) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. HAW G5 1 (542951) 22.0 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on Hawthorn 161 kV (542973) 161 kV Bus a. Apply Fault at the Hawthorn 161 kV (542973) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@1 b.2. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 11 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 21 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on Hawthorn North (543665) 161 kV Bus a. Apply Fault at the Hawthorn North (543665) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@1 b.2. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #@2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on Hawthorn 345 kV (542972) 345 kV Bus a. Apply Fault at the Hawthorn 345 kV (542972) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on Nashua 345 kV (542980) 345 kV Bus a. Apply Fault at the Nashua 345 kV (542980) 345 kV Bus b. Clear Fault after 4.75 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on Northeast North (543666) 161 kV Bus a. Apply Fault at the Northeast North (543666) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NEASTN5 (543666) 161.0 kV to LEVEE 5 (542976) 161.0 kV Transmission Circuit #1 b.2. NEASTN5 (543666) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to Trip Bus # b.4. NE CT14 (542971) 13.8 kV to Trip Bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on Northeast South (542985) 161 kV Bus a. Apply Fault at the Northeast South (542985) 161 kV Bus b. Clear Fault after 7.75 cycles and trip the following elements: b.1. NE CT17 (542983) 13.8 kV to Trip Bus # b.2. NE CT18 (542984) 13.8 kV to Trip Bus # b.3. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.4. NEASTS5 (542985) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 b.5. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 b.6. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on CROCKET7 345.00 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 345.00 (509241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 b.2. CROCKET4 (509240) 138.0 kV to CROCKET7 (509241) 345.0 kV to CROCK-B1 (509243) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. TENRUSK7 (508585) 345.0 kV to TENGEN 7 (508586) 345.0 kV Transmission Circuit #1 b.3. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on LEBROCG1 18.000 (506752) 18 kV Bus a. Apply Fault at the LEBROCG1 18.000 (506752) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG1 (506752) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on LEBROCG2 18.000 (506753) 18 kV Bus a. Apply Fault at the LEBROCG2 18.000 (506753) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to TENRUSK7 (508585) 345.0 kV Transmission Circuit #1 b.2. LEBROCG2 (506753) 18.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to DIANA 7 (508832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 4 (507759) 138.0 kV to SW SHV 7 (507760) 345.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.2. SW SHV 7 (507760) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. WILKES-1 (508826) 13.2 kV to WILKES 4 (508840) 138.0 kV to WILKES 7 (508841) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on WILKES 7 345.00 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 345.00 (508841) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WELSH 7 (508359) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 b.2. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINT2-1 (506920) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORAM 4 (507774) 138.0 kV to LONGWD 4 (508808) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 4 (508808) 138.0 kV to OAKPH 4 (508816) 138.0 kV Transmission Circuit #1 b.2. LONGWD 4 (508808) 138.0 kV to LONGWD 7 (508809) 345.0 kV to LONGW1-1 (508819) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to DEC392 5 (547484) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTRY 5 (504201) 161.0 kV to FLINTCR5 (506934) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to SILOAM 5 (506948) 161.0 kV Transmission Circuit #1 b.2. FLINT1-1 (506921) 13.8 kV to FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. L.E.S.-7 (511468) 345.0 kV to G17-171-TAP (760938) 345.0 kV Transmission Circuit #1 b.2. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on L.E.S.-7 345.00 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 345.00 (511468) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to L.E.S.-7 (511468) 345.0 kV Transmission Circuit #1 b.2. LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) 138.0 kV to L.E.S.-7 (511468) 345.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.5. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEAUCRK5 (513570) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GREC TAP5 (512865) 345.0 kV to GRECSTG_1 (512615) 21.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7LUTESVIL (344974) 345.0 kV to J1519 POI (45194) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply Fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7ADNA (345015) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.3. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on 8EL DORADO% 500.00 (337561) 500 kV Bus a. Apply Fault at the 8EL DORADO% 500.00 (337561) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 b.2. 7SAREPTA% (337376) 345.0 kV to LONGWD 7 (508809) 345.0 kV Transmission Circuit #1 b.3. 8EL DORADO% (337561) 500.0 kV to 7EL DORADO (337562) 345.0 kV to 1EL DORADO2 (337565) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 b.6. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on TUCO_INT 7345.00 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7345.00 (525832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 b.2. TUCO_TR1 1 (525824) 13.2 kV to TUCO_INT 7 (525832) 345.0 kV to TUCO_INT 6 (525830) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Two Winding #1 b.2. BORDER 7 (515458) 345.0 kV to TUCO_INT 7 (525832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.3. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on FTSMITH7 345.00 (515302) 345 kV Bus a. Apply Fault at the FTSMITH7 345.00 (515302) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHW5 (515301) 161.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH41 (515791) 13.8 kV Three Winding #4 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 8ANO% (337909) 500.0 kV to FTSMITH8 (515305) 500.0 kV Transmission Circuit #1 b.2. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #1 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on FTSMTHW5 161.00 (515301) 161 kV Bus a. Apply Fault at the FTSMTHW5 161.00 (515301) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMTHE5 (515300) 161.0 kV to FTSMTHW5 (515301) 161.0 kV Transmission Circuit #2 b.2. FTSMTHW5 (515301) 161.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH51 (515728) 13.8 kV Three Winding #5 b.5. FTSMTHW5 (515301) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to MUSKOG5G (515225) 18.0 kV Two Winding #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071-TAP (763069) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply Fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 b.2. 7WNWMADRID1A (301407) 345.0 kV to 7ESSEX (300038) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on 7SAREPTA% 345.00 (337376) 345 kV Bus a. Apply Fault at the 7SAREPTA% 345.00 (337376) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SAREPTA% (337376) 345.0 kV to 3SAREPTA! (337363) 115.0 kV Two Winding #1 b.2. 7SAREPTA% (337376) 345.0 kV to 7EL DORADO (337562) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on SW SHV 7 345.00 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 345.00 (507760) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV2-1 (507777) 13.8 kV Three Winding #2 b.2. SW SHV 7 (507760) 345.0 kV to SW SHV 4 (507759) 138.0 kV to SWSHV1-1 (507778) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on LEBROCK7 345.00 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 345.00 (508572) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #2 b.2. LEBROCK7 (508572) 345.0 kV to PIRKEY 7 (508563) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_093 | Single Phase Fault with Stuck Breaker on TENRUSK7 345.00 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 345.00 (508585) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TENRUSK7 (508585) 345.0 kV to CROCKET7 (509241) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_094 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_095 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_096 | Single Phase Fault with Stuck Breaker on LONGWD 7 345.00 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 345.00 (508809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LONGWD 7 (508809) 345.0 kV to WILKES 7 (508841) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_097 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_098 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to G22-176-TAP (770500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_099 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_100 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_101 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_102 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_103 | Single Phase Fault with Stuck Breaker on O.K.U.-7 345.00 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 345.00 (511456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. O.K.U.-7 (511456) 345.0 kV to G18-015-TAP (762467) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_104 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_105 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_106 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_107 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_108 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.2. MUSKOGE7 (515224) 345.0 kV to FTSMITH7 (515302) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_109 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_110 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BORDER 7 (515458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_112 | Single Phase Fault with Stuck Breaker on BORDER 7345.00 (515458) 345 kV Bus a. Apply Fault at the BORDER 7345.00 (515458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BORDER 7 (515458) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_113 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_114 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_115 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_117 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_118 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_119 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_120 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_121 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_122 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | G18-071-GEN1 trips on voltage protection settings. | Disabling voltage protection settings for G18-071-GEN1 prevents tripping. There are no stability constraints when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_123 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OPENSKY7 (515621) 345.0 kV to G15052_T (560053) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_124 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_125 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_126 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH7 (515302) 345.0 kV to FTSMITH8 (515305) 500.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.2. FTSMITH7 (515302) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | GEN-2022-098 | 25W | Transfer | GROUP4_P4_REGIONAL_FAULT_127 | Single Phase Fault with Stuck Breaker on FTSMITH8 500.00 (515305) 500 kV Bus a. Apply Fault at the FTSMITH8 500.00 (515305) 500 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSMITH8 (515305) 500.0 kV to 8ANO% (337909) 500.0 kV Transmission Circuit #1 b.2. FTSMITH8 (515305) 500.0 kV to FTSMITH7 (515302) 345.0 kV to FTSMTH11 (515726) 13.8 kV Three Winding #1 b.3. # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Study Name | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (kA) | Request In Service 25SP Fault Current 3-Phase (kA) | Change in Fault Current (kA) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 768941 | GEN-2022-098345.00 | 345 | 6.759 | 7.1093 | 0.3503
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 560088 | G17-075-TAP 345.00 | 345 | 7.2948 | 7.6438 | 0.349
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 589130 | GEN-2017-075345.00 | 345 | 7.2856 | 7.6337 | 0.3481
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515136 | SUNNYSD7 345.00 | 345 | 11.7672 | 11.9301 | 0.1629
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 765451 | G21-016-TAP 345.00 | 345 | 11.4764 | 11.6246 | 0.1482
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 765450 | GEN-2021-016345.00 | 345 | 11.1185 | 11.2575 | 0.139
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 764115 | G20-074-TAP 345.00 | 345 | 11.001 | 11.1221 | 0.1211
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 764105 | GEN-2020-074345.00 | 345 | 10.9944 | 11.1154 | 0.121
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515135 | SUNNYSD4 138.00 | 138 | 19.5357 | 19.6519 | 0.1162
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 521157 | HUGO 7 345.00 | 345 | 11.2953 | 11.3975 | 0.1022
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 520560 | HUGOITC4 138.00 | 138 | 22.1604 | 22.2412 | 0.0808
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510911 | VALIANT7 345.00 | 345 | 13.6895 | 13.7673 | 0.0778
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 520948 | HUGO PP4 138.00 | 138 | 22.4586 | 22.5355 | 0.0769
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 514809 | JOHNCO 7 345.00 | 345 | 11.0244 | 11.0909 | 0.0665
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515144 | LONEGRV4 138.00 | 138 | 13.8207 | 13.8766 | 0.0559
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 588670 | GEN-2017-023138.00 | 138 | 18.5514 | 18.604 | 0.0526
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 511568 | TERRYRD7 345.00 | 345 | 11.0158 | 11.0621 | 0.0463
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515415 | CHEEKTP4 138.00 | 138 | 12.4511 | 12.4957 | 0.0446
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515137 | UNIROY 4 138.00 | 138 | 13.1458 | 13.1884 | 0.0426
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 514808 | JOHNCO 4 138.00 | 138 | 15.7734 | 15.8145 | 0.0411
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515372 | ARDWEST4 138.00 | 138 | 12.9387 | 12.9789 | 0.0402
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510907 | PITTSB-7 345.00 | 345 | 14.8503 | 14.8844 | 0.0341
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515138 | CARTER 4 138.00 | 138 | 12.8965 | 12.9297 | 0.0332
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510925 | KIOWA 7 345.00 | 345 | 14.566 | 14.5988 | 0.0328
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510918 | VALIANT4 138.00 | 138 | 15.036 | 15.0687 | 0.0327
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 760938 | G17-171-TAP 345.00 | 345 | 12.21 | 12.2421 | 0.0321
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515164 | ROCKYPT4 138.00 | 138 | 12.0056 | 12.0373 | 0.0317
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 760939 | GEN-2017-171345.00 | 345 | 12.1352 | 12.1669 | 0.0317
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 516006 | DMNDSPG7 345.00 | 345 | 7.8472 | 7.8771 | 0.0299
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515162 | FNDTION4 138.00 | 138 | 12.0854 | 12.1135 | 0.0281
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515172 | SPRNDAL4 138.00 | 138 | 12.0135 | 12.0416 | 0.0281
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515143 | WOLFCRK4 138.00 | 138 | 9.9012 | 9.928 | 0.0268
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515873 | DRPSPRG4 138.00 | 138 | 11.1114 | 11.1351 | 0.0237
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 511468 | L.E.S.-7 345.00 | 345 | 15.3401 | 15.3635 | 0.0234
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 763318 | GEN-2018-115345.00 | 345 | 15.0237 | 15.0461 | 0.0224
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 521125 | CHEEK_4 138.00 | 138 | 8.6422 | 8.6637 | 0.0215
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515120 | RUSSET-4 138.00 | 138 | 11.5983 | 11.6196 | 0.0213
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 508298 | LYDIA 7 345.00 | 345 | 13.4964 | 13.5173 | 0.0209
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 508071 | NWTXARK4 138.00 | 138 | 25.7642 | 25.7824 | 0.0182
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515122 | SXMLCKT4 138.00 | 138 | 11.4189 | 11.4363 | 0.0174
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 764555 | GEN-2020-087345.00 | 345 | 15.038 | 15.0551 | 0.0171
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 520918 | FROGVIL4 138.00 | 138 | 10.6044 | 10.6212 | 0.0168
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 764075 | GEN-2020-054345.00 | 345 | 12.0819 | 12.0985 | 0.0166
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 508072 | NWTXARK7 345.00 | 345 | 13.917 | 13.9335 | 0.0165
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515044 | SEMINOL4 138.00 | 138 | 40.8303 | 40.8458 | 0.0155
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 520411 | SAWYER4 138.00 | 138 | 10.4755 | 10.4909 | 0.0154
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 511571 | RUSHSPR7 345.00 | 345 | 6.7601 | 6.7754 | 0.0153
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 764520 | G20-020-TAP 345.00 | 345 | 10.1338 | 10.1485 | 0.0147
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 764510 | GEN-2020-020345.00 | 345 | 10.1201 | 10.1348 | 0.0147
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515045 | SEMINOL7 345.00 | 345 | 28.5208 | 28.5354 | 0.0146
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 763131 | GEN-2018-082345.00 | 345 | 9.5379 | 9.5516 | 0.0137
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 762900 | GEN-2018-055345.00 | 345 | 6.424 | 6.4377 | 0.0137
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510866 | V-WEYCO4 138.00 | 138 | 9.5526 | 9.5659 | 0.0133
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515561 | CARTRCO4 138.00 | 138 | 9.3813 | 9.3943 | 0.013
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515150 | CANEYCK4 138.00 | 138 | 9.343 | 9.3559 | 0.0129
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 588710 | GEN-2017-027138.00 | 138 | 9.3294 | 9.3423 | 0.0129
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 769841 | GEN-2022-143138.00 | 138 | 9.2798 | 9.2926 | 0.0128
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515130 | POOLVIL4 138.00 | 138 | 9.1355 | 9.148 | 0.0125
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 5917 | SPPMAINBUS 345.00 | 345 | 21.6327 | 21.6439 | 0.0112
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 5919 | WELSHDC1 345.00 | 345 | 21.6327 | 21.6439 | 0.0112
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 5921 | SPP-CAP1 345.00 | 345 | 21.6327 | 21.6439 | 0.0112
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 5922 | SPP-CAP2 345.00 | 345 | 21.6327 | 21.6439 | 0.0112
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 5923 | SPP-CAP3 345.00 | 345 | 21.6327 | 21.6439 | 0.0112
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 5924 | SPP-REAC1 345.00 | 345 | 21.6327 | 21.6439 | 0.0112
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 508359 | WELSH 7 345.00 | 345 | 21.6327 | 21.6439 | 0.0112
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 765660 | GEN-2021-038345.00 | 345 | 20.1142 | 20.1239 | 0.0097
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515575 | ARBWIND4 138.00 | 138 | 8.6405 | 8.6502 | 0.0097
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 521079 | VALLANT4 138.00 | 138 | 8.5688 | 8.5782 | 0.0094
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515160 | MRIETA 2 138.00 | 138 | 7.4697 | 7.4789 | 0.0092
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515131 | FOX 4 138.00 | 138 | 7.2487 | 7.2575 | 0.0088
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515422 | C-RIVER7 345.00 | 345 | 11.38 | 11.3886 | 0.0086
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 520988 | MARIETA4 138.00 | 138 | 7.3833 | 7.3919 | 0.0086
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515420 | SCMMRCT2 69.000 | 69 | 9.1236 | 9.1319 | 0.0083
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 514934 | DRAPER 7 345.00 | 345 | 25.6543 | 25.6612 | 0.0069
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 760830 | GEN-2017-149345.00 | 345 | 3.7991 | 3.8057 | 0.0066
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515163 | ROCKYPT2 69.000 | 69 | 7.9337 | 7.9402 | 0.0065
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 521098 | WSBNKTP4 138.00 | 138 | 6.5632 | 6.5695 | 0.0063
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515129 | RATLIFF4 138.00 | 138 | 6.8968 | 6.9028 | 0.006
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 521036 | RATTAN 4 138.00 | 138 | 6.8055 | 6.8114 | 0.0059
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 507455 | TURK 7 345.00 | 345 | 9.1062 | 9.111 | 0.0048
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 508832 | DIANA 7 345.00 | 345 | 19.3733 | 19.3778 | 0.0045
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510886 | IDABEL-4 138.00 | 138 | 6.8042 | 6.8086 | 0.0044
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510946 | C-RIVER4 138.00 | 138 | 13.8725 | 13.8769 | 0.0044
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 765880 | GEN-2021-063138.00 | 138 | 8.5865 | 8.5908 | 0.0043
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 588838 | G17-092-SWYD345.00 | 345 | 18.5387 | 18.543 | 0.0043
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 588839 | FIREWHL-TAP 345.00 | 345 | 18.5387 | 18.543 | 0.0043
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 588810 | GEN-2017-040345.00 | 345 | 18.116 | 18.1201 | 0.0041
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 762592 | GEN-2018-024345.00 | 345 | 17.9789 | 17.9829 | 0.004
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510910 | VALIANT2 69.000 | 69 | 7.3485 | 7.3523 | 0.0038
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510888 | B.BOWTP4 138.00 | 138 | 7.1579 | 7.1615 | 0.0036
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 520419 | GARVIN4 138.00 | 138 | 5.9531 | 5.9564 | 0.0033
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515134 | PRARPNT4 138.00 | 138 | 5.5678 | 5.5708 | 0.003
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 768401 | GEN-2022-071138.00 | 138 | 11.5905 | 11.5935 | 0.003
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510870 | WCITYTP2 69.000 | 69 | 6.3886 | 6.3915 | 0.0029
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 589300 | GEN-2017-092345.00 | 345 | 15.0373 | 15.0401 | 0.0028
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515563 | ORIGINW4 138.00 | 138 | 6.1641 | 6.1669 | 0.0028
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510864 | B.BOW 4 138.00 | 138 | 6.153 | 6.1556 | 0.0026
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 771721 | GEN-2022-238138.00 | 138 | 18.3841 | 18.3864 | 0.0023
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 508841 | WILKES 7 345.00 | 345 | 15.5236 | 15.5259 | 0.0023
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 769201 | GEN-2022-111345.00 | 345 | 15.1716 | 15.1738 | 0.0022
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 515128 | RATLIFF2 69.000 | 69 | 5.1506 | 5.1525 | 0.0019
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510893 | HUGO---2 69.000 | 69 | 5.0877 | 5.0894 | 0.0017
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510876 | KIPUMPT2 69.000 | 69 | 4.8739 | 4.8755 | 0.0016
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 510901 | HUGO---4 138.00 | 138 | 3.4965 | 3.4981 | 0.0016
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 514908 | ARCADIA7 345.00 | 345 | 27.981 | 27.9826 | 0.0016
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 769761 | GEN-2022-139345.00 | 345 | 17.0079 | 17.009 | 0.0011
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 762845 | GEN-2018-050345.00 | 345 | 15.4832 | 15.4841 | 0.0009
GEN-2022-098 | GEN-2022-098 LOSIS | 04 CENTRAL | 760032 | GEN-2017-133345.00 | 345 | 5.0556 | 5.0557 | 0.0001