## Executive Summary
Executive Summary: DISIS-2023-001 Interconnection Facilities Study Report
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on January 29, 2023. The primary objective of the IFS is to identify necessary Transmission Owner Interconnection Facilities, Network Upgrades, other direct assigned upgrades, cost estimates, and associated upgrade lead times needed to grant the requested Interconnection Service. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 4.1 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process.
DISIS Manual Version 4.1
https://spp.org/media/2360/gi-manual-business-practice-7250-20250715.pdf
DISIS-2023-001 Facility Studies Postings
https://opsportal.spp.org/Studies/GenList?yearTypeId=221
This Facilities Study Report analyzes the impact of interconnecting new generation for total of:
9917.2 MW
The minimum cost of interconnecting all requests included in this Facilities Study Report is estimated at:
Total Interconnection Upgrade Cost: $604,205,690 Total Steady State/Stability Network Upgrade Cost: $182,874,000 Total Affected Systems Cost: $54,436,000
By: SPP Generator Interconnection Department
Published: 2/17/2026
Introduction
The interconnecting Transmission Owner applicable to the interconnection request, performed a detailed IFS at the request of SPP. SPP has determined that full Interconnection Service will be available after the assigned Transmission Owner Interconnection Facilities (TOIF), Non-Shared Network Upgrades, Shared Network Upgrades, Contingent Network Upgrades, and Affected System Upgrades that are required for full interconnection service are completed. The primary objective of the IFS is to identify necessary Transmission Owner Interconnection Facilities, Network Upgrades, other direct assigned upgrades, cost estimates, and associated upgrade lead times needed to grant the requested Interconnection Service.
Phase(s) of Interconnection Service
It is not expected that Interconnection Service will occur in phases. However, full Interconnection Service will not be available until all Interconnection Facilities and Network Upgrade(s) can be placed in service.
Compensation for Amounts Advanced for Network Upgrade(s)
FERC Order ER20-1687-000 eliminated the use of Attachment Z2 revenue crediting as an option for compensation. The Incremental Long Term Congestion Right (ILTCR) process will be the sole process to compensate upgrade sponsors as of July 1st, 2020.
Interconnection Customer Interconnection Facilities
The proposed Generating Facility will consist of generation equipment with a total nameplate capacity as specified in the Interconnection Request. The Interconnection Customer’s Interconnection Facilities, to be designed, procured, constructed, installed, maintained, and owned by the Interconnection Customer at its sole expense, are expected to include, but are not limited to, the following:
• Medium-voltage (e.g., 34.5 kV) underground cable collection circuits; • A medium-voltage to high-voltage transformation substation with associated switchgear; • One or more step-up transformers (e.g., high-voltage/medium-voltage MVA-rated transformers) to be owned and maintained by the Interconnection Customer at the Interconnection Customer’s substation; • A high-voltage transmission line, which may be overhead or underground, to connect the Interconnection Customer’s substation to the Point of Interconnection (“POI”) at the designated transmission bus at the existing Transmission Owner substation; • All transmission facilities required to connect the Interconnection Customer’s substation to the POI; • Equipment at the Interconnection Customer’s substation necessary to maintain composite power delivery at continuous rated power output at the high side of the generator substation, within a power factor range of 95% lagging to 95% leading, in accordance with applicable regulatory requirements (e.g., FERC Order 827 or its successor). The Interconnection Customer may utilize generation technology capabilities or other equipment to provide reactive power support under no- or reduced-generation conditions. Documentation and design specifications demonstrating compliance with these requirements shall be provided; and, • All necessary relay, protection, control, and communication systems required to protect the Interconnection Customer’s Interconnection Facilities and Generating Facilities, and to coordinate with the Transmission Owner’s corresponding systems.
Transmission Owner Interconnection Facilities and Non-Shared Network Upgrade(s)
To facilitate interconnection, the interconnecting Transmission Owner will perform work necessary for the acceptance of the Interconnection Customer’s Interconnection Facilities. The Assigned Upgrade Costs tab lists the Interconnection Customer’s estimated cost responsibility for Transmission Owner Interconnection Facilities (TOIF), Non-Shared Network Upgrade(s), Contingent Upgrade(s), and provides an estimated lead time for completion of construction. The estimated lead time begins when the Generator Interconnection Agreement has been fully executed. All studies have been conducted assuming that higher-queued Interconnection Request(s) and the associated Network Upgrade(s) will be placed into service. If higher-queued Interconnection Request(s) withdraw from the queue, suspend or terminate service, the Interconnection Customer’s share of costs may be revised. Restudies, conducted at the customer’s expense, will determine the Interconnection Customer’s revised allocation of Shared Network Upgrades.
Contingent Network Upgrade(s)
Certain Contingent Network Upgrades are currently not the cost responsibility of the Interconnection Customer but will be required for full Interconnection Service. Depending upon the status of higher- or equally-queued customers, the Interconnection Request’s in-service date is at risk of being delayed or Interconnection Service is at risk of being reduced until the in-service date of these Contingent Network Upgrades.
Affected System Upgrade(s)
To facilitate interconnection, the Affected System Transmission Owner will be required to perform the facilities study work as shown below necessary for the acceptance of the Interconnection Customer’s Interconnection Facilities. The Affected Systems tab displays the current impact study costs provided by either MISO or AECI as part of the Affected System Impact review. The Affected System facilities study could provide revised costs and will provide each Interconnection Customer’s allocation responsibilities for the upgrades.
Conclusion
After all Interconnection Facilities and Network Upgrades have been placed into service, the requested Interconnection Service can be granted. Full Interconnection Service will be delayed until the TOIF, Non-Shared NU, Shared NU, Contingent NU, Affected System Upgrades that are required for full interconnection service are completed. The Interconnection Customer’s estimated cost responsibility for full interconnection service is summarized in the table below. Use the following link for Quarterly Updates on upgrades from this report: https://spp.org/spp-documents-filings/?id=18641 A draft Generator Interconnection Agreement will be provided to the Interconnection Customer consistent with the final results of this IFS report. The Transmission Owner and Interconnection Customer will have 60 days to negotiate the terms of the GIA consistent with the SPP Open Access Transmission Tariff (OATT).

## Revision History
Revision History
Date | Author | Change Description
4607000% | SPP | Initial draft report issued.

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4591200% | Interconnection Costs

## Requests
GEN Number | Queue | Capacity | Location County & State | Host TO | Host TO Name | POI Name | POI kV Level | Generation Type | Service Type | COD | Number of Generators and Description | Number of Step-Up Transformers | Step-up Transformer MVA Ratings (ONAN/ONAF/ONAF) | Generator Lead Miles | Reactive Compensation
GEN-2023-015 | DIS-23-1 | 330 | Finney County, KS | SPS | Southwestern Public Service Company | Finney-Carpenter 345 KV line | 345 | Solar | ER/NR | 4626600% | Ninty (90) 3.78 MW SUNGROW SG4400UD-MV-US inverters | One | 238/317/396 | approximately 2.06 mile | -4.8
GEN-2023-033 | DIS-23-1 | 200 | Clay County, MO | WERE | Evergy | Liberty South 161 kV Substation | 161 | Battery/Storage | ER/NR | 4693500% | Seventy-six (76) 3.45 MW SMA SCS 3450 UP-US inverters | Two | 72/96/120 | approximately 0.1 mile | -0.1
GEN-2023-034 | DIS-23-1 | 130 | Sedgwick County, KS | WERE | Evergy | Clear Water - Waco 138 kV line | 138 | Solar | ER/NR | 4626600% | Thirty-five (35) 3.86 MW SUNGROW SG4400UD-MV-US inverters | One | 93/124/154 | approximately 1.6 mile | -12.5
GEN-2023-035 | DIS-23-1 | 200 | Grady County, OK | WFEC | Western Farmers Electric Cooperative | Cleveland - Amber Tap 138 kV Line | 138 | Solar | ER/NR | 4626600% | Fifty-five (55) 3.86 MW SUNGROW SG4400UD-MV-US inverters | One | 146/194/242 | approximately 0.96 mile | -6.48
GEN-2023-037 | DIS-23-1 | 200 | Wyandotte County, KS | KACY | Board of Public Utilities of Kansas City | Nearman 161 kV Substation | 161 | Battery/Storage | ER/NR | 4693500% | Seventy-six (76) 3.45 MW SMA SCS 3450 UP-US inverters | Two | 72/96/120 | approximately 0.1 mile | -0.2
GEN-2023-038 | DIS-23-1 | 200 | Coal County, OK | OGE | Oklahoma Gas & Electric | Lula 138 kV Substation | 138 | Solar | ER/NR | 4626600% | Fifty-four (54) 3.86 MW SUNGROW SG4400UD-MV-US inverters | One | 146/194/242 | approximately 0.1 mile | -13.08
GEN-2023-055 | DIS-23-1 | 100 | Mayes County, OK | GRDA | Grand River Dam Authority | Kerr Grove 161 kV | 161 | Battery/Storage | ER/NR | 4690400% | Thirty (30) 3.44 MW Power Electronics PCSM FP4200M inverters | One | 88/107/126 | approximately 0.12 mile | -0.09
GEN-2023-057 | DIS-23-1 | 150 | Pawnee County, OK | GRDA | Grand River Dam Authority | Pawnee Switch 138 kV | 138 | Battery/Storage | ER/NR | 4690400% | Forty-four (44) 3.44 MW Power Electronics PCSM FP4200M inverters | One | 130/158/186 | approximately 0.01 mile | -0.05
GEN-2023-059 | DIS-23-1 | 200 | Harrison & Panola County, TX | AEP | American Electric Power | Tap Rockhill to South Shreveport 138 kV line | 138 | Hybrid | ER/NR | 4723800% | Fifty (50) 3.86 MW SUNGROW SG4400UD-MV-UD inverters and ten (10) 20.286 MW gas turbines | Two | 144/192/240 and 138/180/225 | approximately 0.4 mile | -2.01
GEN-2023-061 | DIS-23-1 | 100 | Jasper County, MO | SWPA | Southwestern Power Administration | Carthage 161 kV Substation | 161 | Battery/Storage | ER/NR | 4748300% | Thirty-two (32) SMA SCS 3800 UP | One | 75/100/125 | approximately 0.1 mile | -0.2
GEN-2023-063 | DIS-23-1 | 135 | Rogers County, OK | AEP | American Electric Power | Catoosa - Owasso 88th 138 kV line | 138 | Hybrid | ER/NR | 4708800% | Forty-four (44) Sungrow SG3600UD-MV and thirty-six (36) Sungrow SC5000UD-MV inverters | One | 96/128/160 | approximately 0.26 mile | -0.98
GEN-2023-064 | DIS-23-1 | 200 | LeFlore County, OK | SWPA | Southwestern Power Administration | RS Kerr-Stigler 161 kV line | 161 | Hybrid | ER/NR | 4745300% | Sixty-five (65) Sungrow SG3600UD-MV and fifty-three (53) Sungrow SC5000UD-MV inverters | One | 142/190/237 | approximately 0.13 mile | -1.21
GEN-2023-069 | DIS-23-1 | 100 | Atoka County, OK | WFEC | Western Farmers Electric Cooperative | Tupelo - Atoka 138 kV Line | 138 | Hybrid | ER/NR | 4702600% | Thirty-five (35) Sungrow SG3600UD and Eleven (11) Sungrow SC5000UD inverters | One | 72/96/120 | approximately 0.04 mile | -1.15
GEN-2023-077 | DIS-23-1 | 255 | Cass County, NE | OPPD | Omaha Public Power District | Substation 3740 345 kV | 345 | Thermal | ER | 4678400% | One 303 MW 800H Gas Turbine | One | 235/315/390 | N/A | 0
GEN-2023-078 | DIS-23-1 | 255 | Cass County, NE | OPPD | Omaha Public Power District | Substation 3740 345 kV | 345 | Thermal | ER | 4678400% | One 303 MW 800H Gas Turbine | One | 235/315/390 | N/A | 0
GEN-2023-079 | DIS-23-1 | 272.7 | Cass County, NE | OPPD | Omaha Public Power District | Substation 3740 345 kV | 345 | Thermal | ER | 4824500% | One 303 MW 800H Gas Turbine | One | 235/315/390 | N/A | 0
GEN-2023-088 | DIS-23-1 | 117 | Okfuskee & Okmulgee County, OK | WFEC | Western Farmers Electric Cooperative | Pharaoh 138 kV Substation | 138 | Wind | ER/NR | 4711800% | twenty-six26 Vestas V163 4.5 MW wind turbines | One | 105/128/150 | approximately 0.09 mile | 0.24
GEN-2023-092 | DIS-23-1 | 125 | Choctaw County, OK | WFEC | Western Farmers Electric Cooperative | Unger - Frogville 138 kV line | 138 | Hybrid | ER/NR | 4702600% | Forty-three (43) Sungrow SG3600UD and thirteen (13) Sungrow SC5000UD inverters | One | 93/124/155 | approximately 0.04 mile | -1.5
GEN-2023-099 | DIS-23-1 | 300 | Jackson County, KS | WERE | Evergy | Jeffery Energy Center 345 kV Substation | 345 | Solar | ER | 4784800% | Eighty (80) 3.75 MW PE HEM FP4200M inverters | Two | 102/136/170 | approximately 6 mile | -1.6
GEN-2023-102 | DIS-23-1 | 475 | Woods County, OK | OGE | Oklahoma Gas & Electric | Degrasse 345 kV Substation | 345 | Hybrid | ER/NR | 4729900% | One Hunderd Sixty-one (161) Sungrow SG 3600 UD (Solar) and thirty-nine (39) Sungrow SC 5000 UD-MV (BESS) | Four | 93/124/155 | approximately 10 mile | -5.96
GEN-2023-104 | DIS-23-1 | 100 | Woods County, OK | WFEC | Western Farmers Electric Cooperative | Mooreland - Noel 138 kV Line | 138 | Hybrid | ER/NR | 4702600% | Thirty-five (35) Sungrow SG3600UD and Eleven (11) Sungrow SC5000UD inverters | One | 72/96/120 | approximately 0.04 mile | -1.15
GEN-2023-107 | DIS-23-1 | 300 | Finney & Kearny County, KS | SUNC | Sunflower Electric Power Corporation | Setab 345 kV | 345 | Wind | ER | 4784800% | Sixty-eight (68) Vestas v163 4.5 MW wind turbines | Two | 110/147/184 | approximately 15.51 mile | -81.5
GEN-2023-120 | DIS-23-1 | 130 | Swisher County, TX | SPS | Southwestern Public Service Company | Kress 115 kV Substation | 115 | Solar | ER | 4784800% | Thirty-five (35) PE HEM FP4200M inverters | One | 90/120/150 | approximately 0.01 mile | -2.91
GEN-2023-132 | DIS-23-1 | 150 | Craighead County, AR | SWPA | Southwestern Power Administration | Jonesboro - Independence 161 kV | 161 | Solar | ER/NR | 4711800% | Thirty-three (33) Sungrow SG 4400UD | One | 130/158/186 | approximately 0.04 mile | -1.28
GEN-2023-135 | DIS-23-1 | 52 | Bowie County, TX | AEP | American Electric Power | Lydia 345kV substation | 345 | Solar | ER/NR | 4638700% | Seventy-five (75) TMEIC, PVU-L0840GR inverters | One | 34/46/55 | approximately 0.95 mile | -4.9
GEN-2023-153 | DIS-23-1 | 120 | Perkins County, NE | Tri-State | Tri-State Generation and Transmission Association | Grant 115 kV Substation | 115 | Hybrid | ER/NR | 4699600% | Thirty-two (32) Power Electronics Freesun Gen3 4200 M inverters | Two | 337/450/562 | approximately 1.98 mile | -2.63
GEN-2023-161 | DIS-23-1 | 74.9 | Blaine County, OK | OGE | Oklahoma Gas & Electric | Roman Nose 138 kV Substation | 138 | Battery/Storage | ER/NR | 4666200% | Twenty-one (21) Power Electronics FP4200FM inverters | One | 85/115/115 | approximately 1.15 mile | -0.17
GEN-2023-170 | DIS-23-1 | 150 | Chariton County, MO | WERE | Evergy | Salisbury 161 kV Substation | 161 | Battery/Storage | ER | 4690500% | Forty-three (43) Power Electronics PCSK FP4200K inverters | One | 100/133/167 | approximately 0.20 mile | -0.7
GEN-2023-171 | DIS-23-1 | 150 | Jackson County, MO | INDN | Independence Power & Light | Sub M 161 kV Substation | 161 | Battery/Storage | ER/NR | 4690500% | Forty-three (43) Power Electronics PCSK FP4200K inverters | One | 100/133/167 | approximatley 0.01 mile | -0.7
GEN-2023-172 | DIS-23-1 | 200 | Kearny County, KS | SUNC | Sunflower Electric Power Corporation | Holcomb 345 kV | 345 | Wind | ER/NR | 4748300% | Forty-six (46) Vestas v163 4.5 MW wind turbines | Two | 125/138/150 | approximately 2.5 mile | -13.9
GEN-2023-173 | DIS-23-1 | 100 | Kearny County, KS | SUNC | Sunflower Electric Power Corporation | Holcomb 345 kV | 345 | Wind | ER/NR | 4748300% | Twenty-three (23) Vestas v163 4.5 wind turbines | Two | 125/138/150 | approximately 0.01 mile | -9.7
GEN-2023-177 | DIS-23-1 | 200 | Garvin County, OK | OGE | Oklahoma Gas & Electric | Paoli - Seminole 138 kV line tap | 138 | Solar | ER/NR | 4690500% | Fifty-one (51) Sungrow 4400UD-MV-US inverters | One | 72/96/120 | approxmately 0.05 mile | -0.28
GEN-2023-193 | DIS-23-1 | 175 | Harrison County, TX | AEP | American Electric Power | Pirkey - Whitney 138 kV Line | 138 | Hybrid | ER/NR | 4684300% | Fifty (50) Sungrow SG4400UD-MV inverters | One | 129/172/215 | approximately 0.1 mile | -1.66
GEN-2023-199 | DIS-23-1 | 250 | Dakota County, NE | NPPD | Nebraska Public Power District | Twin Church 230 kV Substation | 230 | Hybrid | ER/NR | 4647400% | Eighty-five (85) Sungrow SG3600UD inverters and sixty-two (62) Sungrow SC5000UD inverters | Two | 177/236/295 | approximately 0.02 mile | -2.98
GEN-2023-204 | DIS-23-1 | 914.6 | Morris County, TX | AEP | American Electric Power | Welsh-Lydia 345kV Line | 345 | Thermal | ER | 4708800% | One 480 MW combustion turbine | Two | 337/420/562 | approximately 0.2 mile | -0.04
GEN-2023-205 | DIS-23-1 | 180 | Hughes County, OK | AEP | American Electric Power | McAlester City - Weleetka 138 kV line | 138 | Solar | ER/NR | 4711800% | Forty-eight (48) Sungrow SG 4400UD inverters | One | 156/190/223 | approximately 0.04 mile | -1.6
GEN-2023-206 | DIS-23-1 | 50 | Sebastian County, AR | OGE | Oklahoma Gas & Electric | Battlefield BESS 161 kV Substation | 161 | Battery/Storage | ER/NR | 4748300% | Thirteen (13) Power Electronics FS4200M inverters | One | 141/188/235 | approximately 0.03 mile | -0.35
GEN-2023-210 | DIS-23-1 | 191 | Lincoln County, OK | WFEC | Western Farmers Electric Cooperative | Prague - Chernicky 138 kV Line | 138 | Solar | ER/NR | 4626600% | Fifty-two (52) Sungrow SG4400UD inverters | One | 138/184/229 | approximately 0.05 mile | -4.73
GEN-2023-220 | DIS-23-1 | 250 | Osage County, KS | WERE | Evergy | Emporia Energy Center - Swissvale 345 kV Line | 345 | Solar | ER/NR | 4745300% | Seventy (70) Power Electronics HEM FS4010M inverters | One | 167/225/281 | approximately 0.11 mile | -2.9
GEN-2023-221 | DIS-23-1 | 250 | Osage County, KS | WERE | Evergy | Emporia Energy Center - Swissvale 345 kV Line | 345 | Solar | ER/NR | 4745300% | Seventy (70) Power Electronics HEM FS4010M inverters | One | 167/225/281 | approximately 0.09 mile | -3
GEN-2023-222 | DIS-23-1 | 478 | Gage County, NE | NPPD | Nebraska Public Power District | New Beatrice Power Station 345 kV | 345 | Thermal | ER/NR | 4763500% | Two (2) 282.6 MVA GE generators | One | 180/240/300 | approximately 0.1 mile | -0.05
GEN-2023-223 | DIS-23-1 | 239 | Gage County, NE | NPPD | Nebraska Public Power District | New Beatrice Power Station 345 kV | 115 | Thermal | ER/NR | 4763500% | One (1) 282.2 MVA GE generator | One | 180/240/300 | approximately 0.1 mile | -0.1
GEN-2023-224 | DIS-23-1 | 478 | Lancaster County, NE | NPPD | Nebraska Public Power District | Olive Creek 345 kV Substation | 345 | Thermal | ER | 4727000% | Two (2) 282.6 MVA GE generators | One | 180/240/300 | approximately 0.47 mile | -0.75
GEN-2023-225 | DIS-23-1 | 217 | Lancaster County, NE | NPPD | Nebraska Public Power District | Olive Creek 345 kV Substation | 345 | Thermal | ER | 4727000% | Twelve (12) Wartsila 18V50DF inverters | Two | 90/120/150 | approximately 0.47 mile | -0.75
GEN-2023-229 | DIS-23-1 | 230 | Caddo County, OK | AEP | American Electric Power | Southwestern Power Station 138 kV Substation (SWS4) | 138 | Wind | ER/NR | 4723800% | Seventy-two (72) Power Electronics HEM FS4200M inverters | Two | 100/134/167 | approximately 9.26 mile | -19.91
GEN-2023-230 | DIS-23-1 | 150 | Bossier County, LA | AEP | American Electric Power | Red Pointe 138 kV Substation | 138 | Hybrid | ER/NR | 4707600% | Twenty-five (25)MVPS 4400-S2-US inverters | Two | 100/134/167 | approximately 1.9 mile | -1.23
GEN-2023-241 | DIS-23-1 | 93 | Franklin & Wood County, TX | AEP | American Electric Power | Winnsboro 138 kV Substation | 138 | Solar | ER | 4722700% | Twenty-five (25) Power Electronics HEM FS4200M inverters | One | 65/87/108 | approximately 1.14 mile | -1.09

## Assigned Upgrade Costs
Gen Number | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Upgrade Cost Responsibility | Allocated Cost | % Allocated | Total Upgrade Cost | ILTCR Eligibility | TO | Lead Time
ASGI-2023-001 | 170626 | NRIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | Contingent | 0 | 0% | 1301149472 | Ineligible | SPS | 36
ASGI-2023-001 | 170713 | NRIS | Tuco Int 345/230 kV Transformer Replacement | Contingent | Replace Tuco Int 345/230 kV Transformer to a minimum of 655 MVA | Contingent | 0 | 0% | 8302968 | Ineligible | SPS | 0
ASGI-2023-001 | 170593, 170608 | NRIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | OGE/SPS
ASGI-2023-001 | 170603 | NRIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | Contingent | 0 | 0% | 53295780 | Ineligible | SPS
ASGI-2023-001 | 170626 | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | Contingent | 0 | 0% | 1301149472 | Ineligible | SPS | 36
ASGI-2023-001 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 0
ASGI-2023-001 | 170593, 170608 | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | OGE/SPS
ASGI-2023-001 | 170594, 170609 | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | Contingent | 0 | 0% | 335411258 | Ineligible | OGE/SPS
GEN-2023-015 | 170626 | NRIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | Contingent | 0 | 0% | 1301149472 | Ineligible | SPS | 36
GEN-2023-015 | 170593, 170608 | NRIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | OGE/SPS
GEN-2023-015 | 170628 | NRIS | Build New Tolk to Potter County 345 kV Line | Contingent | Build a new 115.0 mile 345 kV circuit from Tolk to Potter with a standard rating of 1792 MVA | Contingent | 0 | 0% | 315122604 | Ineligible | SPS | 36
GEN-2023-015 | 170713 | NRIS | Tuco Int 345/230 kV Transformer Replacement | Contingent | Replace Tuco Int 345/230 kV Transformer to a minimum of 655 MVA | Contingent | 0 | 0% | 8302968 | Ineligible | SPS | 0
GEN-2023-015 | 143182 | NRIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 0
GEN-2023-015 | 171463 | ERIS | Switch Out Carpenter Line Reactor | Current Study | Switch out the Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line. Line reactor is not remote switchable. | Shared | 848067.0607 | 58.49% | 1450000 | Eligible | SPS
GEN-2023-015 | 171461 | ERIS | Build Second Red Willow 345/115 kV Transformer | Current Study | Build a second 345/115kV transformer at Red Willow | Shared | 9334906.4849 | 31.12% | 30000000 | Eligible | NPPD
GEN-2023-015 | 171464 | ERIS | Switch Out Finney Line Reactors | Current Study | Switch out the Finney (50 MVAR) - Carpenter (25 MVAR) 345kV line reactors. Line reactors are not remote switchable. | Shared | 848067.0607 | 58.49% | 1450000 | Eligible | SPS
GEN-2023-015 | 170665 | ERIS | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Contingent | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | Contingent |  | 0% | 102596000 | Ineligible | SEPC
GEN-2023-015 | 170651, 170655 | ERIS | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Contingent | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Contingent | 0 | 0% | 0 | Ineligible | ITCGP/NPPD
GEN-2023-015 | N/A | ERIS | Switch out Beaver to Badger Line Reactors | Current Study | Switch out Badger to Beaver 345 kV Double Circuit line reactors (150 MVAR total) | Shared | 0 | 58.49% | 0 | Eligible
GEN-2023-015 | 170628 | ERIS | Build New Tolk to Potter County 345 kV Line | Contingent | Build a new 115.0 mile 345 kV circuit from Tolk to Potter with a standard rating of 1792 MVA | Contingent | 0 | 0% | 315122604 | Ineligible | SPS | 36
GEN-2023-015 | 158701 | ERIS | Finney-Carpenter 345 KV line GEN-2023-015 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-015 (330MW/Solar), into Finney-Carpenter 345 KV line | Non-Shared | 42358867 | 100% | 42358867 | Ineligible | SPS | 48
GEN-2023-015 | 158700 | ERIS | Finney-Carpenter 345 KV line GEN-2023-015 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-015 (330MW/Solar), into Finney-Carpenter 345 KV line | Non-Shared | 3480128 | 100% | 3480128 | Ineligible | SPS | 48
GEN-2023-033 | 171463 | ERIS | Switch Out Carpenter Line Reactor | Current Study | Switch out the Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line. Line reactor is not remote switchable. | Shared | 18870.5878 | 1.301% | 1450000 | Eligible | SPS
GEN-2023-033 | 171464 | ERIS | Switch Out Finney Line Reactors | Current Study | Switch out the Finney (50 MVAR) - Carpenter (25 MVAR) 345kV line reactors. Line reactors are not remote switchable. | Shared | 18870.5878 | 1.301% | 1450000 | Eligible | SPS
GEN-2023-033 | N/A | ERIS | Switch out Beaver to Badger Line Reactors | Current Study | Switch out Badger to Beaver 345 kV Double Circuit line reactors (150 MVAR total) | Shared | 0 | 1.301% | 0 | Eligible
GEN-2023-033 | 170628 | ERIS | Build New Tolk to Potter County 345 kV Line | Contingent | Build a new 115.0 mile 345 kV circuit from Tolk to Potter with a standard rating of 1792 MVA | Contingent | 0 | 0% | 315122604 | Ineligible | SPS | 36
GEN-2023-033 | 158735 | ERIS | Liberty South 161 kV Substation GEN-2023-033 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-033 (200MW/Battery/Storage), into Liberty South 161 kV Substation | Non-Shared | 1265759 | 100% | 1265759 | Ineligible | Evergy | 36
GEN-2023-033 | 158734 | ERIS | Liberty South 161 kV Substation GEN-2023-033 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-033 (200MW/Battery/Storage), into Liberty South 161 kV Substation | Non-Shared | 940803 | 100% | 940803 | Ineligible | Evergy | 36
GEN-2023-034 | 170692 | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | Contingent |  | 0% | 96000000 | Ineligible | GMO
GEN-2023-034 | 158737 | ERIS | Clear Water - Waco 138 kV line GEN-2023-034 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-034 (130MW/Solar), into Clear Water - Waco 138 kV line | Non-Shared | 15091408 | 100% | 15091408 | Ineligible | Evergy | 36
GEN-2023-034 | 158736 | ERIS | Clear Water - Waco 138 kV line GEN-2023-034 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-034 (130MW/Solar), into Clear Water - Waco 138 kV line | Non-Shared | 928794 | 100% | 928794 | Ineligible | Evergy | 36
GEN-2023-035 | 82111, 82112, 82115 | ERIS | Line - Cogar - OU SW 138 kV | Contingent | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | Contingent | 0 | 0% | 37489652 | Ineligible | WFEC | 0
GEN-2023-035 | 170698 | NRIS | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Contingent | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | Contingent | 0 | 0% | 18105000 | Ineligible | OGE
GEN-2023-035 | 82111, 82112, 82115 | NRIS | Line - Cogar - OU SW 138 kV | Contingent | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | Contingent | 0 | 0% | 37489652 | Ineligible | WFEC | 0
GEN-2023-035 | 158739 | ERIS | Cleveland - Amber Tap 138 kV Line GEN-2023-035 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-035 (200MW/Solar), into Cleveland - Amber Tap 138 kV Line | Non-Shared | 6050000 | 100% | 6050000 | Ineligible | WFEC | 60
GEN-2023-035 | 158738 | ERIS | Cleveland - Amber Tap 138 kV Line GEN-2023-035 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-035 (200MW/Solar), into Cleveland - Amber Tap 138 kV Line | Non-Shared | 517000 | 100% | 517000 | Ineligible | WFEC | 60
GEN-2023-037 | 171463 | ERIS | Switch Out Carpenter Line Reactor | Current Study | Switch out the Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line. Line reactor is not remote switchable. | Shared | 18416.5806 | 1.27% | 1450000 | Eligible | SPS
GEN-2023-037 | 171464 | ERIS | Switch Out Finney Line Reactors | Current Study | Switch out the Finney (50 MVAR) - Carpenter (25 MVAR) 345kV line reactors. Line reactors are not remote switchable. | Shared | 18416.5806 | 1.27% | 1450000 | Eligible | SPS
GEN-2023-037 | N/A | ERIS | Switch out Beaver to Badger Line Reactors | Current Study | Switch out Badger to Beaver 345 kV Double Circuit line reactors (150 MVAR total) | Shared | 0 | 1.27% | 0 | Eligible
GEN-2023-037 | 170628 | ERIS | Build New Tolk to Potter County 345 kV Line | Contingent | Build a new 115.0 mile 345 kV circuit from Tolk to Potter with a standard rating of 1792 MVA | Contingent | 0 | 0% | 315122604 | Ineligible | SPS | 36
GEN-2023-037 | 158743 | ERIS | Nearman 161 kV Substation GEN-2023-037 Interconnection (Non-Shared NU) (KACY) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-037 (200MW/Battery/Storage), into Nearman 161 kV Substation | Non-Shared | 3357305 | 100% | 3357305 | Ineligible | KACY | 40
GEN-2023-037 | 158742 | ERIS | Nearman 161 kV Substation GEN-2023-037 Interconnection (TOIF) (KACY) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-037 (200MW/Battery/Storage), into Nearman161 kV Substation | Non-Shared | 0 | 100% | 0 | Ineligible | KACY | 0
GEN-2023-038 | 170658 | NRIS | Reconfigure Little City to Brown 138 kV Line | Contingent | Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation | Contingent | 0 | 0% | 375000 | Ineligible | OGE
GEN-2023-038 | 171462 | ERIS | Lula 138 kV Substation Reconfiguration | Current Study | Lula 138 kV (GEN-2023-038 POI) subtation to be reconfigured to invalidate the P4 fault during facility study. (The Interconnection costs include the estimate to invalidate the P4 contingency) | Non-Shared | 0 | 100% | 0 | Eligible | OGE
GEN-2023-038 | 158745 | ERIS | Lula 138 kV Substation GEN-2023-038 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-038 (200MW/Solar), into Lula 138 kV Substation | Non-Shared | 5417961 | 100% | 5417961 | Ineligible | OGE | 36
GEN-2023-038 | 158744 | ERIS | Lula 138 kV Substation GEN-2023-038 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-038 (200MW/Solar), into Lula 138 kV Substation | Non-Shared | 2684397 | 100% | 2684397 | Ineligible | OGE | 36
GEN-2023-055 | 158769 | ERIS | Kerr Grove 161 kV GEN-2023-055 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-055 (100MW/Battery/Storage), into Kerr Grove 161 kV | Non-Shared | 1750000 | 100% | 1750000 | Ineligible | GRDA | 24
GEN-2023-055 | 158768 | ERIS | Kerr Grove 161 kV GEN-2023-055 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-055 (100MW/Battery/Storage), into Kerr Grove 161 kV | Non-Shared | 2619247 | 100% | 2619247 | Ineligible | GRDA | 24
GEN-2023-057 | 158773 | ERIS | Pawnee Switch 138 kV GEN-2023-057 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-057 (150MW/Battery/Storage), into Pawnee Switch 138 kV | Non-Shared | 0 | 100% | 0 | Ineligible | GRDA | 24
GEN-2023-057 | 158772 | ERIS | Pawnee Switch 138 kV GEN-2023-057 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-057 (150MW/Battery/Storage), into Pawnee Switch 138 kV | Non-Shared | 990399 | 100% | 990399 | Ineligible | GRDA | 18
GEN-2023-059 | 170693, 170694 | ERIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Contingent | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Contingent | 0 | 0% | 8205000 | Ineligible | EDE/GMO
GEN-2023-059 | 158775 | ERIS | Tap Rockhill to South Shreveport 138 kV line GEN-2023-059 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-059 (200MW/Hybrid), into Tap Rockhill to South Shreveport 138 kV line | Non-Shared | 11850000 | 100% | 11850000 | Ineligible | AEP | 36
GEN-2023-059 | 158774 | ERIS | Tap Rockhill to South Shreveport 138 kV line GEN-2023-059 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-059 (200MW/Hybrid), into Tap Rockhill to South Shreveport 138 kV line | Non-Shared | 2125000 | 100% | 2125000 | Ineligible | AEP | 36
GEN-2023-061 | 158778 | ERIS | Carthage 161 kV Substation GEN-2023-061 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-061 (100MW/Battery/Storage), into Carthage 161 kV Substation | Non-Shared | 4200000 | 100% | 4200000 | Ineligible | SWPA | 48
GEN-2023-061 | 158777 | ERIS | Carthage 161 kV Substation GEN-2023-061 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-061 (100MW/Battery/Storage), into Carthage 161 kV Substation | Non-Shared | 700000 | 100% | 700000 | Ineligible | SWPA | 48
GEN-2023-063 | 158782 | ERIS | Catoosa - Owasso 88th 138 kV line GEN-2023-063 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-063 (135MW/Hybrid), into Catoosa - Owasso 88th 138 kV line | Non-Shared | 11850000 | 100% | 11850000 | Ineligible | AEP | 36
GEN-2023-063 | 158781 | ERIS | Catoosa - Owasso 88th 138 kV line GEN-2023-063 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-063 (135MW/Hybrid), into Catoosa - Owasso 88th 138 kV line | Non-Shared | 2125000 | 100% | 2125000 | Ineligible | AEP | 36
GEN-2023-064 | 158784 | ERIS | RS Kerr-Stigler 161 kV line GEN-2023-064 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-064 (200MW/Hybrid), into RS Kerr-Stigler 161 kV line | Non-Shared | 8600000 | 100% | 8600000 | Ineligible | SWPA | 48
GEN-2023-064 | 158783 | ERIS | RS Kerr-Stigler 161 kV line GEN-2023-064 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-064 (200MW/Hybrid), into RS Kerr-Stigler 161 kV line | Non-Shared | 800000 | 100% | 800000 | Ineligible | SWPA | 48
GEN-2023-069 | 170698 | NRIS | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Contingent | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | Contingent | 0 | 0% | 18105000 | Ineligible | OGE
GEN-2023-069 | 170658 | NRIS | Reconfigure Little City to Brown 138 kV Line | Contingent | Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation | Contingent | 0 | 0% | 375000 | Ineligible | OGE
GEN-2023-069 | 158793 | ERIS | Tupelo - Atoka 138 kV Line GEN-2023-069 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-069 (100MW/Hybrid), into Tupelo - Atoka 138 kV Line | Non-Shared | 6050000 | 100% | 6050000 | Ineligible | WFEC | 60
GEN-2023-069 | 158792 | ERIS | Tupelo - Atoka 138 kV Line GEN-2023-069 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-069 (100MW/Hybrid), into Tupelo - Atoka 138 kV Line | Non-Shared | 517000 | 100% | 517000 | Ineligible | WFEC | 60
GEN-2023-077 | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | Contingent | 0 | 0% | 137721276 | Ineligible | NPPD/ITCGP | 60
GEN-2023-077 | 143660, 143661, 143662 | ERIS | Line - S3454 - S3740 345 kV | Contingent | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | Contingent | 0 | 0% | 151169707 | Ineligible | OPPD | 60
GEN-2023-077 | 170693, 170694 | ERIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Contingent | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Contingent | 0 | 0% | 8205000 | Ineligible | EDE/GMO
GEN-2023-077 | 143660, 143661, 143662 | ERIS | Line - S3454 - S3740 345 kV | Contingent | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | Contingent | 0 | 0% | 151169707 | Ineligible | OPPD | 60
GEN-2023-077 | 158803 | ERIS | Substation 3740 345 kV GEN-2023-077 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077 (255MW/Thermal), into Substation 3740 345 kV | Non-Shared | 3348775 | 100% | 3348775 | Ineligible | OPPD | 42
GEN-2023-077 | 158676 | ERIS | Substation 3740 345 kV Interconnection (DISIS-2023-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077/078/079 (255MW/255MW/303MW/Thermal), into Substation 3740 345 kV | Shared | 12899764.9815 | 31.37% | 41127486 | Ineligible | OPPD | 48
GEN-2023-078 | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | Contingent | 0 | 0% | 137721276 | Ineligible | NPPD/ITCGP | 60
GEN-2023-078 | 143660, 143661, 143662 | ERIS | Line - S3454 - S3740 345 kV | Contingent | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | Contingent | 0 | 0% | 151169707 | Ineligible | OPPD | 60
GEN-2023-078 | 170693, 170694 | ERIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Contingent | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Contingent | 0 | 0% | 8205000 | Ineligible | EDE/GMO
GEN-2023-078 | 143660, 143661, 143662 | ERIS | Line - S3454 - S3740 345 kV | Contingent | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | Contingent | 0 | 0% | 151169707 | Ineligible | OPPD | 60
GEN-2023-078 | 158804 | ERIS | Substation 3740 345 kV GEN-2023-078 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-078 (255MW/Thermal), into Substation 3740 345 kV | Non-Shared | 3004365 | 100% | 3004365 | Ineligible | OPPD | 42
GEN-2023-078 | 158676 | ERIS | Substation 3740 345 kV Interconnection (DISIS-2023-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077/078/079 (255MW/255MW/303MW/Thermal), into Substation 3740 345 kV | Shared | 12899764.9815 | 31.37% | 41127486 | Ineligible | OPPD | 48
GEN-2023-079 | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | Contingent | 0 | 0% | 137721276 | Ineligible | NPPD/ITCGP | 60
GEN-2023-079 | 143660, 143661, 143662 | ERIS | Line - S3454 - S3740 345 kV | Contingent | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | Contingent | 0 | 0% | 151169707 | Ineligible | OPPD | 60
GEN-2023-079 | 170693, 170694 | ERIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Contingent | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Contingent | 0 | 0% | 8205000 | Ineligible | EDE/GMO
GEN-2023-079 | 143660, 143661, 143662 | ERIS | Line - S3454 - S3740 345 kV | Contingent | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | Contingent | 0 | 0% | 151169707 | Ineligible | OPPD | 60
GEN-2023-079 | 158805 | ERIS | Substation 3740 345 kV GEN-2023-079 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-079 (303MW/Thermal), into Substation 3740 345 kV | Non-Shared | 3004365 | 100% | 3004365 | Ineligible | OPPD | 42
GEN-2023-079 | 158676 | ERIS | Substation 3740 345 kV Interconnection (DISIS-2023-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077/078/079 (255MW/255MW/303MW/Thermal), into Substation 3740 345 kV | Shared | 15327956.0369 | 37.27% | 41127486 | Ineligible | OPPD | 48
GEN-2023-088 | 170698 | NRIS | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Contingent | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | Contingent | 0 | 0% | 18105000 | Ineligible | OGE
GEN-2023-088 | 158823 | ERIS | Pharaoh 138 kV Substation GEN-2023-088 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-088 (117MW/Wind), into Pharaoh 138 kV Substation | Non-Shared | 1200000 | 100% | 1200000 | Ineligible | WFEC | 60
GEN-2023-088 | 158822 | ERIS | Pharaoh 138 kV Substation GEN-2023-088 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-088 (117MW/Wind), into Pharaoh 138 kV Substation | Non-Shared | 517000 | 100% | 517000 | Ineligible | WFEC | 60
GEN-2023-092 | 170698 | NRIS | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Contingent | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | Contingent | 0 | 0% | 18105000 | Ineligible | OGE
GEN-2023-092 | 170658 | NRIS | Reconfigure Little City to Brown 138 kV Line | Contingent | Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation | Contingent | 0 | 0% | 375000 | Ineligible | OGE
GEN-2023-092 | 158828 | ERIS | Unger - Frogville 138 kV line GEN-2023-092 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-092 (125MW/Hybrid), into Unger - Frogville 138 kV line | Non-Shared | 6050000 | 100% | 6050000 | Ineligible | WFEC | 60
GEN-2023-092 | 158827 | ERIS | Unger - Frogville 138 kV line GEN-2023-092 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-092 (125MW/Hybrid), into Unger - Frogville 138 kV line | Non-Shared | 517000 | 100% | 517000 | Ineligible | WFEC | 60
GEN-2023-099 | 171463 | ERIS | Switch Out Carpenter Line Reactor | Current Study | Switch out the Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line. Line reactor is not remote switchable. | Shared | 29569.0467 | 2.039% | 1450000 | Eligible | SPS
GEN-2023-099 | 171464 | ERIS | Switch Out Finney Line Reactors | Current Study | Switch out the Finney (50 MVAR) - Carpenter (25 MVAR) 345kV line reactors. Line reactors are not remote switchable. | Shared | 29569.0467 | 2.039% | 1450000 | Eligible | SPS
GEN-2023-099 | 170692 | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | Contingent |  | 0% | 96000000 | Ineligible | GMO
GEN-2023-099 | N/A | ERIS | Switch out Beaver to Badger Line Reactors | Current Study | Switch out Badger to Beaver 345 kV Double Circuit line reactors (150 MVAR total) | Shared | 0 | 2.039% | 0 | Eligible
GEN-2023-099 | 170628 | ERIS | Build New Tolk to Potter County 345 kV Line | Contingent | Build a new 115.0 mile 345 kV circuit from Tolk to Potter with a standard rating of 1792 MVA | Contingent | 0 | 0% | 315122604 | Ineligible | SPS | 36
GEN-2023-099 | 158838 | ERIS | Jeffery Energy Center 345 kV Substation GEN-2023-099 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-099 (300MW/Solar), into Jeffery Energy Center 345 kV Substation | Non-Shared | 0 | 100% | 0 | Ineligible | Evergy | 36
GEN-2023-099 | 158837 | ERIS | Jeffery Energy Center 345 kV Substation GEN-2023-099 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-099 (300MW/Solar), into Jeffery Energy Center 345 kV Substation | Non-Shared | 112910 | 100% | 112910 | Ineligible | Evergy | 60
GEN-2023-102 | 170698 | NRIS | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Contingent | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | Contingent | 0 | 0% | 18105000 | Ineligible | OGE
GEN-2023-102 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 0
GEN-2023-102 | 158842 | ERIS | Degrasse 345 kV Substation GEN-2023-102 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-102 (475MW/Hybrid), into Degrasse 345 kV Substation | Non-Shared | 2986797 | 100% | 2986797 | Ineligible | OGE | 48
GEN-2023-102 | 158662 | ERIS | Degrasse 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-100/102 (300/475MW/Hybrid), into Degrasse 345 kV Substation | Non-Shared | 7460545 | 100% | 7460545 | Ineligible | OGE | 36
GEN-2023-104 | 170667 | ERIS | Rebuild NOELSW4 to ROSEVLY4 138 kV line 1 | Contingent | Rebuild the NOELSW4 to ROSEVALY4 138 kV line CKT1 (8.15 miles) to a minimum rating of 200 MVA | Contingent | 0 | 0% | 7335000 | Ineligible | WFEC
GEN-2023-104 | 158846 | ERIS | Mooreland - Noel 138 kV Line GEN-2023-104 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-104 (100MW/Hybrid), into Mooreland - Noel 138 kV Line | Non-Shared | 6050000 | 100% | 6050000 | Ineligible | WFEC | 60
GEN-2023-104 | 158845 | ERIS | Mooreland - Noel 138 kV Line GEN-2023-104 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-104 (100MW/Hybrid), into Mooreland - Noel 138 kV Line | Non-Shared | 517000 | 100% | 517000 | Ineligible | WFEC | 60
GEN-2023-107 | 171463 | ERIS | Switch Out Carpenter Line Reactor | Current Study | Switch out the Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line. Line reactor is not remote switchable. | Shared | 241033.8637 | 16.62% | 1450000 | Eligible | SPS
GEN-2023-107 | 171461 | ERIS | Build Second Red Willow 345/115 kV Transformer | Current Study | Build a second 345/115kV transformer at Red Willow | Shared | 12235623.1428 | 40.79% | 30000000 | Eligible | NPPD
GEN-2023-107 | 171464 | ERIS | Switch Out Finney Line Reactors | Current Study | Switch out the Finney (50 MVAR) - Carpenter (25 MVAR) 345kV line reactors. Line reactors are not remote switchable. | Shared | 241033.8637 | 16.62% | 1450000 | Eligible | SPS
GEN-2023-107 | 170665 | ERIS | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Contingent | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | Contingent |  | 0% | 102596000 | Ineligible | SEPC
GEN-2023-107 | 170651, 170655 | ERIS | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Contingent | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Contingent | 0 | 0% | 0 | Ineligible | ITCGP/NPPD
GEN-2023-107 | N/A | ERIS | Switch out Beaver to Badger Line Reactors | Current Study | Switch out Badger to Beaver 345 kV Double Circuit line reactors (150 MVAR total) | Shared | 0 | 16.62% | 0 | Eligible
GEN-2023-107 | 170628 | ERIS | Build New Tolk to Potter County 345 kV Line | Contingent | Build a new 115.0 mile 345 kV circuit from Tolk to Potter with a standard rating of 1792 MVA | Contingent | 0 | 0% | 315122604 | Ineligible | SPS | 36
GEN-2023-107 | 158849 | ERIS | Setab 345 kV Substation GEN-2023-107 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-107 (300MW/Wind), into Setab 345 kV | Non-Shared | 2206495 | 100% | 2206495 | Ineligible | SUNC | 48
GEN-2023-107 | 158675 | ERIS | Setab 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-107 (300MW/Wind), into Setab 345 kV Substation | Non-Shared | 5338489 | 100% | 5338489 | Ineligible | SUNC | 48
GEN-2023-120 | 158863 | ERIS | Kress 115 kV Substation GEN-2023-120 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-120 (130MW/Solar), into Kress 115 kV Substation | Non-Shared | 4967846 | 100% | 4967846 | Ineligible | SPS | 42
GEN-2023-120 | 158862 | ERIS | Kress 115 kV Substation GEN-2023-120 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-120 (130MW/Solar), into Kress 115 kV Substation | Non-Shared | 2840814 | 100% | 2840814 | Ineligible | SPS | 42
GEN-2023-120 | 170626 | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | Contingent | 0 | 0% | 1301149472 | Ineligible | SPS | 36
GEN-2023-120 | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | Contingent | 0 | 0% | 12238460 | Ineligible | AEPW/OKGE | 0
GEN-2023-120 | 170593, 170608 | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | OGE/SPS
GEN-2023-120 | 170594, 170609 | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | Contingent | 0 | 0% | 335411258 | Ineligible | OGE/SPS
GEN-2023-132 | 171455, 171456 | ERIS | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line | Current Study | Rebuild the 5HEBER.N# to GREERSF5 161 kV line CKT1 (1.6 miles) to a minimum rating of 228 MVA | Non-Shared | 2224000 | 100% | 2224000 | Eligible | EES/SWPA
GEN-2023-132 | 171455, 171456 | NRIS | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line | Contingent | Rebuild the 5HEBER.N# to GREERSF5 161 kV line CKT1 (1.6 miles) to a minimum rating of 228 MVA | Contingent | 0 | 0% | 2224000 | Ineligible | EES/SWPA
GEN-2023-132 | 158875 | ERIS | Jonesboro - Independence 161 kV GEN-2023-132 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-132 (150MW/Solar), into Jonesboro - Independence 161 kV | Non-Shared | 8600000 | 100% | 8600000 | Ineligible | SWPA | 48
GEN-2023-132 | 158874 | ERIS | Jonesboro - Independence 161 kV GEN-2023-132 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-132 (150MW/Solar), into Jonesboro - Independence 161 kV | Non-Shared | 800000 | 100% | 800000 | Ineligible | SWPA | 48
GEN-2023-135 | 158881 | ERIS | Lydia 345kV substation GEN-2023-135 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-135 (52MW/Solar), into Lydia 345kV substation | Non-Shared | 171180 | 100% | 171180 | Ineligible | AEP | 18
GEN-2023-135 | 158880 | ERIS | Lydia 345kV substation GEN-2023-135 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-135 (52MW/Solar), into Lydia 345kV substation | Non-Shared | 206941 | 100% | 206941 | Ineligible | AEP | 18
GEN-2023-153 | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | Contingent | 0 | 0% | 137721276 | Ineligible | NPPD/ITCGP | 60
GEN-2023-153 | 144231, 144238, 144237, 144230, 143714, 144236 | NRIS | Multi - Tande - Finstad - Leland Olds 345 kV | Contingent | Build a 48 mile 345 kV line from Finstad to Tande. Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer Install a switched shunt at Finstad. Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. Build a 123 mile 345 kV line from Leland Olds to Finstad. | Contingent | 0 | 0% | 336607354 | Ineligible | BEPC | 48
GEN-2023-153 | 158909 | ERIS | Grant 115 kV Substation GEN-2023-153 Interconnection (Non-Shared NU) (Tri-State) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-153 (120MW/Hybrid), into Grant 115 kV Substation | Non-Shared | 5250000 | 100% | 5250000 | Ineligible | Tri-State | 36
GEN-2023-153 | 158908 | ERIS | Grant 115 kV Substation GEN-2023-153 Interconnection (TOIF) (Tri-State) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-153 (120MW/Hybrid), into Grant 115 kV Substation | Non-Shared | 1250000 | 100% | 1250000 | Ineligible | Tri-State | 36
GEN-2023-161 | 158923 | ERIS | Roman Nose 138 kV Substation GEN-2023-161 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-161 (74.9MW/Battery/Storage), into Roman Nose 138 kV Substation | Non-Shared | 1502516 | 100% | 1502516 | Ineligible | OGE | 36
GEN-2023-161 | 158922 | ERIS | Roman Nose 138 kV Substation GEN-2023-161 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-161 (74.9MW/Battery/Storage), into Roman Nose 138 kV Substation | Non-Shared | 1764041 | 100% | 1764041 | Ineligible | OGE | 36
GEN-2023-170 | 158939 | ERIS | Salisbury 161 kV Substation GEN-2023-170 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-170 (150MW/Battery/Storage), into Salisbury 161 kV Substation | Non-Shared | 6267996 | 100% | 6267996 | Ineligible | Evergy | 36
GEN-2023-170 | 158938 | ERIS | Salisbury 161 kV Substation GEN-2023-170 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-170 (150MW/Battery/Storage), into Salisbury 161 kV Substation | Non-Shared | 1085688 | 100% | 1085688 | Ineligible | Evergy | 36
GEN-2023-171 | 158941 | ERIS | Sub M 161 kV Substation GEN-2023-171 Interconnection (Non-Shared NU) (INDN) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-171 (150MW/Battery/Storage), into Sub M 161 kV Substation | Non-Shared | 3280000 | 100% | 3280000 | Ineligible | INDN | 48
GEN-2023-171 | 158940 | ERIS | Sub M 161 kV Substation GEN-2023-171 Interconnection (TOIF) (INDN) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-171 (150MW/Battery/Storage), into Sub M 161 kV Substation. | Non-Shared | 500000 | 100% | 500000 | Ineligible | INDN | 48
GEN-2023-171 | 171463 | ERIS | Switch Out Carpenter Line Reactor | Current Study | Switch out the Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line. Line reactor is not remote switchable. | Shared | 14015.6403 | 0.9666% | 1450000 | Eligible | SPS
GEN-2023-171 | 171464 | ERIS | Switch Out Finney Line Reactors | Current Study | Switch out the Finney (50 MVAR) - Carpenter (25 MVAR) 345kV line reactors. Line reactors are not remote switchable. | Shared | 14015.6403 | 0.9666% | 1450000 | Eligible | SPS
GEN-2023-171 | N/A | ERIS | Switch out Beaver to Badger Line Reactors | Current Study | Switch out Badger to Beaver 345 kV Double Circuit line reactors (150 MVAR total) | Shared | 0 | 0.9666% | 0 | Eligible
GEN-2023-171 | 170628 | ERIS | Build New Tolk to Potter County 345 kV Line | Contingent | Build a new 115.0 mile 345 kV circuit from Tolk to Potter with a standard rating of 1792 MVA | Contingent | 0 | 0% | 315122604 | Ineligible | SPS | 36
GEN-2023-172 | 158942 | ERIS | Holcomb 345 kV GEN-2023-172 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172 (200MW/Wind), into Holcomb 345 kV | Non-Shared | 2718247 | 100% | 2718247 | Ineligible | SUNC | 48
GEN-2023-172 | 158666 | ERIS | Holcomb 345 kV Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172/173 (200/100MW/Wind), into Holcomb 345 kV | Shared | 6005658.67 | 66.67% | 9008488 | Ineligible | SUNC | 48
GEN-2023-172 | 171463 | ERIS | Switch Out Carpenter Line Reactor | Current Study | Switch out the Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line. Line reactor is not remote switchable. | Shared | 186684.8135 | 12.87% | 1450000 | Eligible | SPS
GEN-2023-172 | 171461 | ERIS | Build Second Red Willow 345/115 kV Transformer | Current Study | Build a second 345/115kV transformer at Red Willow | Shared | 5619646.9149 | 18.73% | 30000000 | Eligible | NPPD
GEN-2023-172 | 171464 | ERIS | Switch Out Finney Line Reactors | Current Study | Switch out the Finney (50 MVAR) - Carpenter (25 MVAR) 345kV line reactors. Line reactors are not remote switchable. | Shared | 186684.8135 | 12.87% | 1450000 | Eligible | SPS
GEN-2023-172 | 170665 | ERIS | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Contingent | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | Contingent |  | 0% | 102596000 | Ineligible | SEPC
GEN-2023-172 | 170651, 170655 | ERIS | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Contingent | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Contingent | 0 | 0% | 0 | Ineligible | ITCGP/NPPD
GEN-2023-172 | N/A | ERIS | Switch out Beaver to Badger Line Reactors | Current Study | Switch out Badger to Beaver 345 kV Double Circuit line reactors (150 MVAR total) | Shared | 0 | 12.87% | 0 | Eligible
GEN-2023-172 | 170628 | ERIS | Build New Tolk to Potter County 345 kV Line | Contingent | Build a new 115.0 mile 345 kV circuit from Tolk to Potter with a standard rating of 1792 MVA | Contingent | 0 | 0% | 315122604 | Ineligible | SPS | 36
GEN-2023-173 | 158943 | ERIS | Holcomb 345 kV GEN-2023-173 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-173 (100MW/Wind), into Holcomb 345 kV | Non-Shared | 2718247 | 100% | 2718247 | Ineligible | SUNC | 48
GEN-2023-173 | 158666 | ERIS | Holcomb 345 kV Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172/173 (200/100MW/Wind), into Holcomb 345 kV | Shared | 3002829.33 | 33.33% | 9008488 | Ineligible | SUNC | 48
GEN-2023-173 | 171463 | ERIS | Switch Out Carpenter Line Reactor | Current Study | Switch out the Carpenter 25 MVAR line reactor on the Carpenter to Hitchland 345 kV line. Line reactor is not remote switchable. | Shared | 93342.4067 | 6.437% | 1450000 | Eligible | SPS
GEN-2023-173 | 171461 | ERIS | Build Second Red Willow 345/115 kV Transformer | Current Study | Build a second 345/115kV transformer at Red Willow | Shared | 2809823.4574 | 9.366% | 30000000 | Eligible | NPPD
GEN-2023-173 | 171464 | ERIS | Switch Out Finney Line Reactors | Current Study | Switch out the Finney (50 MVAR) - Carpenter (25 MVAR) 345kV line reactors. Line reactors are not remote switchable. | Shared | 93342.4067 | 6.437% | 1450000 | Eligible | SPS
GEN-2023-173 | 170665 | ERIS | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Contingent | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | Contingent |  | 0% | 102596000 | Ineligible | SEPC
GEN-2023-173 | 170651, 170655 | ERIS | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Contingent | Switch out Axtell to G16-050-TAP 345 kV line reactor at Axtell (50 MVAR) | Contingent | 0 | 0% | 0 | Ineligible | ITCGP/NPPD
GEN-2023-173 | N/A | ERIS | Switch out Beaver to Badger Line Reactors | Current Study | Switch out Badger to Beaver 345 kV Double Circuit line reactors (150 MVAR total) | Shared | 0 | 6.437% | 0 | Eligible
GEN-2023-173 | 170628 | ERIS | Build New Tolk to Potter County 345 kV Line | Contingent | Build a new 115.0 mile 345 kV circuit from Tolk to Potter with a standard rating of 1792 MVA | Contingent | 0 | 0% | 315122604 | Ineligible | SPS | 36
GEN-2023-177 | 158950 | ERIS | Paoli - Seminole 138 kV line tap GEN-2023-177 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-177 (200MW/Solar), into Paoli - Seminole 138 kV line tap | Non-Shared | 7079843 | 100% | 7079843 | Ineligible | OGE | 36
GEN-2023-177 | 158949 | ERIS | Paoli - Seminole 138 kV line tap GEN-2023-177 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-177 (200MW/Solar), into Paoli - Seminole 138 kV line tap | Non-Shared | 3759390 | 100% | 3759390 | Ineligible | OGE | 36
GEN-2023-193 | 158972 | ERIS | Pirkey - Whitney 138 kV Line GEN-2023-193 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-193 (175MW/Hybrid), into Pirkey - Whitney 138 kV Line | Non-Shared | 11850000 | 100% | 11850000 | Ineligible | AEP | 36
GEN-2023-193 | 158971 | ERIS | Pirkey - Whitney 138 kV Line GEN-2023-193 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-193 (175MW/Hybrid), into Pirkey - Whitney 138 kV Line | Non-Shared | 2125000 | 100% | 2125000 | Ineligible | AEP | 36
GEN-2023-199 | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | Contingent | 0 | 0% | 137721276 | Ineligible | NPPD/ITCGP | 60
GEN-2023-199 | 170654 | NRIS | Rebuild the AXTELL 7 to KEARNEY7 115kV Line 1 | Contingent | Rebuild the existing AXTELL 7 to KEARNEY7 115 kV line 1 (10.74 miles) to a minimum rating of 254 MVA (minimum rating of 255 MVA is required for DISIS-2023-001, NPPD has confirmed the rebuild from DISIS-2021-001 Cluster can achieve it) | Contingent | 0 | 0% | 25000000 | Ineligible | NPPD
GEN-2023-199 | 170653 | NRIS | Build a new AXTELL 345/115 kV Transformer 2 | Contingent | Build a new AXTELL 345/115 kV Transformer 2 to a minimum rating of 336 MVA | Contingent | 0 | 0% | 25000000 | Ineligible | NPPD
GEN-2023-199 | 158982 | ERIS | Twin Church 230 kV Substation GEN-2023-199 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-199 (250MW/Hybrid), into Twin Church 230 kV Substation | Non-Shared | 1200000 | 100% | 1200000 | Ineligible | NPPD | 36
GEN-2023-199 | 158981 | ERIS | Twin Church 230 kV Substation GEN-2023-199 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-199 (250MW/Hybrid), into Twin Church 230 kV Substation | Non-Shared | 500000 | 100% | 500000 | Ineligible | NPPD | 36
GEN-2023-204 | 158992 | ERIS | Welsh-Lydia 345kV Line GEN-2023-204 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-204 (953MW/Thermal), into Welsh-Lydia 345kV Line | Non-Shared | 20000000 | 100% | 20000000 | Ineligible | AEP | 42
GEN-2023-204 | 158991 | ERIS | Welsh-Lydia 345kV Line GEN-2023-204 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-204 (953MW/Thermal), into Welsh-Lydia 345kV Line | Non-Shared | 3275000 | 100% | 3275000 | Ineligible | AEP | 42
GEN-2023-204 | 170693, 170694 | ERIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Contingent | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Contingent | 0 | 0% | 8205000 | Ineligible | EDE/GMO
GEN-2023-205 | 158994 | ERIS | McAlester City - Weleetka 138 kV line GEN-2023-205 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-205 (180MW/Solar), into McAlester City - Weleetka 138 kV line | Non-Shared | 11850000 | 100% | 11850000 | Ineligible | AEP | 36
GEN-2023-205 | 158993 | ERIS | McAlester City - Weleetka 138 kV line GEN-2023-205 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-205 (180MW/Solar), into McAlester City - Weleetka 138 kV line | Non-Shared | 1925000 | 100% | 1925000 | Ineligible | AEP | 36
GEN-2023-206 | 158996 | ERIS | Battlefield BESS 161 kV Substation GEN-2023-206 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-206 (50MW/Battery/Storage), into Battlefield BESS 161 kV Substation | Non-Shared | 30000 | 100% | 30000 | Ineligible | OGE | 24
GEN-2023-206 | 158995 | ERIS | Battlefield BESS 161 kV Substation GEN-2023-206 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-206 (50MW/Battery/Storage), into Battlefield BESS 161 kV Substation | Non-Shared | 100000 | 100% | 100000 | Ineligible | OGE | 24
GEN-2023-210 | 159004 | ERIS | Prague - Chernicky 138 kV Line GEN-2023-210 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-210 (191MW/Solar), into Prague - Chernicky 138 kV Line | Non-Shared | 6050000 | 100% | 6050000 | Ineligible | WFEC | 60
GEN-2023-210 | 159003 | ERIS | Prague - Chernicky 138 kV Line GEN-2023-210 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-210 (191MW/Solar), into Prague - Chernicky 138 kV Line | Non-Shared | 517000 | 100% | 517000 | Ineligible | WFEC | 60
GEN-2023-210 | 170698 | NRIS | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Contingent | Rebuild the existing WOODWRD4 to WINDFRM4 138 kV line 1 (12.07 miles) to a minimum rating of 200 MVA | Contingent | 0 | 0% | 18105000 | Ineligible | OGE
GEN-2023-220 | 159019 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-220 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-220 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | Non-Shared | 32882571 | 100% | 32882571 | Ineligible | Evergy | 56
GEN-2023-220 | 159018 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-220 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-220 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | Non-Shared | 1958092 | 100% | 1958092 | Ineligible | Evergy | 56
GEN-2023-220 | 170628 | ERIS | Build New Tolk to Potter County 345 kV Line | Contingent | Build a new 115.0 mile 345 kV circuit from Tolk to Potter with a standard rating of 1792 MVA | Contingent | 0 | 0% | 315122604 | Ineligible | SPS | 36
GEN-2023-221 | 159021 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-221 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-221 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | Non-Shared | 33237331 | 100% | 33237331 | Ineligible | Evergy | 56
GEN-2023-221 | 159020 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-221 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-221 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | Non-Shared | 1958092 | 100% | 1958092 | Ineligible | Evergy | 56
GEN-2023-221 | 170628 | ERIS | Build New Tolk to Potter County 345 kV Line | Contingent | Build a new 115.0 mile 345 kV circuit from Tolk to Potter with a standard rating of 1792 MVA | Contingent | 0 | 0% | 315122604 | Ineligible | SPS | 36
GEN-2023-222 | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | Contingent | 0 | 0% | 137721276 | Ineligible | NPPD/ITCGP | 60
GEN-2023-222 | 171457 | ERIS | Build the Daykin 345 kV Substation | Current Study | Tap the new Tobias to Elm Creek 345 kV line and build a 345 kV Substation (Daykin) | Shared | 15333333.3333 | 66.67% | 23000000 | Eligible | NPPD
GEN-2023-222 | 171458 | ERIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Monolith 345 kV line 1 (approximately 23 miles) to a standard rating of 1793 MVA | Shared | 40666666.6667 | 66.67% | 61000000 | Eligible | NPPD
GEN-2023-222 | 171459 | ERIS | Build a new Beatrice Power Station 345/115 kV to DAYKIN 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Daykin 345 kV line 1 (approximately 22 miles) to a standard rating of 1793 MVA | Shared | 35333333.3333 | 66.67% | 53000000 | Eligible | NPPD
GEN-2023-222 | 170654 | NRIS | Rebuild the AXTELL 7 to KEARNEY7 115kV Line 1 | Contingent | Rebuild the existing AXTELL 7 to KEARNEY7 115 kV line 1 (10.74 miles) to a minimum rating of 254 MVA (minimum rating of 255 MVA is required for DISIS-2023-001, NPPD has confirmed the rebuild from DISIS-2021-001 Cluster can achieve it) | Contingent | 0 | 0% | 25000000 | Ineligible | NPPD
GEN-2023-222 | 171460 | NRIS | Rebuild the existing LOWELL7 to MINDEN7 115 kV line | Current Study | Rebuild the LOWELL7 to MINDEN7 115 kV line CKT1 (10.75 miles) to a minimum rating of 128 MVA | Shared | 7166666.6667 | 66.67% | 10750000 | Eligible | NPPD
GEN-2023-222 | 170693, 170694 | ERIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Contingent | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Contingent | 0 | 0% | 8205000 | Ineligible | EDE/GMO
GEN-2023-222 | 71963, 71964, 71965, 71966, 71967, 71968 | ERIS | Multi - Sheldon - Monolith 115 kV | Contingent | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | Contingent | 0 | 0% | 60975092 | Ineligible | NPPD | 36
GEN-2023-222 | 170653 | NRIS | Build a new AXTELL 345/115 kV Transformer 2 | Contingent | Build a new AXTELL 345/115 kV Transformer 2 to a minimum rating of 336 MVA | Contingent | 0 | 0% | 25000000 | Ineligible | NPPD
GEN-2023-222 | 71963, 71964, 71965, 71966, 71967, 71968 | NRIS | Multi - Sheldon - Monolith 115 kV | Contingent | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | Contingent | 0 | 0% | 60975092 | Ineligible | NPPD | 36
GEN-2023-222 | 171457 | NRIS | Build the Daykin 345 kV Substation | Contingent | Tap the new Tobias to Elm Creek 345 kV line and build a 345 kV Substation (Daykin) | Contingent | 0 | 0% | 23000000 | Ineligible | NPPD
GEN-2023-222 | 171458 | NRIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Monolith 345 kV line 1 (approximately 23 miles) to a standard rating of 1793 MVA | Contingent | 0 | 0% | 61000000 | Ineligible | NPPD
GEN-2023-222 | 171459 | NRIS | Build a new Beatrice Power Station 345/115 kV to DAYKIN 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Daykin 345 kV line 1 (approximately 22 miles) to a standard rating of 1793 MVA | Contingent | 0 | 0% | 53000000 | Ineligible | NPPD
GEN-2023-222 | 159022 | ERIS | New Beatrice Power Station 345 kV GEN-2023-222 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222 (478MW/Thermal), into New Beatrice Power Station 345 kV | Non-Shared | 1000000 | 100% | 1000000 | Ineligible | NPPD | 60
GEN-2023-222 | 158670 | ERIS | New Beatrice Power Station 345 kV Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222/223 (478/239MW/Thermal), into New Beatrice Power Station 345 kV | Shared | 38933333.33 | 66.67% | 58400000 | Ineligible | NPPD
GEN-2023-223 | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | Contingent | 0 | 0% | 137721276 | Ineligible | NPPD/ITCGP | 60
GEN-2023-223 | 171457 | ERIS | Build the Daykin 345 kV Substation | Current Study | Tap the new Tobias to Elm Creek 345 kV line and build a 345 kV Substation (Daykin) | Shared | 7666666.6667 | 33.33% | 23000000 | Eligible | NPPD
GEN-2023-223 | 171458 | ERIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Monolith 345 kV line 1 (approximately 23 miles) to a standard rating of 1793 MVA | Shared | 20333333.3333 | 33.33% | 61000000 | Eligible | NPPD
GEN-2023-223 | 171459 | ERIS | Build a new Beatrice Power Station 345/115 kV to DAYKIN 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Daykin 345 kV line 1 (approximately 22 miles) to a standard rating of 1793 MVA | Shared | 17666666.6667 | 33.33% | 53000000 | Eligible | NPPD
GEN-2023-223 | 170654 | NRIS | Rebuild the AXTELL 7 to KEARNEY7 115kV Line 1 | Contingent | Rebuild the existing AXTELL 7 to KEARNEY7 115 kV line 1 (10.74 miles) to a minimum rating of 254 MVA (minimum rating of 255 MVA is required for DISIS-2023-001, NPPD has confirmed the rebuild from DISIS-2021-001 Cluster can achieve it) | Contingent | 0 | 0% | 25000000 | Ineligible | NPPD
GEN-2023-223 | 171460 | NRIS | Rebuild the existing LOWELL7 to MINDEN7 115 kV line | Current Study | Rebuild the LOWELL7 to MINDEN7 115 kV line CKT1 (10.75 miles) to a minimum rating of 128 MVA | Shared | 3583333.3333 | 33.33% | 10750000 | Eligible | NPPD
GEN-2023-223 | 170693, 170694 | ERIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Contingent | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Contingent | 0 | 0% | 8205000 | Ineligible | EDE/GMO
GEN-2023-223 | 71963, 71964, 71965, 71966, 71967, 71968 | ERIS | Multi - Sheldon - Monolith 115 kV | Contingent | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | Contingent | 0 | 0% | 60975092 | Ineligible | NPPD | 36
GEN-2023-223 | 170653 | NRIS | Build a new AXTELL 345/115 kV Transformer 2 | Contingent | Build a new AXTELL 345/115 kV Transformer 2 to a minimum rating of 336 MVA | Contingent | 0 | 0% | 25000000 | Ineligible | NPPD
GEN-2023-223 | 71963, 71964, 71965, 71966, 71967, 71968 | NRIS | Multi - Sheldon - Monolith 115 kV | Contingent | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | Contingent | 0 | 0% | 60975092 | Ineligible | NPPD | 36
GEN-2023-223 | 171457 | NRIS | Build the Daykin 345 kV Substation | Contingent | Tap the new Tobias to Elm Creek 345 kV line and build a 345 kV Substation (Daykin) | Contingent | 0 | 0% | 23000000 | Ineligible | NPPD
GEN-2023-223 | 171458 | NRIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Monolith 345 kV line 1 (approximately 23 miles) to a standard rating of 1793 MVA | Contingent | 0 | 0% | 61000000 | Ineligible | NPPD
GEN-2023-223 | 171459 | NRIS | Build a new Beatrice Power Station 345/115 kV to DAYKIN 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Daykin 345 kV line 1 (approximately 22 miles) to a standard rating of 1793 MVA | Contingent | 0 | 0% | 53000000 | Ineligible | NPPD
GEN-2023-223 | 159023 | ERIS | New Beatrice Power Station 345 kV GEN-2023-223 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-223 (239MW/Thermal), into New Beatrice Power Station 345 kV | Non-Shared | 1000000 | 100% | 1000000 | Ineligible | NPPD | 60
GEN-2023-223 | 158670 | ERIS | New Beatrice Power Station 345 kV Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222/223 (478/239MW/Thermal), into New Beatrice Power Station 345 kV | Shared | 19466666.67 | 33.33% | 58400000 | Ineligible | NPPD
GEN-2023-224 | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | Contingent | 0 | 0% | 137721276 | Ineligible | NPPD/ITCGP | 60
GEN-2023-224 | 170693, 170694 | ERIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Contingent | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Contingent | 0 | 0% | 8205000 | Ineligible | EDE/GMO
GEN-2023-224 | 71963, 71964, 71965, 71966, 71967, 71968 | ERIS | Multi - Sheldon - Monolith 115 kV | Contingent | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | Contingent | 0 | 0% | 60975092 | Ineligible | NPPD | 36
GEN-2023-224 | 159024 | ERIS | Olive Creek 345 kV Substation GEN-2023-224 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224 (478MW/Thermal), into Olive Creek 345 kV Substation | Non-Shared | 1000000 | 100% | 1000000 | Ineligible | NPPD | 60
GEN-2023-224 | 158671 | ERIS | Olive Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224/225 (478/217MW/Thermal), into Olive Creek 345 kV Substation | Shared | 76204892.09 | 68.78% | 110800000 | Ineligible | NPPD | 60
GEN-2023-225 | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | Contingent | 0 | 0% | 137721276 | Ineligible | NPPD/ITCGP | 60
GEN-2023-225 | 170693, 170694 | ERIS | Rebuild the RIV4525 to G20-079-TAP 161kV Line 1 | Contingent | Rebuild the existing RIV4525 to G20-079-TAP 161 kV line 1 (5.47 miles) to a minimum rating of 650 MVA | Contingent | 0 | 0% | 8205000 | Ineligible | EDE/GMO
GEN-2023-225 | 71963, 71964, 71965, 71966, 71967, 71968 | ERIS | Multi - Sheldon - Monolith 115 kV | Contingent | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. Add a new 345/115 kV ckt 1 transformer at Monolith substation. Add a new 345/115 kV ckt 2 transformer at Monolith substation. Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | Contingent | 0 | 0% | 60975092 | Ineligible | NPPD | 36
GEN-2023-225 | 159025 | ERIS | Olive Creek 345 kV Substation GEN-2023-225 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-225 (217MW/Thermal), into Olive Creek 345 kV Substation | Non-Shared | 1000000 | 100% | 1000000 | Ineligible | NPPD | 60
GEN-2023-225 | 158671 | ERIS | Olive Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224/225 (478/217MW/Thermal), into Olive Creek 345 kV Substation | Shared | 34595107.91 | 31.22% | 110800000 | Ineligible | NPPD | 60
GEN-2023-229 | 159033 | ERIS | Southwestern Power Station 138 kV Sub (SWS4) GEN-2023-229 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-229 (230MW/Wind), into Southwestern Power Station 138 kV Substation (SWS4) | Non-Shared | 3553691 | 100% | 3553691 | Ineligible | AEP | 36
GEN-2023-229 | 159032 | ERIS | Southwestern Power Station 138 kV Substation (SWS4) GEN-2023-229 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-229 (230MW/Wind), into Southwestern Power Station 138 kV Substation (SWS4) | Non-Shared | 2164113 | 100% | 2164113 | Ineligible | AEP | 36
GEN-2023-229 | 82111, 82112, 82115 | ERIS | Line - Cogar - OU SW 138 kV | Contingent | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | Contingent | 0 | 0% | 37489652 | Ineligible | WFEC | 0
GEN-2023-229 | 170593, 170608 | NRIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | Contingent | 0 | 0% | 428620878 | Ineligible | OGE/SPS
GEN-2023-230 | 159035 | ERIS | Red Pointe 138 kV Substation GEN-2023-230 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-230 (150MW/Hybrid), into Red Pointe 138 kV Substation | Non-Shared | 3338007 | 100% | 3338007 | Ineligible | AEP | 30
GEN-2023-230 | 159034 | ERIS | Red Pointe 138 kV Substation GEN-2023-230 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-230 (150MW/Hybrid), into Red Pointe 138 kV Substation | Non-Shared | 2575383 | 100% | 2575383 | Ineligible | AEP | 30
GEN-2023-241 | 159051 | ERIS | Winnsboro 138 kV Substation GEN-2023-241 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-241 (93MW/Solar), into Winnsboro 138 kV Substation | Non-Shared | 4107515 | 100% | 4107515 | Ineligible | AEP | 36
GEN-2023-241 | 159050 | ERIS | Winnsboro 138 kV Substation GEN-2023-241 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-241 (93MW/Solar), into Winnsboro 138 kV Substation | Non-Shared | 2327363 | 100% | 2327363 | Ineligible | AEP | 36
Total | [6 empty] | 787079690

## Affected Systems Costs
Gen Number | Upgrade Name | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost
GEN-2023-006 | NU00A: Blackberry 345 kV Station Modifications | Modification to Blackberry 345 kV station required for GEN-2023-006 to interconnect on Blackberry-Wolf Creek 345 kV line | 350000 | 100% | 350000
GEN-2023-006 | NU04: 300794 5LAMAR 161 300950 5JASPER 161 1 | Rebuild 12.8 mile long Jasper-Lamar 161 kV line to 1192 ACSR at 100C. Upgrade jumpers on both sides of line to 1192 ACSR. | 3345227 | 28.42% | 11770001
GEN-2023-023 | NU01: 300071 5CLINTN 161 300124 5HOLDENB2 161 1 | Rebuild 30.2 mile long segment of Clinton-Holden 161 kV line to 795 ACSR at 100C. | 1355005 | 6.903% | 19629999
GEN-2023-028 | NU05: 301451 2GRAY TP 69.0 512628 PENSA 2 69.0 1 | Rebuild 4.4 mile long Gray Tap-Pensacola 69 kV line to 795 ACSR at 100C. | 1239251 | 43.33% | 2860000
GEN-2023-032 | NU01: 300071 5CLINTN 161 300124 5HOLDENB2 161 1 | Rebuild 30.2 mile long segment of Clinton-Holden 161 kV line to 795 ACSR at 100C. | 1194344 | 6.084% | 19629999
GEN-2023-033 | NU01: 300071 5CLINTN 161 300124 5HOLDENB2 161 1 | Rebuild 30.2 mile long segment of Clinton-Holden 161 kV line to 795 ACSR at 100C. | 2516004 | 12.82% | 19629999
GEN-2023-033 | NU06: 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | Rebuild 6.1 mile long Missouri City-Eckles 161 kV line to 1192 ACSS at 200C. Upgrade jumpers at Missouri City to 1192 ACSS at 200C. | 2146138 | 53.37% | 4021000
GEN-2023-036 | NU01: 300071 5CLINTN 161 300124 5HOLDENB2 161 1 | Rebuild 30.2 mile long segment of Clinton-Holden 161 kV line to 795 ACSR at 100C. | 4056374 | 20.66% | 19629999
GEN-2023-037 | NU01: 300071 5CLINTN 161 300124 5HOLDENB2 161 1 | Rebuild 30.2 mile long segment of Clinton-Holden 161 kV line to 795 ACSR at 100C. | 1333785 | 6.795% | 19629999
GEN-2023-049 | NU05: 301451 2GRAY TP 69.0 512628 PENSA 2 69.0 1 | Rebuild 4.4 mile long Gray Tap-Pensacola 69 kV line to 795 ACSR at 100C. | 1013903 | 35.45% | 2860000
GEN-2023-050 | NU02: 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | Upgrade Disconnect Switches at Mansfield on Mansfield-Logan 161 kV line to 2000 amp switches. | 14294 | 4.084% | 350000
GEN-2023-050 | NU04: 300794 5LAMAR 161 300950 5JASPER 161 1 | Rebuild 12.8 mile long Jasper-Lamar 161 kV line to 1192 ACSR at 100C. Upgrade jumpers on both sides of line to 1192 ACSR. | 3553663 | 30.19% | 11770001
GEN-2023-055 | NU05: 301451 2GRAY TP 69.0 512628 PENSA 2 69.0 1 | Rebuild 4.4 mile long Gray Tap-Pensacola 69 kV line to 795 ACSR at 100C. | 157627 | 5.511% | 2860000
GEN-2023-057 | NU03: 300131 4FISHERTP 138 300140 4SILVCTY 138 1 | Rebuild 14.7 mile long Fisher Tap-Silver City 138 kV line to 1192 ACSR at 100C. Upgrade jumpers on both sides of line to 1192 ACSR. Upgrade Wave Trap on the Fisher Tap-Silver City 138 kV line at the Silver City station to 2000 amps. | 5297881 | 36.65% | 14455000
GEN-2023-064 | NU00B: Stigler 161 kV Station Modifications | Modification to Stigler 161 kV station required for GEN-2023-064 to interconnect on RS Kerr-Stigler 161 kV line | 250000 | 100% | 250000
GEN-2023-075 | NU04: 300794 5LAMAR 161 300950 5JASPER 161 1 | Rebuild 12.8 mile long Jasper-Lamar 161 kV line to 1192 ACSR at 100C. Upgrade jumpers on both sides of line to 1192 ACSR. | 1461311 | 12.42% | 11770001
GEN-2023-081 | NU03: 300131 4FISHERTP 138 300140 4SILVCTY 138 1 | Rebuild 14.7 mile long Fisher Tap-Silver City 138 kV line to 1192 ACSR at 100C. Upgrade jumpers on both sides of line to 1192 ACSR. Upgrade Wave Trap on the Fisher Tap-Silver City 138 kV line at the Silver City station to 2000 amps. | 1528225 | 10.57% | 14455000
GEN-2023-081 | NU04: 300794 5LAMAR 161 300950 5JASPER 161 1 | Rebuild 12.8 mile long Jasper-Lamar 161 kV line to 1192 ACSR at 100C. Upgrade jumpers on both sides of line to 1192 ACSR. | 1093079 | 9.287% | 11770001
GEN-2023-085 | NU00C: Mansfield and Logan 161 kV Station Modifications | Modification to Mansfield and Logan 161 kV stations required for GEN-2023-085 to interconnect on MansfieldLogan 161 kV line. | 500000 | 100% | 500000
GEN-2023-085 | NU02: 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | Upgrade Disconnect Switches at Mansfield on Mansfield-Logan 161 kV line to 2000 amp switches. | 335706 | 95.92% | 350000
GEN-2023-088 | NU03: 300131 4FISHERTP 138 300140 4SILVCTY 138 1 | Rebuild 14.7 mile long Fisher Tap-Silver City 138 kV line to 1192 ACSR at 100C. Upgrade jumpers on both sides of line to 1192 ACSR. Upgrade Wave Trap on the Fisher Tap-Silver City 138 kV line at the Silver City station to 2000 amps. | 1435667 | 9.932% | 14455000
GEN-2023-099 | NU01: 300071 5CLINTN 161 300124 5HOLDENB2 161 1 | Rebuild 30.2 mile long segment of Clinton-Holden 161 kV line to 795 ACSR at 100C. | 995792 | 5.073% | 19629999
GEN-2023-116 | NU01: 300071 5CLINTN 161 300124 5HOLDENB2 161 1 | Rebuild 30.2 mile long segment of Clinton-Holden 161 kV line to 795 ACSR at 100C. | 1068544 | 5.443% | 19629999
GEN-2023-134 | NU03: 300131 4FISHERTP 138 300140 4SILVCTY 138 1 | Rebuild 14.7 mile long Fisher Tap-Silver City 138 kV line to 1192 ACSR at 100C. Upgrade jumpers on both sides of line to 1192 ACSR. Upgrade Wave Trap on the Fisher Tap-Silver City 138 kV line at the Silver City station to 2000 amps. | 1958432 | 13.55% | 14455000
GEN-2023-138 | NU05: 301451 2GRAY TP 69.0 512628 PENSA 2 69.0 1 | Rebuild 4.4 mile long Gray Tap-Pensacola 69 kV line to 795 ACSR at 100C. | 312718 | 10.93% | 2860000
GEN-2023-169 | NU00D: Missouri City 161 kV Station Modifications | Modification to Missouri City 161 kV station required for GEN-2023-169 to interconnect on Missouri CityLiberty South 161 kV line. | 250000 | 100% | 250000
GEN-2023-169 | NU01: 300071 5CLINTN 161 300124 5HOLDENB2 161 1 | Rebuild 30.2 mile long segment of Clinton-Holden 161 kV line to 795 ACSR at 100C. | 2131404 | 10.86% | 19629999
GEN-2023-169 | NU06: 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | Rebuild 6.1 mile long Missouri City-Eckles 161 kV line to 1192 ACSS at 200C. Upgrade jumpers at Missouri City to 1192 ACSS at 200C. | 1446658 | 35.98% | 4021000
GEN-2023-170 | NU06: 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | Rebuild 6.1 mile long Missouri City-Eckles 161 kV line to 1192 ACSS at 200C. Upgrade jumpers at Missouri City to 1192 ACSS at 200C. | 234750 | 5.838% | 4021000
GEN-2023-171 | NU01: 300071 5CLINTN 161 300124 5HOLDENB2 161 1 | Rebuild 30.2 mile long segment of Clinton-Holden 161 kV line to 795 ACSR at 100C. | 1993857 | 10.16% | 19629999
GEN-2023-191 | NU05: 301451 2GRAY TP 69.0 512628 PENSA 2 69.0 1 | Rebuild 4.4 mile long Gray Tap-Pensacola 69 kV line to 795 ACSR at 100C. | 136501 | 4.773% | 2860000
GEN-2023-205 | NU03: 300131 4FISHERTP 138 300140 4SILVCTY 138 1 | Rebuild 14.7 mile long Fisher Tap-Silver City 138 kV line to 1192 ACSR at 100C. Upgrade jumpers on both sides of line to 1192 ACSR. Upgrade Wave Trap on the Fisher Tap-Silver City 138 kV line at the Silver City station to 2000 amps. | 1538843 | 10.65% | 14455000
GEN-2023-210 | NU03: 300131 4FISHERTP 138 300140 4SILVCTY 138 1 | Rebuild 14.7 mile long Fisher Tap-Silver City 138 kV line to 1192 ACSR at 100C. Upgrade jumpers on both sides of line to 1192 ACSR. Upgrade Wave Trap on the Fisher Tap-Silver City 138 kV line at the Silver City station to 2000 amps. | 1442274 | 9.978% | 14455000
GEN-2023-222 | NU01: 300071 5CLINTN 161 300124 5HOLDENB2 161 1 | Rebuild 30.2 mile long segment of Clinton-Holden 161 kV line to 795 ACSR at 100C. | 1492445 | 7.603% | 19629999
GEN-2023-224 | NU01: 300071 5CLINTN 161 300124 5HOLDENB2 161 1 | Rebuild 30.2 mile long segment of Clinton-Holden 161 kV line to 795 ACSR at 100C. | 1492445 | 7.603% | 19629999
GEN-2023-224 | NU06: 301563 5MOCITYB1 161 548808 ECKLES-161 161 1 | Rebuild 6.1 mile long Missouri City-Eckles 161 kV line to 1192 ACSS at 200C. Upgrade jumpers at Missouri City to 1192 ACSS at 200C. | 193454 | 4.811% | 4021000
GEN-2023-231 | NU04: 300794 5LAMAR 161 300950 5JASPER 161 1 | Rebuild 12.8 mile long Jasper-Lamar 161 kV line to 1192 ACSR at 100C. Upgrade jumpers on both sides of line to 1192 ACSR. | 2316721 | 19.68% | 11770001
GEN-2023-237 | NU03: 300131 4FISHERTP 138 300140 4SILVCTY 138 1 | Rebuild 14.7 mile long Fisher Tap-Silver City 138 kV line to 1192 ACSR at 100C. Upgrade jumpers on both sides of line to 1192 ACSR. Upgrade Wave Trap on the Fisher Tap-Silver City 138 kV line at the Silver City station to 2000 amps. | 1253678 | 8.673% | 14455000
Total |  |  | 54436000

## Total Allocated Cost
Gen Number | Total Allocated Cost Estimate | Creditible Upgrade Total | Non-Creditible Upgrade Total
ASGI-2023-001 | 0 | 0 | 0
GEN-2023-015 | 56870035.6064 | 11031040.6064 | 45838995
GEN-2023-033 | 6906445.1755 | 37741.1755 | 2206562
GEN-2023-034 | 16020202 | 0 | 16020202
GEN-2023-035 | 6567000 | 0 | 6567000
GEN-2023-037 | 4727923.1612 | 36833.1612 | 3357305
GEN-2023-038 | 8102358 | 0 | 8102358
GEN-2023-055 | 4526874 | 0 | 4369247
GEN-2023-057 | 6288280 | 0 | 990399
GEN-2023-059 | 13975000 | 0 | 13975000
GEN-2023-061 | 4900000 | 0 | 4900000
GEN-2023-063 | 13975000 | 0 | 13975000
GEN-2023-064 | 9650000 | 0 | 9400000
GEN-2023-069 | 6567000 | 0 | 6567000
GEN-2023-077 | 16248539.9815 | 0 | 16248539.9815
GEN-2023-078 | 15904129.9815 | 0 | 15904129.9815
GEN-2023-079 | 18332321.0369 | 0 | 18332321.0369
GEN-2023-088 | 3152667 | 0 | 1717000
GEN-2023-092 | 6567000 | 0 | 6567000
GEN-2023-099 | 1167840.0934 | 59138.0934 | 112910
GEN-2023-102 | 10447342 | 0 | 10447342
GEN-2023-104 | 6567000 | 0 | 6567000
GEN-2023-107 | 20262674.8702 | 12717690.8702 | 7544984
GEN-2023-120 | 7808660 | 0 | 7808660
GEN-2023-132 | 11624000 | 2224000 | 9400000
GEN-2023-135 | 378121 | 0 | 378121
GEN-2023-153 | 6500000 | 0 | 6500000
GEN-2023-161 | 3266557 | 0 | 3266557
GEN-2023-170 | 7588434 | 0 | 7353684
GEN-2023-171 | 5801888.2805 | 28031.2805 | 3780000
GEN-2023-172 | 14716922.2118 | 5993016.5418 | 8723905.67
GEN-2023-173 | 8717584.6009 | 2996508.2709 | 5721076.33
GEN-2023-177 | 10839233 | 0 | 10839233
GEN-2023-193 | 13975000 | 0 | 13975000
GEN-2023-199 | 1700000 | 0 | 1700000
GEN-2023-204 | 23275000 | 0 | 23275000
GEN-2023-205 | 15313843 | 0 | 13775000
GEN-2023-206 | 130000 | 0 | 130000
GEN-2023-210 | 8009274 | 0 | 6567000
GEN-2023-220 | 34840663 | 0 | 34840663
GEN-2023-221 | 35195423 | 0 | 35195423
GEN-2023-222 | 139925778.33 | 98500000 | 39933333.33
GEN-2023-223 | 69716666.67 | 49250000 | 20466666.67
GEN-2023-224 | 78890791.09 | 0 | 77204892.09
GEN-2023-225 | 35595107.91 | 0 | 35595107.91
GEN-2023-229 | 5717804 | 0 | 5717804
GEN-2023-230 | 5913390 | 0 | 5913390
GEN-2023-241 | 6434878 | 0 | 6434878
Total | 809600652